## BoQ1
Government eProcurement System Created By: Tapan Kumar Bala Created Date/Time: 15-Jan-2021 12:04 PM Tender Title: Provision of High mast lighting tower in Old apron area near Cargo gate and Street lights at Airline bus parking area at LGBI Airport, Guwahati Tender ID: 2020_AAI_64860_1
Tender Inviting Authority: Asst. General Manager (Engg – Elect), AAI, LGBI Airport, Guwahati, Assam – 781015
Name of Work: Provision of High mast lighting tower in Old apron area near Cargo gate and Street lights at Airline bus parking area at LGBI Airport, Guwahati.
Contract No: AAI/AGM(E-E)/NIT-13/2020-21
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | North Eastern Engineers(GSTN-18AABFN4790M3ZP) |  | BR Power Control and Automation Services(GSTN-06AREPS4024K1ZP) |  | SHREE GOURI ELECTRIC ENTERPRISE(GSTN-19ADDPB4683J1ZE) |  | D.D.METAL CORPORATION(GSTN-18ACGPD4624F2ZW)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, manufacture & Supply of 16M high mast system complete with all accessories. Mast shaft shall be in two sections, hot dip galvanised and suitable for wind velocity as per IS:875. It shall also include accessories for high mast inclduing head frame, steel wire rope 6 mm dia (SS) with electrically operated raising and lowering mechanism, luminaries carriage suitable to install 16 nos of LED Light fixtures in 0°-180°of horizontal plane and suitable counterweight in 180°-360°of horizontal plane with its accissories in symmetrical arrangement, double drum winch, 1.1 KV grade multicore copper conductor trailing cable, connector, junction box, lightening finial etc. The mast shall have an integral power tool motor, manual handle installed inside the base compartment for its operation including supply of :- a) Foundation bolts manufactured from special steel along with nuts, washers, anchor plate and common template (as per OEM standard). b) 5 core 4sq.mm. copper conductor flexible EPR/ PCP cotton braided LT trailing cable of suitable length for 16 mtr height apron high mast lighting tower including supply and fixing of 5 pin [3P + N + E] plug and GT connector with cable sleev complete as required. | 1.00 | Set |  | 135000.00 | 135000.00 | 118500.00 | 118500.00 | 130000.00 | 130000.00 | 156000.00 | 156000.00 | 118500.00 | BR Power Control and Automation Services
2.00 | Supply, Erection, Testing and Commissioning of hot dipped galvanized octagonal Street light pole of 7 metre long made out of 3mm thick sheet having top dia 70 mm and bottom dia 130 mm with single arm of size 1 metre complete with 12 mm thick MS sheet base plate of size 220 mm X 220 mm i/c stiffner and 04 Nos. foundation bolts of size 20 mm dia and 750 mm long and door provision of size 75 x 400mm for cable entry as per techincal specification including errection on the existing CC pedestal etc complete as required. The pole shall be installed in RCC foundation 1:2:4 (i.e 1 cement : 2 coarse sand: 4 graded stone) of size 500 x 500 x 1000 mm including excavation & refilling in soil/hard rock/concrete with the help of breaker machine by laying iron barmesh fabricated with 8 mm, 10 mm & 12 mm dia iron bar as per the manufacturer design complete as required. (cost of the foundation to be included in the item) | 10.00 | Job |  | 14000.00 | 140000.00 | 12000.00 | 120000.00 | 15000.00 | 150000.00 | 10000.00 | 100000.00 | 100000.00 | D.D.METAL CORPORATION
3.00 | Supply of outdoor type antiglare LED flood light fixture with lumen output ≥ 38000 lm, maximum power consumption not more than 400W and minimum lifetime of 50000 burning hours and having aesthetically designed single piece pressure die cast extruded aluminium/aluminium alloy housing, heat sink with general spread optics having IP-66 including accessories such as LED of approved make, electronic gear/driver with surge voltage, open/short circuit protections and power factor correction facility, suitable for mounting on carriage of High Mast lighting tower and on operating voltage of 140 V to 280 V AC and frequency 50Hz +/-5% etc. complete as per approved makes & enclosed technical specifications. | 16.00 | Each |  | 15400.00 | 246400.00 | 20800.00 | 332800.00 | 17000.00 | 272000.00 | 17000.00 | 272000.00 | 246400.00 | North Eastern Engineers
4.00 | Supply of Pole mountable outdoor type 120Watt ± 10% (nominal) LED street light fixture with minimum lumens output of 11400 lumens, minimum lifetime of 50000 burning hours and having aesthetically designed pressure die cast extruded aluminium/ aluminium alloy housing, heat sink with general spread optics having IP-66 including accessories such as LED of approved make, electronic gear/ driver with surge voltage, open/ short circuit protections and power factor correction facility suitable for operation on 140 V to 280 V AC and frequency 50Hz +/-5% etc. complete as per approved makes & enclosed technical specifications. | 12.00 | Each |  | 4180.00 | 50160.00 | 6458.00 | 77496.00 | 6000.00 | 72000.00 | 5200.00 | 62400.00 | 50160.00 | North Eastern Engineers
5.00 | Supply of "Integral LED Aviation Obstruction Light fitting" comprising of aluminium housing with polycarbonate encloser, heat sink, driver, surge protection system and suitable for mounting on carriage of High Mast lighting tower along with mounting pipe, clamps, connections etc. complete as per site requirements. | 1.00 | Each |  | 3843.00 | 3843.00 | 2800.00 | 2800.00 | 6500.00 | 6500.00 | 5000.00 | 5000.00 | 2800.00 | BR Power Control and Automation Services
6.00 | Installation, Testing & Commissioning of 16M high mast system complete with all accessories including construction of shallow foundation with M20 grade concrete for the highmast considering the safe soil bearing capacity at site as 10 T/sqmtr at 2 metre depth with all materials and labour as per manufacturers recomendations along with fixing of foundation bolts, trailing cable with plug and GT connector, installation of LED Flood Light luminiaries, LED Aviation obstruction light & its wiring, necessary wiring from junction box to indiviual luminaire & MCB in base compartment with all required accessories, terminations, connection etc. complete as required as per site requirement. | 1.00 | Job |  | 72000.00 | 72000.00 | 96530.00 | 96530.00 | 80000.00 | 80000.00 | 111000.00 | 111000.00 | 72000.00 | North Eastern Engineers
7.00 | Supply and fixing of side hinged-door fixed with base SMC junction Box of size 250mmx200mmx100mm (Loop-in-Loop-out Box) on the GI pole with suitable size MS clamp including providing & fixing 63A, 4Pole connector (for loop in & loop out to terminate 2Nos, 4 core 25 sq. mm. armoured aluminum cable) and 6Amp SP MCB 'C' curve in din rail, Interconnection etc. as required. (Make: Sintex: model no. JS-JB-2520 or its equivalent) | 13.00 | Nos. |  | 1000.00 | 13000.00 | 890.00 | 11570.00 | 1200.00 | 15600.00 | 1600.00 | 20800.00 | 11570.00 | BR Power Control and Automation Services
8.00 | Erection of LED street light fitting on existing pole of height upto 10mtr. from ground level including supplying and drawing three core 1.5 sq.mm FR PVC insulated copper conductor cable in the pole from fitting to pole junction box including connection, testing and commissioning etc. complete as required. | 12.00 | Nos. |  | 200.00 | 2400.00 | 710.00 | 8520.00 | 500.00 | 6000.00 | 1500.00 | 18000.00 | 2400.00 | North Eastern Engineers
9.00 | Feeder Pillar (HIGH MAST PANEL) Supply, Installation, Testing and commissioning of double door, weather proof, fully compartmentalised, free standing type, duly painted outdoor type feeder pillar/control cum power panel (IP 55 protection) fabricated from 2mm thick CRCA sheet and having 32 Amps TPN MCB Incomer, Single dial time Switch, 25 Amps TP Contactors for automatic switching of luminaires, two nos of power contactoros (25 Amps) and ON/OFF push buttons for lowering and raising of lantern carriage of high mast, suitable sizes power and control wirings, mounting legs (600 mm ), foundation connectors for power and control cables, R-Y-B indication lamps with control MCBs, power & control wiring and other required controls, switchgears and accessories required for satisfactory operation of high mast lighting tower. | 1.00 | Job |  | 52000.00 | 52000.00 | 22500.00 | 22500.00 | 75000.00 | 75000.00 | 24000.00 | 24000.00 | 22500.00 | BR Power Control and Automation Services
10.00 | Feeder Pillar Design, fabrication, supply, installation, testing and commissioning of double door, weather proof, dust & vermin proof, duly painted, fully compartmentalised free standing type outdoor type feeder pillar (with IP55 protection) fabricated from 2mm thick CRCA sheet including supply and fixing of following switch gears and accessories complete with bus bars, neutral link, interconnections, CTs, Ammeter and Voltmeter with selector switches and LED phase indicating lamps as required as per enclosed specifications and approved make.: Incoming: (i) 63A, 25KA (Ics=100%Icu) thermal magnetic release type TP MCCB with suitable size Spreader terminals in both end for cable termination, Direct rotary operating mechanism and having over load and short ckt. protections - 1 No. (ii) 3- Phase, 4 wire operation Digital Voltmeter with LED display, slector switch and protection fuses/MCBs- 1 No. (iii) Digital Amps meter with LED display,Slector Switch with 3 Nos of class 1.0, 5 VA CTs- 1 No. (iv) LED Type R-Y-B indication lamps- 1 set. Busbar 200 Amps TP& N high conducting aluminium bus bars- 1 Set. Outgoing: (i) 32A, 10KA, C curve DP MCB- 6 Nos. (Feeder Pillar should be PTTA type only) | 1.00 | Job |  | 72000.00 | 72000.00 | 38000.00 | 38000.00 | 70000.00 | 70000.00 | 30000.00 | 30000.00 | 30000.00 | D.D.METAL CORPORATION
11.00 | Supply of following size XLPE insulated PVC sheathed Aluminium conductor armoured power cable of 1.1 KV grade confirming to IS 7098 (Part-I) with up to date ammendment etc. complete as required.
11.01 | 3.5C x 50 sq. mm. | 250.00 | Mtrs. |  | 234.00 | 58500.00 | 215.00 | 53750.00 | 235.00 | 58750.00 | 280.00 | 70000.00 | 53750.00 | BR Power Control and Automation Services
11.02 | 3.5C x 35 sq. mm. | 350.00 | Mtrs. |  | 180.00 | 63000.00 | 166.00 | 58100.00 | 172.00 | 60200.00 | 187.00 | 65450.00 | 58100.00 | BR Power Control and Automation Services
11.03 | 4C x 16 sq. mm. | 950.00 | Mtrs. |  | 124.00 | 117800.00 | 110.00 | 104500.00 | 114.00 | 108300.00 | 120.00 | 114000.00 | 104500.00 | BR Power Control and Automation Services
12.00 | Supply of 50mm dia.(O.D.) HDPE pipe (High Density Polyethylene) of grade PE80, PN6 ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984:1995 with latest ammendments complete as required. | 550.00 | Mtrs. |  | 100.00 | 55000.00 | 90.00 | 49500.00 | 110.00 | 60500.00 | 170.00 | 93500.00 | 49500.00 | BR Power Control and Automation Services
13.00 | Laying of DWC/HDPE pipe (High Density Polyethylene) of 50mm dia. direct in ground up to a depth of 75 cm including excavation and refilling the trench complete with fitting, cutting and jointing etc. as required. | 260.00 | Mtrs. |  | 40.00 | 10400.00 | 120.00 | 31200.00 | 250.00 | 65000.00 | 200.00 | 52000.00 | 10400.00 | North Eastern Engineers
14.00 | Laying of DWC/HDPE pipe (High Density Polyethylene) of 50mm dia. direct in ground up to a depth of 45 cm under hard/concrere/bituminous surface including breaking of all type of surface and repairing the same with providing and laying 100mm thick in position cement concrete of 1:3:6 ( i.e 1 cement: 3 coarse sand: 6 graded stone) including refilling the trench complete as required. | 290.00 | Mtrs. |  | 120.00 | 34800.00 | 220.00 | 63800.00 | 400.00 | 116000.00 | 300.00 | 87000.00 | 34800.00 | North Eastern Engineers
15.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
15.01 | Upto 35 sq. mm | 540.00 | Mtrs. |  | 35.00 | 18900.00 | 32.00 | 17280.00 | 50.00 | 27000.00 | 120.00 | 64800.00 | 17280.00 | BR Power Control and Automation Services
15.02 | Above 35 sq. mm and upto 95 sq. mm | 30.00 | Mtrs. |  | 45.00 | 1350.00 | 51.00 | 1530.00 | 60.00 | 1800.00 | 120.00 | 3600.00 | 1350.00 | North Eastern Engineers
16.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray/ surface as required.
16.01 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 760.00 | Mtrs. |  | 35.00 | 26600.00 | 33.00 | 25080.00 | 50.00 | 38000.00 | 100.00 | 76000.00 | 25080.00 | BR Power Control and Automation Services
16.02 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 220.00 | Mtrs. |  | 45.00 | 9900.00 | 51.00 | 11220.00 | 60.00 | 13200.00 | 120.00 | 26400.00 | 9900.00 | North Eastern Engineers
17.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.
17.01 | 3.5C x 50 sq.mm. | 2.00 | Each |  | 104.00 | 208.00 | 750.00 | 1500.00 | 300.00 | 600.00 | 300.00 | 600.00 | 208.00 | North Eastern Engineers
17.02 | 3.5 x 35 sq. mm. | 2.00 | Each |  | 104.00 | 208.00 | 550.00 | 1100.00 | 250.00 | 500.00 | 200.00 | 400.00 | 208.00 | North Eastern Engineers
17.03 | 4C x 16 sq. mm. | 30.00 | Each |  | 108.00 | 3240.00 | 410.00 | 12300.00 | 250.00 | 7500.00 | 150.00 | 4500.00 | 3240.00 | North Eastern Engineers
18.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 2.00 | Each |  | 11700.00 | 23400.00 | 19632.00 | 39264.00 | 7000.00 | 14000.00 | 8000.00 | 16000.00 | 14000.00 | SHREE GOURI ELECTRIC ENTERPRISE
19.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Mtrs. |  | 207.00 | 4140.00 | 145.00 | 2900.00 | 550.00 | 11000.00 | 600.00 | 12000.00 | 2900.00 | BR Power Control and Automation Services
20.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 20.00 | Mtrs. |  | 117.00 | 2340.00 | 140.00 | 2800.00 | 120.00 | 2400.00 | 150.00 | 3000.00 | 2340.00 | North Eastern Engineers
21.00 | Earthing with G.I. earth pipe 4.5 meter long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2.00 | Each |  | 10800.00 | 21600.00 | 1100.00 | 2200.00 | 6000.00 | 12000.00 | 9000.00 | 18000.00 | 2200.00 | BR Power Control and Automation Services
22.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 20.00 | Mtrs. |  | 54.00 | 1080.00 | 32.00 | 640.00 | 265.00 | 5300.00 | 300.00 | 6000.00 | 640.00 | BR Power Control and Automation Services
23.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 400.00 | Mtrs. |  | 10.00 | 4000.00 | 35.00 | 14000.00 | 20.00 | 8000.00 | 21.00 | 8400.00 | 4000.00 | North Eastern Engineers
| Total in Figures |  |  |  |  | 1243269.00 |  | 1321380.00 |  | 1487150.00 |  | 1520850.00
Lowest Amount Quoted BY: North Eastern Engineers(1243269.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of High mast lighting tower in Old apron area near Cargo gate and Street lights at Airline bus parking area at LGBI Airport, Guwahati Tender ID: 2020_AAI_64860_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | North Eastern Engineers | 1243269.00 | L1
| 2 | BR Power Control and Automation Services | 1321380.00 | L2
| 3 | SHREE GOURI ELECTRIC ENTERPRISE | 1487150.00 | L3
| 4 | D.D.METAL CORPORATION | 1520850.00 | L4