## BoQ1
Government eProcurement System Created By: Ashvin Kumar Singh Created Date/Time: 12-Jan-2021 04:38 PM Tender Title: Provision of Ground Lighting Facility for Southern Link Taxi at Chandigarh International Airport, Mohali. Tender ID: 2020_AAI_64965_1
Tender Inviting Authority: Asstt. General Manager (Engg- Elect.), Chandigarh International Airport Ltd.(CHIAL), Mohali (PB)
Name of Work: Provision of Ground Lighting Facility for Southern Link Taxi at Chandigarh International Airport, Mohali.
Contract No: 0172-2242404, 0172-2242434
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Vardhman Airport Solutions Pvt Ltd(GSTN-07AAECN5914F1ZK) |  | AMA Private Limited(GSTN-27AAACA1016F1ZE) |  | Sai Avionics(GSTN-07ADHFS8725N1ZC)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of FAA certified LED type inset Bi-directional fitting for aviation visual aid at Taxiway center line suitable for straight section/ straight section (Off set) / curved section complete with LED, shallow base & matching body, single plug, inner & outer cover complete with other accessories, ready for site installation suitable for 6.6A etc. as required. Bi-directional green/green. | 135.00 | Each | 100.00 | 29000.00 | 3915000.00 | 43000.00 | 5805000.00 | 42500.00 | 5737500.00 | 3915000.00 | Vardhman Airport Solutions Pvt Ltd
2.00 | Supply of FAA certified LED type inset Bi-directional fitting for aviation visual aid at Taxiway center line suitable for curved section complete with LED, shallow base & matching body, single plug, inner & outer cover complete with other accessories, ready for site installation suitable for 6.6A etc. as required. Bi-directional green/yellow. | 12.00 | Each | 100.00 | 29500.00 | 354000.00 | 42500.00 | 510000.00 | 42000.00 | 504000.00 | 354000.00 | Vardhman Airport Solutions Pvt Ltd
3.00 | Supply of elevated type Omni- directional, medium intensity LED Taxiway Edge Light fitting suitable for Taxiway, Apron Edge Lights, Turning Pad Lights for operation at 6.6 Amps, series circuit supply, complete with Omni-directional Blue lens, Lens clamping mechanism, breakable coupling, gasket, two pin secondary leads, base plate with 06 No's, M - 10 stainless steel bolts and other accessories including White LED with an integrated encapsulated electronic module as required conforming the manufactures who meet ICAO requirement for ISO CANDELA as specififed in Annexure- 14. Omni- directional Blue | 106.00 | Each | 10.00 | 4000.00 | 424000.00 | 4100.00 | 434600.00 | 4250.00 | 450500.00 | 424000.00 | Vardhman Airport Solutions Pvt Ltd
4.00 | Supply of FAA certified LED type Inset Omni-directional fitting for aviation visual aid at taxiway line suitable for curved section complete with LED, shallow base & matching body, single plug, inner & outer cover complete with other accessories, ready for site installation suitable for 6.6A etc. as required. Omni- directional Blue | 20.00 | Each | 100.00 | 27500.00 | 550000.00 | 42500.00 | 850000.00 | 30000.00 | 600000.00 | 550000.00 | Vardhman Airport Solutions Pvt Ltd
5.00 | Supply of FAA certified LED type Inset Uni-directional Stop Bar fitting for aviation visual aid at Rapid taxiway line suitable for curved section complete with LED, shallow base & matching body, single plug, inner & outer cover complete with other accessories, ready for site installation suitable for 6.6A etc. as required. Uni-directional Stop Bar Fitting Red. | 11.00 | Each | 100.00 | 29500.00 | 324500.00 | 38000.00 | 418000.00 | 35000.00 | 385000.00 | 324500.00 | Vardhman Airport Solutions Pvt Ltd
6.00 | Supply of Indoor type air cooled constant current regulator of micro processor controlled, thristor type suitable for operation on 230/415 volts, 50Hz input AC supply with 6.6A output having 5 steps variation of current output and able to communicate with PC or PLC controlled system, with digital output ammeter (0-10A), overcurrent, overvoltage, open circuit and earth fault protection and earth leakage meter, two stage earth leakage detector, positive back indication equipment's, individual lamp control and monitoring system module, hours run counter, LCD display, complete as required for the following rating and confirm to specifications enclosed. 2.5 kw | 1.00 | Each | 100.00 | 130000.00 | 130000.00 | 125000.00 | 125000.00 | 150000.00 | 150000.00 | 125000.00 | AMA Private Limited
7.00 | Supply of Indoor type air cooled constant current regulator of micro processor controlled, thristor type suitable for operation on 230/415 volts, 50Hz input AC supply with 6.6A output having 5 steps variation of current output and able to communicate with PC or PLC controlled system, with digital output ammeter (0-10A), overcurrent, overvoltage, open circuit and earth fault protection and earth leakage meter, two stage earth leakage detector, positive back indication equipment's, individual lamp control and monitoring system module, hours run counter, LCD display, complete as required for the following rating and confirm to specifications enclosed. 4 kw | 4.00 | Each | 100.00 | 140000.00 | 560000.00 | 138000.00 | 552000.00 | 160000.00 | 640000.00 | 552000.00 | AMA Private Limited
8.00 | Supply of 5 kV Type C without metallic screen, Cross-linked polyethylene 6 Sqmm unshielded round stranded bare copper class 2 with Polyethylene (PE) outer sheath cable as required as per the technical specification. UN-SHIELDED PRIMARY CABLE 1CX 6SQ MM | 40300.00 | Metre | 10.00 | 68.00 | 2740400.00 | 68.00 | 2740400.00 | 61.00 | 2458300.00 | 2458300.00 | Sai Avionics
9.00 | Supply of 2X4 Sq.mm secondary lead made out of multi stranded copper conductor, EPR insulated PCP sheathed, anti termite & anti rodent treated 600V grade cable as specified in particular specification and as required. | 4700.00 | Metre | 100.00 | 93.00 | 437100.00 | 100.00 | 470000.00 | 95.00 | 446500.00 | 437100.00 | Vardhman Airport Solutions Pvt Ltd
10.00 | Supply of 6 Sqmm Plug of type I, class B connector & suitable field attachment with 5 KV grade XLPE insulated PE sheathed single core screened copper conductor cable as required. | 380.00 | Each | 100.00 | 165.00 | 62700.00 | 180.00 | 68400.00 | 200.00 | 76000.00 | 62700.00 | Vardhman Airport Solutions Pvt Ltd
11.00 | Supply of 6 Sqmm Receptacle of type I, class B connector & suitable field attachment with 5 KV grade XLPE insulated PE sheathed single core screened copper conductor cable as required. | 175.00 | Each | 100.00 | 165.00 | 28875.00 | 200.00 | 35000.00 | 200.00 | 35000.00 | 28875.00 | Vardhman Airport Solutions Pvt Ltd
12.00 | Supply of 5 KV, 6.6 A/6.6 A, 50 Hz rubber encapsulated isolating transformer suitable for individual series lamps airport lighting circuits. The transformer shall be designed to be water proof and suitable for direct burial in the earth or installation in a base, conforming to IS:12290 (latest edition) with up to amendments complete as per specifications attached. 15 watts, 6.6A/6.6A | 130.00 | Each | 100.00 | 2250.00 | 292500.00 | 2300.00 | 299000.00 | 2150.00 | 279500.00 | 279500.00 | Sai Avionics
13.00 | Supply of 5 KV, 6.6 A/6.6 A, 50 Hz rubber encapsulated isolating transformer suitable for individual series lamps airport lighting circuits. The transformer shall be designed to be water proof and suitable for direct burial in the earth or installation in a base, conforming to IS:12290 (latest edition) with up to amendments complete as per specifications attached. 45 watts, 6.6A/6.6A | 150.00 | Each | 10.00 | 2520.00 | 378000.00 | 2800.00 | 420000.00 | 2700.00 | 405000.00 | 378000.00 | Vardhman Airport Solutions Pvt Ltd
14.00 | Supply of 5 KV, 6.6 A/6.6 A, 50 Hz rubber encapsulated isolating transformer suitable for individual series lamps airport lighting circuits. The transformer shall be designed to be water proof and suitable for direct burial in the earth or installation in a base, conforming to IS:12290 (latest edition) with up to amendments complete as per specifications attached. 100 watts, 6.6A/6.6A | 12.00 | Each | 100.00 | 3500.00 | 42000.00 | 3800.00 | 45600.00 | 3700.00 | 44400.00 | 42000.00 | Vardhman Airport Solutions Pvt Ltd
15.00 | Supply of 40 mm dia HDPE pipe (Outer Dia) PE-80 grade, PN-6, minimum wall thickness 3.0 mm suitable for laying cable complete as required as per technical specifications. | 17700.00 | Metre | 100.00 | 47.00 | 831900.00 | 46.00 | 814200.00 | 36.00 | 637200.00 | 637200.00 | Sai Avionics
16.00 | Supply of 32 mm dia HDPE pipe (Outer Dia) PE-80 grade, PN-6, minimum wall thickness 2.4 mm suitable for laying cable complete as required as per technical specifications | 2300.00 | Metre | 100.00 | 33.00 | 75900.00 | 35.00 | 80500.00 | 35.00 | 80500.00 | 75900.00 | Vardhman Airport Solutions Pvt Ltd
17.00 | Supply of following size of 1.1KV grade multicore stranded aluminium conductor XLPE insulated & PVC sheathed armoured cable (FRLS Type) as per IS: 7098 (Part-1) 1988 complete as required & as per enclosed specification. (4C x 10 Sqmm) | 500.00 | Metre | 100.00 | 80.00 | 40000.00 | 105.00 | 52500.00 | 150.00 | 75000.00 | 40000.00 | Vardhman Airport Solutions Pvt Ltd
18.00 | Supply of 3.5 core 95 sq.mm size heavy duty XLPE insulated PVC sheathed aluminium conductor armoured power cable of 1.1KV grade confirming to IS 7098, Part-I 1988 with up to date amendments and confirm to particular specifications enclosed in the tender. | 100.00 | Metre | 100.00 | 300.00 | 30000.00 | 375.00 | 37500.00 | 200.00 | 20000.00 | 20000.00 | Sai Avionics
19.00 | Supply of C.I. Isolating Transformer housing box, water tight round type, metal container of outside size 330mm height 450mm made of 10mm thick cast iron moulding suitable to receive a light fitting base plate on the top and underground housing associated with transformer power cable and having a clear hole at 75 mm above bottom surface suitable to receive two nos. of 40mm dia HDPE pipe (As per the site requirement) and also 01 no. of hole for 32 mm dia HDPE pipe at a approx. depth of 100 mm from the top including check nuts as required and another hole at 175mm from the bottom of the CI Box to receive one no. 15mm dia "B" class GI pipe and check nut as required.The box should have two SS earth bolts of M10 x 30mm tapped inside near the hole (4" away from the hole centre) and having a drain hole at the bottom suitably tapped to receive 15mm dia "B" class GI pipe and having clear opening of 220 mm at the top surface and 6 nos. M10 tapped hole at the hole centre 260 mm to receive fitting base plate and bolts complete as required. | 106.00 | Each | 100.00 | 4100.00 | 434600.00 | 4100.00 | 434600.00 | 3900.00 | 413400.00 | 413400.00 | Sai Avionics
20.00 | Supply of CI Base plate of size 15 mm thick and outside dia 330 mm, surface suitable to receive a light fitting-base plate on the top and having a clear opening of 220 mm hole centre and 6 nos of holes tapped to receive M-10 stainless steel bolts as per drawing as required. | 24.00 | Each | 100.00 | 1000.00 | 24000.00 | 900.00 | 21600.00 | 1400.00 | 33600.00 | 21600.00 | AMA Private Limited
21.00 | Supply of MS blanking/blind plate of outside dia 330 mm, 10 mm thick and having 6 nos holes tapped to receive M-10 stainless steel bolts for use with CI Box including supplying of 6 nos M-10 stainless steel bolts. | 82.00 | Each | 100.00 | 650.00 | 53300.00 | 700.00 | 57400.00 | 800.00 | 65600.00 | 53300.00 | Vardhman Airport Solutions Pvt Ltd
22.00 | Supply, installation, testing and commissioning of LED Guidance Sign Board of various sizes as per ICAO Annex.14 Vol.I (legends as approved by Engineer-in-Charge) made out of anodized 2mm thick Aluminum frame with suitable angle support with 1.5MM thick (minimum) Al. back cover, 4 MM thick polycarbonate sheet with glare free face, the letter & symbol should be screen printed on inside of sign face made of self adhesive film of 3M applied on the inside face with required coloring, suitable arrangement shall be made for water tightness & locking arrangement, signboard shall be uniformly internally illuminated with LED lights with 24 V DC converter to achieve illumination level operated on input source 2.5A to 6.6A constant current without flickering including supporting frangible legs & frame etc. complete as required and as specified. | 15.00 | Sq. Mtr. | 100.00 | 30000.00 | 450000.00 | 36000.00 | 540000.00 | 31000.00 | 465000.00 | 450000.00 | Vardhman Airport Solutions Pvt Ltd
23.00 | Installation, testing and commissioning of following Inset fittings with core drilling, aligning & setting including providing sealing material & installation of isolating transformers, crimping / joining of plug & receptacles and moulding the leads, connections etc. as required. | 166.00 | Job | 10.00 | 4000.00 | 664000.00 | 5500.00 | 913000.00 | 4000.00 | 664000.00 | 664000.00 | Vardhman Airport Solutions Pvt Ltd, Sai Avionics
24.00 | Installation, testing and commissioning of elevated taxiway fittings aligning, on the existing transformer housing box i/c. installation of transformer, lens and other accessories, alignment, levelling etc. as required, sealing material, installation of isolating transformer etc. as required. | 96.00 | Job | 100.00 | 50.00 | 4800.00 | 150.00 | 14400.00 | 100.00 | 9600.00 | 4800.00 | Vardhman Airport Solutions Pvt Ltd
25.00 | Installation, testing & commissioning of 2.5 / 4 KW microprocessor controlled CCRs including providing earth connection with GI strip of size 25mm x 5mm, all necessary arrangement, end termination with plug and recepticle etc. for commissioning of CCR etc. as required. | 5.00 | Job | 100.00 | 2000.00 | 10000.00 | 9000.00 | 45000.00 | 5000.00 | 25000.00 | 10000.00 | Vardhman Airport Solutions Pvt Ltd
26.00 | Making field connections of 5 KV grade 6 Sq.mm PVC / XLPE insulated PVC sheathed copper conductor single core cable with 5 KV grade plug/ receptacle suitable for field attachment with HT tape complete as required. | 508.00 | Each | 100.00 | 50.00 | 25400.00 | 100.00 | 50800.00 | 20.00 | 10160.00 | 10160.00 | Sai Avionics
27.00 | Installation, Testing and Commissioning of 5 KV, 6.6 A/6.6 A, 50 Hz rubber encapsulated isolating transformer suitable for individual series lamps airport lighting circuits including HT tape etc complete as required. 15/45/100 watts, 6.6A/6.6A | 264.00 | Each | 100.00 | 50.00 | 13200.00 | 100.00 | 26400.00 | 20.00 | 5280.00 | 5280.00 | Sai Avionics
28.00 | Earthing with GI earth pipe 4.5 m long and 40mm dia, accessories and providing masonary enclosure with cover plate on the top having locking arrangement and watering pipe, complete with charcoal and salt etc. as required. | 10.00 | Each | 10.00 | 4500.00 | 45000.00 | 6500.00 | 65000.00 | 4000.00 | 40000.00 | 40000.00 | Sai Avionics
29.00 | Providing & laying of 6 SWG dia GI wire in the existing pipe/duct/ HDPE etc. as required. | 6000.00 | Metre | 100.00 | 18.00 | 108000.00 | 12.00 | 72000.00 | 12.00 | 72000.00 | 72000.00 | AMA Private Limited, Sai Avionics
30.00 | Laying of HDPE pipe (Size from 32mm to 40mm) by excavation /cutting soft soil upto 80cm, connecting both/one end to existing transformer housing box/Chambers with all assessories like sockets,T, bend, couplers etc. complete with fitting cutting and jointing etc. i/c refilling and making good the damages etc. as required as per specification. | 17700.00 | Metre | 100.00 | 80.00 | 1416000.00 | 70.00 | 1239000.00 | 55.00 | 973500.00 | 973500.00 | Sai Avionics
31.00 | Laying of HDPE pipe (Size from 32mm to 40mm) by cutting bituminous/concrete surface upto required depth as per site, connecting both/one end to existing transformer housing box, with all accessories, like socket, bend, coupler etc as required i/c refilling and making good the damages by proper sealent materials etc. as required as per specification. | 2300.00 | Metre | 100.00 | 130.00 | 299000.00 | 250.00 | 575000.00 | 150.00 | 345000.00 | 299000.00 | Vardhman Airport Solutions Pvt Ltd
32.00 | Laying of HDPE Pipe (Size from 32mm to 40mm) in the existing masonry open duct as required. | 200.00 | Metre | 100.00 | 15.00 | 3000.00 | 20.00 | 4000.00 | 20.00 | 4000.00 | 3000.00 | Vardhman Airport Solutions Pvt Ltd
33.00 | Laying of one no. PVC insulated & PVC sheathed AFL cable of 5 KV grade size upto 25 sqmm in the existing RCC/ METAL/HDPE/Open Trench pipe as required. | 45000.00 | Metre | 100.00 | 15.00 | 675000.00 | 12.00 | 540000.00 | 9.00 | 405000.00 | 405000.00 | Sai Avionics
34.00 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand) with R.C.C. top slab with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4coarse sand : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design: Inside size 120x90 cm and 90 cm deep including C.I. cover with frame (heavy duty) 560 mm internal diameter, total weight of cover and frame to be not less than 208 kg (weight of cover 108 kg and weight of frame 100 kg) | 25.00 | Each | 100.00 | 14500.00 | 362500.00 | 14000.00 | 350000.00 | 5000.00 | 125000.00 | 125000.00 | Sai Avionics
35.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. (Upto 35 sq. mm) | 500.00 | Metre | 100.00 | 14.00 | 7000.00 | 15.00 | 7500.00 | 20.00 | 10000.00 | 7000.00 | Vardhman Airport Solutions Pvt Ltd
36.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required Above 35 sq. mm and upto 95 sq. mm | 40.00 | Metre | 100.00 | 200.00 | 8000.00 | 300.00 | 12000.00 | 260.00 | 10400.00 | 8000.00 | Vardhman Airport Solutions Pvt Ltd
37.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Above 35 sq. mm and upto 95 sq. mm | 60.00 | Metre | 10.00 | 14.00 | 840.00 | 15.00 | 900.00 | 20.00 | 1200.00 | 840.00 | Vardhman Airport Solutions Pvt Ltd
38.00 | Installation of Transformer housing boxes by excavation of earth upto depth of 525 mm with a base concrete of 1:3:6 of size 630x630x100 mm thick, all round concrete of 1:2:4, 150mm thick,the top sloped with 1:2:4 cement concrete including providing and fixing 250 mm long 15mm dia "B" class GI pipe with check nut for drainage of water complete as required as per the technical specification. (wherever the transformers boxes are to be installed in a line, the same has to be aligned in such a way that the centre fall in a straight line) etc. complete as required. | 106.00 | Each | 100.00 | 1600.00 | 169600.00 | 2500.00 | 265000.00 | 1000.00 | 106000.00 | 106000.00 | Sai Avionics
39.00 | Installation of CI Base plate (complete with all accessories) of size 15 mm thick and outside dia 330 mm complete with all accessories as required . | 24.00 | Each | 100.00 | 20.00 | 480.00 | 75.00 | 1800.00 | 50.00 | 1200.00 | 480.00 | Vardhman Airport Solutions Pvt Ltd
40.00 | Installation of MS blanking/blind plate (complete with all accessories) of outside dia 330 mm complete with all accessories as required. | 82.00 | Each | 100.00 | 20.00 | 1640.00 | 75.00 | 6150.00 | 50.00 | 4100.00 | 1640.00 | Vardhman Airport Solutions Pvt Ltd
| Total in Figures |  |  |  |  | 15992235.00 |  | 18999250.00 |  | 16813440.00
Lowest Amount Quoted BY: Vardhman Airport Solutions Pvt Ltd(15992235.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Ground Lighting Facility for Southern Link Taxi at Chandigarh International Airport, Mohali. Tender ID: 2020_AAI_64965_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Vardhman Airport Solutions Pvt Ltd | 15992235.00 | L1
| 2 | Sai Avionics | 16813440.00 | L2
| 3 | AMA Private Limited | 18999250.00 | L3