## BoQ1
Government eProcurement System Created By: D Boominathan Created Date/Time: 11-Jan-2021 06:35 PM Tender Title: Provision of Simple Approach Lighting system (SALS) in Runway 09, Perimeter wall lighting for newly acquired land at Trichy Airport Tender ID: 2020_AAI_65353_1
Tender Inviting Authority: Assistant General Manager (E-E)
Name of Work: Provision of Simple approach lighting system (SALS) in Runway 09, Perimeter wall lighting for newly acquired land at Trichy Airport
Contract No: CW-06/TRY/20-21 Tender ID: 2020_AAI_65353_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Techno Electricals(GSTN-24AAGFT9086M1ZG) |  | Balaji Engineering(GSTN-33ADGPV2628A1ZV) |  | AMA Private Limited(GSTN-27AAACA1016F1ZE)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of Unidirectional Elevated Type High Intensity Approach Light Fitting suitable for use with 200W 6.6A halogen lamp complete with prefocus lamp holder, 200 watt 6.6 A halogen lamp , lens / spreader glass, lens holding mechanisam, reflector assembley, elevation and horizontal adjustment mechanisam, breakable coupling , central column mounting assembly, gaskets, two pin secondary lead plug suitable for connection with isolating transformer, base plate with 6 nos. M-10 stainless steel bolts, spring & plain washers & other accessories etc. and confirming to particular specification with Clear Lense (suitable for Approach Centerline) including lamp etc. as required to meet latest ICAO requirement. (Make: As per AAI list of approved makes) | 20.00 | Each |  | 12545.00 | 250900.00 | 11000.00 | 220000.00 | 8750.00 | 175000.00 | 175000.00 | AMA Private Limited
2.00 | Supply of Inset Type Uni Directional Runway End Light Fitting with clear lens / red filter complete with bottom box and all accessories including 6.6A pre-focused reflector 2 X105W halogen lamp with connected heat resistant accessories prism assembly, optical assembly, "O" ring seal pressure relief test plug gas kit cover complete with all other accessories as per ICAO specification etc. as required and as specified. (Make: As per AAI list of approved makes) | 12.00 | Each |  | 57250.00 | 687000.00 | 60000.00 | 720000.00 | 55467.92 | 665615.04 | 665615.04 | AMA Private Limited
3.00 | Supply of Inset Type Bi-directional Runway edge Light Fitting with clear lens / yellow filter complete with bottom box and all accessories including 6.6A pre-focused reflector 2 X 105W halogen lamp with connected heat resistant accessories prism assembly, optical assembly, "O" ring seal pressure relief test plug gas kit cover complete with all other accessories as per ICAO specification etc. as required and as specified. (Make: As per AAI list of approved makes) | 4.00 | Each |  | 57250.00 | 229000.00 | 60000.00 | 240000.00 | 59999.94 | 239999.76 | 229000.00 | Techno Electricals
4.00 | Supply of Inset Type Uni Directional Approach Centreline Light Fitting with clear lens /clear filter complete with bottom box and all accessories including 6.6A pre-focused reflector 2 X 105W halogen lamp with connected heat resistant accessories prism assembly, optical assembly, "O" ring seal pressure relief test plug gas kit cover complete with all other accessories as per ICAO specification etc. as required and as specified. (Make: As per AAI list of approved makes) | 2.00 | Each |  | 57000.00 | 114000.00 | 60000.00 | 120000.00 | 68022.85 | 136045.70 | 114000.00 | Techno Electricals
5.00 | Supply of following capcaity 5 KV grade 50 Hz series type isolating transformers, encapsulated in polyester resin, finally moulded with neoprene type rubber with primary and secondary connections meeting ICAO requirement as per IS/IEC etc. complete as required. (Secondary lead should be suitable for plug in connection to the secondary lead of the fittings offered) (Make: As per AAI list of approved makes) i) 200 Watt, 6.6A / 6.6A | 46.00 | Each |  | 4500.00 | 207000.00 | 4500.00 | 207000.00 | 4300.00 | 197800.00 | 197800.00 | AMA Private Limited
6.00 | Supply of following size 5 KV grade dry type Plug and Receptacle of type I, class 'B' primary connector kit with field attachment and suitable for 5 KV grade single core copper conductor, copper braided, XLPE insulated PE outer sheathed shielded cable, complete as required confirming to the technical specification. (Make: As per AAI list of approved makes) i) 6sq.mm | 65.00 | Each |  | 475.00 | 30875.00 | 350.00 | 22750.00 | 380.00 | 24700.00 | 22750.00 | Balaji Engineering
7.00 | Supply of following capacity Indoor Type Air Cooled Constant Current Regulator (CCR) of Micro Processor Controlled, Thyristor Type suitable for operation on single phase 230V / 2-phase 400V AC + PE ± 10%, 50 Hz input AC supply with 5 steps variation of current output (2.8, 3.4, 4.0, 5.2 and 6.6 Amp) and able to communicate with PC or PLC controlled system with digital output ammeter (0-10 Amps), over current, over voltage, open circuit and earth fault protection and earth leakage meter, two stage earth leakage detector, positive back indication equipments, hours run counter, LCD display complete as required and confirm to specifications enclosed and suitable for operation on the existing Airfield Lighting Control and Monitoring System (ALCMS) with communication, local and remote control and monitoring even and data recording and history keeping etc complete as required. (Make: As per AAI list of approved makes)
7.01 | 7.5 kW CCR | 1.00 | Each |  | 275250.00 | 275250.00 | 250000.00 | 250000.00 | 195000.00 | 195000.00 | 195000.00 | AMA Private Limited
7.02 | 4 kW CCR | 1.00 | Each |  | 250000.00 | 250000.00 | 175000.00 | 175000.00 | 150000.00 | 150000.00 | 150000.00 | AMA Private Limited
8.00 | Supply of 1 X6 Sqmm, 5 KV grade single core, stranded copper conductor PVC insulated and PVC sheathed unarmoured underground Airfield Lighting Cable generally confirming to IS 1554 Part II with upto date amendments as required (Make: As per AAI list of approved makes) | 6000.00 | Mtr |  | 90.00 | 540000.00 | 90.00 | 540000.00 | 75.00 | 450000.00 | 450000.00 | AMA Private Limited
9.00 | Supply of C.I. Isolating Transformer housing box,water tight round type,metal container of outside size 330mm height 450mm made of 10mm thick cast iron moulding suitable to receive a light fitting base plate on the top and underground housing associated with transformer power cable and having a clear hole centre at one side surface centre 75mm above bottom surface suitable to receive one No. / two of 50mm dia "B" class GI pipe and including check nuts as required and another hole at 175mm from the bottom of the CI Box to receive one no. 15mm dia "B" class GI pipe and check nut as required.The box should have two SS earth bolts of M10 x 30mm tapped inside near the hole (4" away from the hole centre) and having a drain hole at the bottom suitably tapped to receive 15mm dia "B" class GI pipe and having clear opening of 220 mm at the top surface and 6 nos. M10 tapped hole at the hole centre 260 mm to receive fitting base plate and bolts as required as per the drawings. | 31.00 | Each |  | 4525.00 | 140275.00 | 4500.00 | 139500.00 | 4100.00 | 127100.00 | 127100.00 | AMA Private Limited
10.00 | Supply 2X2.5sq.mm 2 pin secondary plug assembly of 2.5mtrs length suitable for runway /taxiway/ approach light fittings. | 30.00 | Each |  | 750.00 | 22500.00 | 1000.00 | 30000.00 | 750.00 | 22500.00 | 22500.00 | Techno Electricals, AMA Private Limited
11.00 | Supply of following height of approach frangible pole including foundation template, 4sets of bolt nuts, with color finish of Aviation yellow with UV-protection and suitable adaptor to install approach light fittings, as per specifications of ICAO. i) 1.5 mtr | 10.00 | Each |  | 9525.00 | 95250.00 | 5000.00 | 50000.00 | 23000.00 | 230000.00 | 50000.00 | Balaji Engineering
12.00 | Supply of following size of XLPE insulated & PVC sheathed, armoured, aluminium conductor under ground cable of 1.1KV grade as per IS 7098:1988 Part-I with upto date amendments complete as required. (Make: As per AAI list of approved makes)
12.01 | 4CX16sq.mm | 1700.00 | Mtr |  | 125.00 | 212500.00 | 225.00 | 382500.00 | 150.00 | 255000.00 | 212500.00 | Techno Electricals
12.02 | 3CX10sq.mm | 200.00 | Mtr |  | 100.00 | 20000.00 | 170.00 | 34000.00 | 120.00 | 24000.00 | 20000.00 | Techno Electricals
13.00 | Supply of 10CX1.5sq.mm PVC insulated and FR PVC sheathed, copper conductor (flexible) industrial cable, 1100Volt, conforming to IS 694 with upto date amendments complete as required. (Make: As per AAI list of approved makes) | 200.00 | Mtr |  | 225.00 | 45000.00 | 350.00 | 70000.00 | 180.00 | 36000.00 | 36000.00 | AMA Private Limited
14.00 | Supply of pole mounted street light LED luminaries having minimum lumen output of 3600 lm, system efficay not less than 110 lumen/watt, control driver with minimum 4kV surge suppressor, made up of pressure die cast Aluminum housing with toughened glass , suitable to operating on single phase, 50Hz AC supply meeting with minimum requirements specfied in the technical specification and equivalent to Model No. BRP046 LED 36W MR S1 PSU GR, Make: Philips/ model No. LSTS-36-CDL-M, Make: Crompton. | 55.00 | Each |  | 3000.00 | 165000.00 | 4500.00 | 247500.00 | 4000.00 | 220000.00 | 165000.00 | Techno Electricals
15.00 | Fabrication and Supply of GI pole of 65 mm dia class B , up to max length of 4.5 mtrs in which one side making wrinkle free bend up to a length of 1mtr with an angle not morethan 20 degree and suitable reducer to fix the LED fixture other end welded with 12mm thick MS/GI base plate (300X300X12mm) with 4no holes and frontside U shape cutting for accommodating the 50mm dia GI pipe along with pole including two coats of aluminium painting and pole number etc as required. Note: The height of pole is presently tentative. Incase of reduced height, the payment will be made proportionately according to the clearance of the NOC. | 50.00 | Each |  | 4692.00 | 234600.00 | 5000.00 | 250000.00 | 5700.00 | 285000.00 | 234600.00 | Techno Electricals
16.00 | Providing & fixing of SMC box of size 250mmX200mm X105mm deep on the existing tubular pole with suitable MS clamp including providing & fixing 1no. 6A SP MCB B series and 1no. 63A 4Way connector, connections etc. complete as required. (Model: GSJB-2520) | 50.00 | Each |  | 1750.00 | 87500.00 | 1500.00 | 75000.00 | 1000.00 | 50000.00 | 50000.00 | AMA Private Limited
17.00 | supply and fixing of GLF "CIRCUIT SELECTOR SWITCH" for End lights with rating of 6.6A, 5000V,ClassA, including all switch gear, panel enclosure and with operation control of manual and remote and termination of all incoming and outgoing cables | 2.00 | Each |  | 1750.00 | 3500.00 | 5000.00 | 10000.00 | 35000.00 | 70000.00 | 3500.00 | Techno Electricals
18.00 | Supply of 40 mm dia (OD-40 mm) size HDPE pipe, lSI marked along with all accessories like socket, couplers etc. conforming to IS 4984-1995, NP6 grade, PE63 etc., complete as required. (Make: As per AAI list of approved makes) | 200.00 | Mtr |  | 100.00 | 20000.00 | 50.00 | 10000.00 | 60.00 | 12000.00 | 10000.00 | Balaji Engineering
19.00 | Providing and laying of 15 mm dia 'B' class GI pipe including groove cutting, threading and alignment of pipe with transformer housing box, inset fittings, providing check nuts and couplings etc as required on the runway and disposal of excavated materials within a lead of 50 meter. | 235.00 | Mtr |  | 250.00 | 58750.00 | 150.00 | 35250.00 | 375.00 | 88125.00 | 35250.00 | Balaji Engineering
20.00 | Provision of Microconcrete plaster on existing groove cut portion above the GI pipe/damaged portion in the tarmac runway and finishing as per directions of E-I-C. | 3.00 | Cu.mtr |  | 5252.00 | 15756.00 | 10000.00 | 30000.00 | 13500.00 | 40500.00 | 15756.00 | Techno Electricals
21.00 | Installation, testing and commisiong of Elevated type approach light fittings/Taxiway fittings/Runway fittings on the existing transformer housing boxes/frangible poles including installation of transformer, lens, lamps gasket,nut bolts, lens holding clamp and other accessories i/c alignment,connection, earth connection etc. as complete as required. | 15.00 | Each |  | 200.00 | 3000.00 | 250.00 | 3750.00 | 350.00 | 5250.00 | 3000.00 | Techno Electricals
22.00 | Installation, Testing and Commissioning of inset type runway end/approach/ runway edge light fitting in the runway with core cutting, aligning with existing 15mm dia GI pipe, connections, inter connection and setting i/c providing sealing material and other accessories etc.,as required for commissioning. | 14.00 | Each |  | 5525.00 | 77350.00 | 7500.00 | 105000.00 | 9000.00 | 126000.00 | 77350.00 | Techno Electricals
23.00 | Making field connections by crimping of 6/16 sq.mm plug & receptable with suitable existing size single core PVC cu. Conductor cable of 5 KV grade Airfield cable including filling the gap with water sealent material applying PVC insulation tape etc. complete as reqd. | 67.00 | Each |  | 100.00 | 6700.00 | 250.00 | 16750.00 | 350.00 | 23450.00 | 6700.00 | Techno Electricals
24.00 | Installation, Testing, Commissioning of 7.5kW /4kW CCR including supply and laying of control cable, connection, making foundation, 2 nos. GI strip earthing etc. as required. | 2.00 | Each |  | 5500.00 | 11000.00 | 5000.00 | 10000.00 | 15000.00 | 30000.00 | 10000.00 | Balaji Engineering
25.00 | Installation of round type transformer housing box with base concrete of 1:3:6 of size 630 x 630 x 100 mm thick all around concrete of 1:2:4, 150 mm thick top slopped with 1:2:4 cement concrete including providing and fixing 10" long 1/2" dia B class GI pipe with check nuts for drainage of water including excavation and refilling, aligning the boxes in straight line etc complete as required. | 31.00 | Each |  | 2563.00 | 79453.00 | 2000.00 | 62000.00 | 4000.00 | 124000.00 | 62000.00 | Balaji Engineering
26.00 | Installation of approach frangible pole with plain cement concrete of foundation size 800mm X 500mm X500mm suitable to install tamplate of approach pole, bolt, nuts and other accessories etc., as required | 10.00 | Each |  | 3500.00 | 35000.00 | 3500.00 | 35000.00 | 6000.00 | 60000.00 | 35000.00 | Techno Electricals, Balaji Engineering
27.00 | Supply of 50mm size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete etc., as required. | 5400.00 | Mtr |  | 79.00 | 426600.00 | 45.00 | 243000.00 | 55.00 | 297000.00 | 243000.00 | Balaji Engineering
28.00 | Laying of 2nos of 50mm size DWC HDPE pipe complete with fitting and cutting, jointing etc.direct in ground (80 cm below ground level) for minimum width of 50cm including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. | 2150.00 | Mtr |  | 142.00 | 305300.00 | 100.00 | 215000.00 | 190.00 | 408500.00 | 215000.00 | Balaji Engineering
29.00 | Laying of 50mm size DWC HDPE pipe complete with fitting and cutting, jointing etc.direct in ground (80 cm below ground level) for minimum width of 35cm including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. | 1100.00 | Mtr |  | 115.00 | 126500.00 | 100.00 | 110000.00 | 180.00 | 198000.00 | 110000.00 | Balaji Engineering
30.00 | Supply and laying of 2CX2.5sq.mm size FR PVC round sheathed, copper conductor(flexible) industrical cable in the existing RCC/HUME/STONE WARE/METAL/DWC-HDPE pipe as required. | 260.00 | Mtr |  | 125.00 | 32500.00 | 125.00 | 32500.00 | 15.00 | 3900.00 | 3900.00 | AMA Private Limited
31.00 | Laying of one number PVC insulated and PVC sheathed/ XLPE power cable of 5 KV/1.1KV grade of upto 35 sq.mm in the existing RCC/HUME/STONE WARE/METAL/DWC-HDPE pipe as required. | 5600.00 | Mtr |  | 12.00 | 67200.00 | 20.00 | 112000.00 | 15.00 | 84000.00 | 67200.00 | Techno Electricals
32.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 5kV/1.1 kV grade of Upto 35 sq. mm (clamped with 1mm thick saddle) on cable tray as required. | 100.00 | Mtr |  | 35.00 | 3500.00 | 50.00 | 5000.00 | 40.00 | 4000.00 | 3500.00 | Techno Electricals
33.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV/5 KVgrade of upto 35 sqmm size in the existing masonry open duct as required | 250.00 | Mtr |  | 25.00 | 6250.00 | 25.00 | 6250.00 | 20.00 | 5000.00 | 5000.00 | AMA Private Limited
34.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 4.0 X 16Sqmm (28mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. (Make: As per AAI list of approved makes) | 104.00 | Set |  | 285.00 | 29640.00 | 250.00 | 26000.00 | 350.00 | 36400.00 | 26000.00 | Balaji Engineering
35.00 | Erection of 3.5 to 5 mtr metalic tubular pole with, construction of RCC foundation suitable for installation of pole with 1:2:4 cement concrete to the required depth as per sepcial conditions (1cement: : 2coarse sand: 4 graded stone aggregate 20mm nominal size) and necessary base concrete of 1:3:6 for 100mm thickness below the pole foundation (1cement: 3 fine sand: 6 graded stone aggregate 40mm nominal size) suitable finishing on surface above the ground level with grounting 4 Nos GI 700mm length botnuts and washers for installtion of tubular pole etc., complete as required.(including reinforcement for RCC work, straightening, placing in position and binding etc., as required) | 50.00 | Each |  | 3000.00 | 150000.00 | 2500.00 | 125000.00 | 4000.00 | 200000.00 | 125000.00 | Balaji Engineering
36.00 | Providing & fixing of 50 mm dia class "B" GI pipe of 1.50 Mtr length including cutting , making bending to recieve cables and threading as required, providing with one no of rubbber bush with holes suitable to receive 2no of 4 x 16 Sqmm and 2 nos of 6 SWG GI wire etc complete as required. | 50.00 | Each |  | 750.00 | 37500.00 | 600.00 | 30000.00 | 350.00 | 17500.00 | 17500.00 | AMA Private Limited
37.00 | Installation testing commissioning of LED luminaires fitting on the existing pole including providing and laying of 3C X 2.5 sqmm PVC insulated , FR PVC round sheathed, copper conductor cable of minimum 4 mtr length from cable looping box(SMC) to fitting including fixing of SMC juction box on the pole etc., as required. including all necessary accessories / clamp / washers on Truss / Recess / Surface / wall braket /Wall mounted/street light of height up to 5 mtrs etc., as required. | 50.00 | Each |  | 400.00 | 20000.00 | 500.00 | 25000.00 | 500.00 | 25000.00 | 20000.00 | Techno Electricals
38.00 | Making Horizontal boring by using suitable mechanical arrangement, Sensor operated, Min. 2.5Mtr Depth, horizontal bore well suitable for inserting 01 no 40mm Dia. HDPE Pipes. job including inserting of HDPE Pipes in bore well hole etc., complete is required. | 200.00 | Mtr |  | 650.00 | 130000.00 | 350.00 | 70000.00 | 1300.00 | 260000.00 | 70000.00 | Balaji Engineering
39.00 | Providing and fixing 6 SWG dia G.l. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ sub main wiring/ cable as required. | 1750.00 | Mtr |  | 25.00 | 43750.00 | 25.00 | 43750.00 | 25.00 | 43750.00 | 43750.00 | Techno Electricals, Balaji Engineering, AMA Private Limited
40.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 10.00 | Set |  | 5525.00 | 55250.00 | 6000.00 | 60000.00 | 7000.00 | 70000.00 | 55250.00 | Techno Electricals
41.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 meter in width, and lift upto 1.5 meter, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 meter. | 30.00 | Cu.mtr |  | 650.00 | 19500.00 | 800.00 | 24000.00 | 1600.00 | 48000.00 | 19500.00 | Techno Electricals
42.00 | Taking GPS based co-ordinates by using total station and identifying the locations of light fixtures, route of cable etc based on GPS co-ordinates and marking, submission of reports / drawings etc. as required and as per directions of the Engineer In charge. | 1.00 | Job |  | 22000.00 | 22000.00 | 10000.00 | 10000.00 | 100000.00 | 100000.00 | 10000.00 | Balaji Engineering
43.00 | Supply of 3.5mtr, 50 mm dia 'B' class GI pipe including check nuts and couplings etc as required | 2.00 | Each |  | 1825.00 | 3650.00 | 2000.00 | 4000.00 | 700.00 | 1400.00 | 1400.00 | AMA Private Limited
| Total in Figures |  |  |  |  | 5396299.00 |  | 5232500.00 |  | 5865535.50
Lowest Amount Quoted BY: Balaji Engineering(5232500.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Simple Approach Lighting system (SALS) in Runway 09, Perimeter wall lighting for newly acquired land at Trichy Airport Tender ID: 2020_AAI_65353_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Balaji Engineering | 5232500.00 | L1
| 2 | Techno Electricals | 5396299.00 | L2
| 3 | AMA Private Limited | 5865535.50 | L3