## BoQ1
Government eProcurement System Created By: Ashok Kumar Created Date/Time: 21-Jan-2021 12:36 PM Tender Title: Shifting of SMU NAV-AIDS from IGI Palam to RCDU Workshop Safdarjung Airport, New Delhi. SH Electrical Works. Tender ID: 2020_AAI_65702_1
Tender Inviting Authority: Asstt. Gen. Mgr., Airports Authority of India, Safdarjung Airport-110003
Name of Work: Shifting of SMU NAV-AIDS from IGI Palam to RCDU Workshop Safdarjung Airport, New Delhi. SH: Electrical Works.
Contract No: AAI/SAP/Engg.(E)/OA/RADAR SMU/2020-21
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ANU ENGINEERING CORPORATION(GSTN-07AJDPK9181G1Z1) |  | NATIONAL SAFETY ENGINEERS(GSTN-07ADCPT3599E3Z6) |  | MASTER ELECTRIC STORE(GSTN-07AAHPB6825H1ZU)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH I - Wiring
2.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required.
2.01 | Group C | 60.00 | Point | 100.00 | 950.00 | 57000.00 | 1300.00 | 78000.00 | 1110.00 | 66600.00 | 57000.00 | ANU ENGINEERING CORPORATION
3.00 | Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit alongwith 1 No. 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 200.00 | Meter | 100.00 | 200.00 | 40000.00 | 290.00 | 58000.00 | 285.00 | 57000.00 | 40000.00 | ANU ENGINEERING CORPORATION
4.00 | Wiring for light/ power plug with 4X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit alongwith 2 Nos. 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 125.00 | Meter | 10.00 | 275.00 | 34375.00 | 430.00 | 53750.00 | 475.00 | 59375.00 | 34375.00 | ANU ENGINEERING CORPORATION
5.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required.
5.01 | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | 50.00 | Meter | 100.00 | 150.00 | 7500.00 | 225.00 | 11250.00 | 195.00 | 9750.00 | 7500.00 | ANU ENGINEERING CORPORATION
5.02 | 2 X 6 sq. mm + 1 X 6 sq. mm earth wire | 30.00 | Meter | 100.00 | 250.00 | 7500.00 | 390.00 | 11700.00 | 390.00 | 11700.00 | 7500.00 | ANU ENGINEERING CORPORATION
6.00 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
6.01 | 20 mm | 50.00 | Meter | 100.00 | 140.00 | 7000.00 | 175.00 | 8750.00 | 110.00 | 5500.00 | 5500.00 | MASTER ELECTRIC STORE
6.02 | 25 mm | 50.00 | Meter | 100.00 | 155.00 | 7750.00 | 195.00 | 9750.00 | 135.00 | 6750.00 | 6750.00 | MASTER ELECTRIC STORE
7.00 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc. as required.
7.01 | 1 or 2 Module (75 mmX75 mm) | 15.00 | Each | 100.00 | 175.00 | 2625.00 | 290.00 | 4350.00 | 199.00 | 2985.00 | 2625.00 | ANU ENGINEERING CORPORATION
7.02 | 4 Module (125mmX75mm) | 10.00 | Each | 100.00 | 200.00 | 2000.00 | 350.00 | 3500.00 | 245.00 | 2450.00 | 2000.00 | ANU ENGINEERING CORPORATION
7.03 | 8 Module (125mmX125mm) | 4.00 | Each | 10.00 | 270.00 | 1080.00 | 450.00 | 1800.00 | 349.00 | 1396.00 | 1080.00 | ANU ENGINEERING CORPORATION
7.04 | 12 Module (200mmX150mm) | 4.00 | Each | 10.00 | 300.00 | 1200.00 | 520.00 | 2080.00 | 399.00 | 1596.00 | 1200.00 | ANU ENGINEERING CORPORATION
8.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 A & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 42.00 | Each | 10.00 | 450.00 | 18900.00 | 590.00 | 24780.00 | 419.00 | 17598.00 | 17598.00 | MASTER ELECTRIC STORE
9.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
9.01 | 6 way (4 + 18), Double door | 4.00 | Each | 100.00 | 3700.00 | 14800.00 | 4500.00 | 18000.00 | 2699.00 | 10796.00 | 10796.00 | MASTER ELECTRIC STORE
9.02 | 8 way (4 + 24), Double door | 1.00 | Each | 100.00 | 4700.00 | 4700.00 | 5500.00 | 5500.00 | 3199.00 | 3199.00 | 3199.00 | MASTER ELECTRIC STORE
10.00 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB’s (but without MCB’s and incomer ) as required. (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
10.01 | 4 way (4 + 12), Double door | 1.00 | Each | 100.00 | 8000.00 | 8000.00 | 3700.00 | 3700.00 | 3999.00 | 3999.00 | 3700.00 | NATIONAL SAFETY ENGINEERS
11.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
11.01 | Single pole | 40.00 | Each | 10.00 | 150.00 | 6000.00 | 190.00 | 7600.00 | 199.00 | 7960.00 | 6000.00 | ANU ENGINEERING CORPORATION
11.02 | SPN | 10.00 | Each | 10.00 | 450.00 | 4500.00 | 400.00 | 4000.00 | 399.00 | 3990.00 | 3990.00 | MASTER ELECTRIC STORE
12.00 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 15.00 | Each | 10.00 | 30.00 | 450.00 | 10.00 | 150.00 | 39.00 | 585.00 | 150.00 | NATIONAL SAFETY ENGINEERS
13.00 | Supplying and fixing of following rating & poles, 240/415 V, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
13.01 | 63 A, triple pole | 4.00 | Each | 10.00 | 1100.00 | 4400.00 | 1200.00 | 4800.00 | 1099.00 | 4396.00 | 4396.00 | MASTER ELECTRIC STORE
13.02 | 63 A, triple pole and neutral | 6.00 | Each | 10.00 | 1400.00 | 8400.00 | 1400.00 | 8400.00 | 1499.00 | 8994.00 | 8400.00 | ANU ENGINEERING CORPORATION, NATIONAL SAFETY ENGINEERS
14.00 | Supplying and fixing 20 A, 240 V, SPN Industrial type socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 A, “C” curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 15.00 | Each | 10.00 | 1200.00 | 18000.00 | 1350.00 | 20250.00 | 1299.00 | 19485.00 | 18000.00 | ANU ENGINEERING CORPORATION
15.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
15.01 | 5/6amps switch | 10.00 | Each | 10.00 | 75.00 | 750.00 | 90.00 | 900.00 | 69.00 | 690.00 | 690.00 | MASTER ELECTRIC STORE
15.02 | 3 pin 5/6 A socket outlet | 10.00 | Each | 10.00 | 100.00 | 1000.00 | 120.00 | 1200.00 | 79.00 | 790.00 | 790.00 | MASTER ELECTRIC STORE
15.03 | LAN Point (RJ45) | 20.00 | Each | 10.00 | 450.00 | 9000.00 | 100.00 | 2000.00 | 30.00 | 600.00 | 600.00 | MASTER ELECTRIC STORE
16.00 | Supplying and drawing of UTP 4 pair CAT 6 LAN Cable in the existing surface/ recessed Steel/ PVC conduit as required.
16.01 | 1 run of cable | 50.00 | Meter | 10.00 | 70.00 | 3500.00 | 55.00 | 2750.00 | 80.00 | 4000.00 | 2750.00 | NATIONAL SAFETY ENGINEERS
16.02 | 2 run of cable | 100.00 | Meter | 10.00 | 100.00 | 10000.00 | 95.00 | 9500.00 | 160.00 | 16000.00 | 9500.00 | NATIONAL SAFETY ENGINEERS
17.00 | Supplying, installation, testing and commissioning of 4 way double door MCCB panel board expendable type made of 1.6mm CRCA sheet steel and epoxy powder coated, modular construction, floor mounting/wall mounting, IP30, bus bar fully rated, complete with 4 way cable alley module on both sides, metering module comprises of digital type ammeter and voltmeter with selector switches and RYB indicating lights with back up protection, and supplying and fixing of following MCCBs / Accessories including connection of all circuits and outgoing cables etc. complete as reqd.(Make:- Havells Load Bank/Legrand/Siemens) i) 4 way double door G Frame panel board (Make: Havells Model No. IHVGF2500400 or equivallent) -1 No ii) Incomer 100 Amps. FP MCCB 25 KA with all spreader links and connections-1 No iii) Outgoings 63 Amps FP MCCB 25 KA with spreader links - 4 Nos iv) Cable alley 4 way double door 250 Amps (Suitable for above Panel board Make: Havells Model No. ISSBOU0698 or equivallent)-1 No. v) Digital meter module ( Ampere meter,Voltmeter with selector switch and LED indication lights-1 Set | 1.00 | Job | 10.00 | 125000.00 | 125000.00 | 75000.00 | 75000.00 | 89000.00 | 89000.00 | 75000.00 | NATIONAL SAFETY ENGINEERS
18.00 | SH-II: Fitting, Fixtures and Misc items
19.00 | Supply of recess mounted LED of size 600mm x 600mm made of CRCA sheet housing, fixture should have rated system lumen output of minimum 3600 lumen with rated efficacy at system level (not chip level) > = 100 lumens/watt, life of fixture is not less than 50000 hrs @ L-70 lumen maintenance, CCT upto 5700K - 6500K, CRI minimum 80, PF >= 0.95, THD < 10% and an operating voltage range of 140 to 270V, internal surge protection > 2KV, with unified glare rating (UGR) <= 19. The fixture should comply with the other parameters as per IS10322. | 28.00 | Each | 10.00 | 2100.00 | 58800.00 | 2100.00 | 58800.00 | 2299.00 | 64372.00 | 58800.00 | ANU ENGINEERING CORPORATION, NATIONAL SAFETY ENGINEERS
20.00 | Supply of 20W (±10%) T8 4 feet high efficacy low power consumption LED tube light fittings (i/c batten & tube rod) having IP20 rating compatible with retrofit type tube light have rated system lumens output of minimum 2000 lumens with rated efficacy at system level (not chip level) >= 100 lumens/Watt, life of fixture is not less than 50000 hrs @ L-70 lumen maintenance, CCT upto 5700K - 6500K, CRI minimum 80, PF >= 0.95, THD < 10% and an operating voltage range of 140 to 270V, internal surge protection > 2KV, with unified glare rating (UGR) <= 19. The fixture should comply with the other parameters as per IS10322. | 18.00 | Each | 10.00 | 600.00 | 10800.00 | 600.00 | 10800.00 | 499.00 | 8982.00 | 8982.00 | MASTER ELECTRIC STORE
21.00 | Installation ,Testing, Commissioning of wall bracket /ceiling fittings of all sizes and shapes containing upto two GLS/CFL/LED lamps per fitting, complete with all accessories including connections etc. as required. | 46.00 | Each | 10.00 | 150.00 | 6900.00 | 100.00 | 4600.00 | 55.00 | 2530.00 | 2530.00 | MASTER ELECTRIC STORE
22.00 | SITC of 400mm sweep 230V, 50 Hz single phase, 1400rpm Wall mounting fan having power consumption less than 60W, MS ribs guard for protection, pull cord control for speed & oscillation On-Off and making the electrical connections with all the accessories as required. | 12.00 | Each | 10.00 | 2000.00 | 24000.00 | 1900.00 | 22800.00 | 1600.00 | 19200.00 | 19200.00 | MASTER ELECTRIC STORE
23.00 | Supply of heavy duty pedestal fan of 600 mm sweep, 1400 RPM motor suitable for operation on 230V, 50 Hz Single phase A.C. supply having smooth oscillation, outer cage for protection, height adjustment arrangement, heavy base for stability, capacitor etc. complete as required. | 2.00 | Each | 10.00 | 5000.00 | 10000.00 | 6370.00 | 12740.00 | 11900.00 | 23800.00 | 10000.00 | ANU ENGINEERING CORPORATION
24.00 | Supply of 300mm sweep 230V, 50 Hz single phase, 1300-1400rpm, double ball bearing Exhaust fan having power consumption less than 70W including louvre for the protection with all the accessories as required. Make: Havells Ventil Air DB or equivalent. | 2.00 | Each | 10.00 | 4500.00 | 9000.00 | 2150.00 | 4300.00 | 1150.00 | 2300.00 | 2300.00 | MASTER ELECTRIC STORE
25.00 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. Upto 450 mm sweep | 2.00 | Each | 10.00 | 300.00 | 600.00 | 200.00 | 400.00 | 350.00 | 700.00 | 400.00 | NATIONAL SAFETY ENGINEERS
26.00 | SH-III: Cable Laying
27.00 | Supply of following sizes of 1.1kv grade multicore Aluminium conductor XLPE insulated PVC sheathed armoured cable (as per IS : 7098:1988 with upto date amendments) complete as requried as per specifications.
27.01 | 3.5 core, 25 Sqmm, Aluminium cable | 50.00 | Meter | 10.00 | 165.00 | 8250.00 | 190.00 | 9500.00 | 200.00 | 10000.00 | 8250.00 | ANU ENGINEERING CORPORATION
27.02 | 3.5 core, 50 Sqmm, Aluminium cable | 20.00 | Meter | 10.00 | 270.00 | 5400.00 | 325.00 | 6500.00 | 350.00 | 7000.00 | 5400.00 | ANU ENGINEERING CORPORATION
27.03 | 3.5 core, 95 Sqmm, Aluminium cable | 50.00 | Meter | 10.00 | 450.00 | 22500.00 | 540.00 | 27000.00 | 564.00 | 28200.00 | 22500.00 | ANU ENGINEERING CORPORATION
28.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
28.01 | Above 35 sq. mm and upto 95 sq. mm | 10.00 | Meter | 10.00 | 300.00 | 3000.00 | 350.00 | 3500.00 | 358.00 | 3580.00 | 3000.00 | ANU ENGINEERING CORPORATION
29.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
29.01 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. | 10.00 | Meter | 10.00 | 300.00 | 3000.00 | 1.00 | 10.00 | 35.00 | 350.00 | 10.00 | NATIONAL SAFETY ENGINEERS
29.02 | Upto 35 sq. mm | 10.00 | Meter | 10.00 | 30.00 | 300.00 | 30.00 | 300.00 | 50.00 | 500.00 | 300.00 | ANU ENGINEERING CORPORATION, NATIONAL SAFETY ENGINEERS
30.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
30.01 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 40.00 | Meter | 10.00 | 60.00 | 2400.00 | 50.00 | 2000.00 | 45.00 | 1800.00 | 1800.00 | MASTER ELECTRIC STORE
30.02 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 50.00 | Meter | 10.00 | 80.00 | 4000.00 | 70.00 | 3500.00 | 105.00 | 5250.00 | 3500.00 | NATIONAL SAFETY ENGINEERS
31.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.
31.01 | 3½ X 25 sq. mm (28 mm) | 6.00 | Each | 10.00 | 100.00 | 600.00 | 80.00 | 480.00 | 250.00 | 1500.00 | 480.00 | NATIONAL SAFETY ENGINEERS
31.02 | 3½ X 50 sq. mm (35 mm) | 2.00 | Each | 10.00 | 150.00 | 300.00 | 90.00 | 180.00 | 325.00 | 650.00 | 180.00 | NATIONAL SAFETY ENGINEERS
31.03 | 3½ X 95 sq. mm (45 mm) | 2.00 | Each | 10.00 | 200.00 | 400.00 | 100.00 | 200.00 | 460.00 | 920.00 | 200.00 | NATIONAL SAFETY ENGINEERS
32.00 | SH-IV EXTERNAL LIGHTNING PROTECTION SYSTEM AND SURGE PROTECTION DEVICES
33.00 | I-AIR TERMINATION SYSTEM
34.00 | Supply and Installation of 8mm dia Aluminium alloy Solid Round Conductor of material AlMgSi used in air termination and down conductor system . Cross sectional area of conductor should be 50 mm². Test Parameter: a.Lightning impulse current of 100kA for 10/350 µs b.Electrical resistivity - 0.036 µΩm, Tensile strength - 120 to 240 MPa or N/mm², Salt spray - No Sign of Corrosion. Tested as per IEC 62561-2. Model - CAPE Type: SRC 8–AL (Article No. 400 008) or equivalent as per AAI approved make list. | 130.00 | Meter | 10.00 | 150.00 | 19500.00 | 175.00 | 22750.00 | 235.00 | 30550.00 | 19500.00 | ANU ENGINEERING CORPORATION
35.00 | Supply of stainless steel Metal roof conductor holder for fixing Aluminium conductor need to be confirmed as per sheet profile to meet the requirement of IS/IEC - 62305 Model - CAPE Type: MRCH 8-10 (Article No: 400 204) or equivalent as per AAI approved make list. | 100.00 | Nos | 10.00 | 250.00 | 25000.00 | 275.00 | 27500.00 | 399.00 | 39900.00 | 25000.00 | ANU ENGINEERING CORPORATION
36.00 | Supply of UV resistance Nylon/PU Conductor Holder for Parapet wall for holding 8 mm dia Aluminium alloy round Conductor. Model - CAPE Type: PCH 8 (Article No. 400 202) or equivalent as per AAI approved make list. | 15.00 | Nos | 10.00 | 45.00 | 675.00 | 70.00 | 1050.00 | 65.00 | 975.00 | 675.00 | ANU ENGINEERING CORPORATION
37.00 | Supply and Installation of UV resistance Nylon/PU roof conductor holder for flat roof with concrete block for fixing 8 mm dia Aluminium alloy Solid Round Conductor in the terrace flat surface at every 1 mtr. Model - CAPE Type: CAPE Type: MBPCH8 (Article No. 403 201) or equivalent as per AAI approved make list. | 10.00 | Nos | 10.00 | 120.00 | 1200.00 | 140.00 | 1400.00 | 185.00 | 1850.00 | 1200.00 | ANU ENGINEERING CORPORATION
38.00 | Supply and Installation of Stainless steel Cross Connector for 8 mm dia Aluminium alloy round conductor & 10 mm Copper bonded conductor at cross junction. Test Parameter Salt Spray Test ( IEC 62561-1) - No sign of Corrosion Model - CAPE Type:CCSS 8-10 ( Article No. 400 206) or equivalent as per AAI approved make list. | 15.00 | Nos | 10.00 | 710.00 | 10650.00 | 715.00 | 10725.00 | 1090.00 | 16350.00 | 10650.00 | ANU ENGINEERING CORPORATION
39.00 | Supply and Installation of Expansion Piece with connector to compensate the expansion and contraction of Solid Round Al. Conductor during temperature variations.Expansion piece should be consider at every 20 mtr length of straight horizontal air termination and connected at both the end with use of straight connector conductor . Test Parameter: Electrical Resistivity Test-0.036 µΩm Salt Spray Test - No Sign of Corrosion Tested as per IEC 62561-1 Model - CAPE Type: EPC 8 ( Article No. 401 209) or equivalent as per AAI approved make list. | 6.00 | Nos | 10.00 | 320.00 | 1920.00 | 350.00 | 2100.00 | 599.00 | 3594.00 | 1920.00 | ANU ENGINEERING CORPORATION
40.00 | Supply and Installation of Aluminium Straight conductor connector for interconnecting 8mm Aluminium conductor to meets the requirement of IS/IEC 62305.Tested for Electrical , Mechanical and chemical as per IEC 62561. Model - CAPE Type : CJ 8 ( Article No 401 211) or equivalent as per AAI approved make list. | 5.00 | Nos | 10.00 | 75.00 | 375.00 | 100.00 | 500.00 | 110.00 | 550.00 | 375.00 | ANU ENGINEERING CORPORATION
41.00 | Supply and Installation of air termination rod of 3 mtr length of material AlMgSi of diametre ø 16/10 mm crimped on both the ends(Tappered Type). The rod shall be mounted with stone and fixing accessories . Test Parameter: Mechanical Load Test for individual aluminium alloy rods - 120 to 280 N/mm² Salt Spray Test-No sign of corrosion Tested as per IEC 62561-1&2 Model - CAPE Type VATF3 ( 401 430) or equivalent as per AAI approved make list. | 2.00 | Nos | 10.00 | 9000.00 | 18000.00 | 7575.00 | 15150.00 | 10400.00 | 20800.00 | 15150.00 | NATIONAL SAFETY ENGINEERS
42.00 | II-DOWN CONDUCTOR SYSTEM
43.00 | Supply and Installation of 8mm dia Aluminium alloy Solid Round Conductor of material AlMgSi used in air termination and down conductor system . Cross sectional area of conductor should be 50 mm². Test Parameter: a.Lightning impulse current of 100kA for 10/350 µs b.Electrical resistivity - 0.036 µΩm, Tensile strength - 120 to 240 MPa or N/mm², Salt spray - No Sign of Corrosion. Tested as per IEC 62561-2. Model - CAPE Type: SRC 8–AL (Article No. 400 008) or equivalent as per AAI approved make list. | 10.00 | Meter | 10.00 | 150.00 | 1500.00 | 1837.00 | 18370.00 | 245.00 | 2450.00 | 1500.00 | ANU ENGINEERING CORPORATION
44.00 | Supply and Installation of Stainless steel Conductor Holder for fixing the 10 mm dia round conductor on the side wall . Test Parameter: Salt Spray Test - No Sign of Corrosion Tested as per IEC 62561-1 Model - Cape Type CH 8-10 ( Article No.400 213) or equivalent as per AAI approved make list. | 10.00 | Nos | 10.00 | 180.00 | 1800.00 | 220.00 | 2200.00 | 279.00 | 2790.00 | 1800.00 | ANU ENGINEERING CORPORATION
45.00 | Supply and Installation of Aluminium Straight conductor connector for interconnecting 8mm Aluminium conductor to meets the requirement of IS/IEC 62305.Tested for Electrical , Mechanical and chemical as per IEC 62561. Model - CAPE Type : CJ 8 ( Article no 401 211) or equivalent as per AAI approved make list. | 1.00 | No | 10.00 | 50.00 | 50.00 | 125.00 | 125.00 | 1250.00 | 1250.00 | 50.00 | ANU ENGINEERING CORPORATION
46.00 | Supply and Installation of Lightning counter - LCD screen shows the number of lightning strikes, hour and date of lightning events Buttons enable TIME/DATE setting and log viewing. Replaceable battery, working life minimum five years, Complies with IEC/EN 62561-6. Model - CAPE Type No: PRO LEC Basic ( Article No. 130 520) or equivalent as per AAI approved make list. | 1.00 | No | 10.00 | 62000.00 | 62000.00 | 56000.00 | 56000.00 | 49000.00 | 49000.00 | 49000.00 | MASTER ELECTRIC STORE
47.00 | Supply and Installation of Stainless Steel Test Joint with enclosure to interconnect between 8 mm Al. round conductor to 10 mm copper bonded round conductor Test Parameter: Salt Spray Test for test joint plate -No sign of Corrosion Tested as per IEC 62561-1 Model - Cape Type TJRRE ( Article No. 401 215) or equivalent as per AAI approved make list. | 2.00 | Nos | 10.00 | 1500.00 | 3000.00 | 1450.00 | 2900.00 | 2700.00 | 5400.00 | 2900.00 | NATIONAL SAFETY ENGINEERS
48.00 | III-Earthing System
49.00 | Supply and Installation of Rust resistant non corossive 10 mm dia Copper bonded round conductor used for Earth termination inside the concrete and soil. Test parameter: Short circuit current test for copper bonded conductor:Test 6 kA ratings, as per cross sectional area for 1 sec(IS3043/IEEE80); Electrical Resistivity before & after salt mist spray test: 0.25µΩm max. Tensile Test 290 to 510 N/mm². Adhesion no peel or crack & Bend test no seperation of Cu, Cu Coating thickness min. 70µm. Tested as per IEC 62561-2. Model - CAPE Type : SRC 10 Cu ( Article No. 400 010) or equivalent as per AAI approved make list. | 6.00 | Meter | 10.00 | 550.00 | 3300.00 | 520.00 | 3120.00 | 799.00 | 4794.00 | 3120.00 | NATIONAL SAFETY ENGINEERS
50.00 | Supply and Installation of Stainless steel Conductor Holder for fixing the 10 mm dia round conductor on the side wall . Test Parameter: Salt Spray Test - No Sign of Corrosion Tested as per IEC 62561-1 Model - Cape Type CH 8-10 ( Article No.400 213) or equivalent as per AAI approved make list. | 2.00 | Nos | 10.00 | 180.00 | 360.00 | 220.00 | 440.00 | 250.00 | 500.00 | 360.00 | ANU ENGINEERING CORPORATION
51.00 | Supply and Installation of UL Listed Maintenance Free Copper coated Earth rod of 3048mm length having the dia of 17.2 mm with copper coating thickness of 254 microns. The rod has been tested for Dimension, Marking, Tensile Strength, Salt mist, coating thickness, Electrical resistivity test before and after corrosion test as per IEC 62561-2 & UL 467. Model - CAPE Type: CBR 1710 (Article No - 300 060) or equivalent as per AAI approved make list. Supply and Installation of earth enchancing mineral compound tested for leaching and TCLP with NABL accredited Lab as per IEC 62561-7 -25 kg Model - CAPE Type: PROSAN 12 (Article: 300 830) or equivalent as per AAI approved make list. Supply and Installation of Earth rod Clamp made up of copper coated for terminating cable / flat conductor. Model - CAPE Type:MSERC 1417 (Article: 300 462), CAPE Type: CPES 10 (Article: 400 504)or equivalent as per AAI approved make list. Supply and Installation of Earth Chamber Inspection Pit made up of poly propylene material. Model - CAPE Type: EC 300 (Article: 300 850) or equivalent as per AAI approved make list. | 2.00 | Nos | 10.00 | 10500.00 | 21000.00 | 10000.00 | 20000.00 | 10999.00 | 21998.00 | 20000.00 | NATIONAL SAFETY ENGINEERS
52.00 | IV-SURGE PROTECTION DEVICES
53.00 | Supply & Installation of Surge Protection Device Type 1/Class B with IP 65 Thermoplastic Enclosure Tested as per IEC 61643 Part 11:2011 in the main panel with following specification: Nominal voltage -230V 50/60Hz and MCOV ≥ 255 V , The Surge Protection Devices shall have TOV withstand (L-N/N-PE) ≥ 440 V for 120 min/1200 V for 200 ms. Lightning Impulse discharge current (L-N/N-PE) - 12.5 kA/50 kA (10/350µ sec) & Max Discharge current (L-N/N-PE) - 65 kA/100 kA (8/20µ sec). Follow Current: Not Allowed. Protective Elements are High Energy MOV & GDT and the Protection Modes for : 3 numbers of Type 1 + 2 SPD for connection between Phase and Neutral and one number of SPD between Neutral and Earth. Short- Circuit Current rating (Isccr) – 50 kA/50 Hz. Back up fuse shall be 315 AgG/gL. Health Status Indication required in all catridge and Remote monitoring facility. Total Response time (L-N/N-PE) < 25 ns / < 100ns. Model - CAPE (RAYCAP) ProTec T1H 300 (3+1)R or equivalent as per AAI approved make list. The supplier shall submit VDE test certificate (on line web link) for the above product | 1.00 | No | 10.00 | 51000.00 | 51000.00 | 48000.00 | 48000.00 | 47000.00 | 47000.00 | 47000.00 | MASTER ELECTRIC STORE
54.00 | SH-V:- Analogue Addressable Fire Detection and Alarm System
55.00 | Supplying, installation, testing and commission of intelligent addressable 2Lopp fire alarm system with 2 Loop Cardmicro processor based alarm panel, central processing unit with the following loop modules and capable of supporting not less then 159 Detectors & 159 Devices in one Loop. minimum up to 2 km, network communication card, minimum 80 character graphics / LCD display screen or other keypad and minimum 4000 events history log in the non volatile memory (EPROM), power supply unit (230 + 5% v, 50 hz), 48 hrs backup with 24 volt sealed maintenance free batteries with automatic charger. The panel shall have facility to connect printer to printout log and facility to have seamless integration with analog / digital voice evacuation system (which is part of the schedule of work under SH: PA system) and shall be complete with all accessories. The panel shall be compatible for IBMS system with open protocol BACnet / Modbus over IP complete as per specifications. (Make- Edward / Notifier / Simplex / Bosch).
55.01 | Two Loop Panel | 1.00 | No | 10.00 | 200000.00 | 200000.00 | 250000.00 | 250000.00 | 195000.00 | 195000.00 | 195000.00 | MASTER ELECTRIC STORE
56.00 | Supplying, installation, testing & commissioning of intelligent analog addressable photothermal detector complete with mounting base complete as required as per specifications. (Make- Edward / Notifier / Simplex / Bosch) | 25.00 | Nos | 10.00 | 3000.00 | 75000.00 | 2600.00 | 65000.00 | 3000.00 | 75000.00 | 65000.00 | NATIONAL SAFETY ENGINEERS
57.00 | Supplying, installation, testing & commissioning of fault isolator complete with base as required. (Make- Edward / Notifier / Simplex / Bosch) | 3.00 | Nos | 10.00 | 2800.00 | 8400.00 | 2500.00 | 7500.00 | 2800.00 | 8400.00 | 7500.00 | NATIONAL SAFETY ENGINEERS
58.00 | Supplying, installation, testing & commissioning of Relay Module complete with base as required. (Make- Edward / Notifier / Simplex / Bosch) | 2.00 | Nos | 10.00 | 3100.00 | 6200.00 | 2900.00 | 5800.00 | 3200.00 | 6400.00 | 5800.00 | NATIONAL SAFETY ENGINEERS
59.00 | Supplying, installation, testing & commissioning of Control Module complete with base as required. (Make- Edward / Notifier / Simplex / Bosch) | 5.00 | Nos | 10.00 | 3300.00 | 16500.00 | 2900.00 | 14500.00 | 2500.00 | 12500.00 | 12500.00 | MASTER ELECTRIC STORE
60.00 | Supplying, installation, testing & commissioning of addressable manual call point complete as required as per specifications. (Make- Edward / Notifier / Simplex / Bosch) | 2.00 | Nos | 10.00 | 2700.00 | 5400.00 | 2375.00 | 4750.00 | 3400.00 | 6800.00 | 4750.00 | NATIONAL SAFETY ENGINEERS
61.00 | Supplying, installation, testing & commissioning of addressable horn cum strobe complete as required as per specifications. (Make: Edward / Notifier / Simplex / Bosch) | 5.00 | Nos | 10.00 | 3300.00 | 16500.00 | 2140.00 | 10700.00 | 5100.00 | 25500.00 | 10700.00 | NATIONAL SAFETY ENGINEERS
62.00 | Supplying, installation, testing & commissioning of Response Indicators for all detectors located above false ceiling complete as required as per technical specifications. | 5.00 | Nos | 10.00 | 200.00 | 1000.00 | 500.00 | 2500.00 | 300.00 | 1500.00 | 1000.00 | ANU ENGINEERING CORPORATION
63.00 | Supplying & laying of 2x1.5 sqmm FRLS armoured cable, 600/1000V rated with annealed copper conductor having XLPE insulation, steel wire armouring & FRLS outer sheath complete as required. (Make: Polycab / Finolex / Havells) | 200.00 | Nos | 10.00 | 120.00 | 24000.00 | 150.00 | 30000.00 | 200.00 | 40000.00 | 24000.00 | ANU ENGINEERING CORPORATION
64.00 | SH-VI:- SITC of AC
65.00 | Supply of 1.5 TR Inverter type, 5 star BEE rating, Hi- wall, Split air-conditioner with rotary compressor operating on refrigerant R-32A/ R-410A. The body of indoor unit shall be made of ABS/HIPS/GS, condensing unit should be of 100% copper coil & having all safety, air filters, evaporator, condenser, cordless remote, electronic operation control & all accessories supplied with the unit by OEM etc as per manufacturer standards suitable for operation on 230 volts , 50 Hz, Single phase, AC supply, complete as required at site. | 10.00 | Each | 10.00 | 42500.00 | 425000.00 | 36000.00 | 360000.00 | 39000.00 | 390000.00 | 360000.00 | NATIONAL SAFETY ENGINEERS
66.00 | Installation, testing, commissioning of hi-wall A/C units etc. and making of necessary hole on concrete/brick wall and making good the damages i/c providing suitable size PVC pipe for drawing the gas/drain pipe and wire etc through the concrete/brick wall as required. | 10.00 | Each | 10.00 | 3000.00 | 30000.00 | 2500.00 | 25000.00 | 1600.00 | 16000.00 | 16000.00 | MASTER ELECTRIC STORE
67.00 | Supply and fitting of Appropriate size and thickness of MS Stand / L-Chair for fixing outdoor unit or Condensing Units along with necessary anchor fastner/bolt & nuts etc on concrete/brick wall or floor etc. as required. | 10.00 | Each | 10.00 | 1000.00 | 10000.00 | 800.00 | 8000.00 | 600.00 | 6000.00 | 6000.00 | MASTER ELECTRIC STORE
68.00 | Supply & fixing of extra copper refrigerant piping of standard gauge for installation of above units as required at site. | 30.00 | Meter | 10.00 | 800.00 | 24000.00 | 650.00 | 19500.00 | 600.00 | 18000.00 | 18000.00 | MASTER ELECTRIC STORE
69.00 | Supply & fixing of hard PVC drain piping of proper dia for installation of above units as required at site beyond company provided standard length. | 40.00 | Meter | 10.00 | 100.00 | 4000.00 | 90.00 | 3600.00 | 100.00 | 4000.00 | 3600.00 | NATIONAL SAFETY ENGINEERS
70.00 | Supply, Installing, Testing and Commissioning of Voltage Stabilizer suitable for 2 TR split AC units on wall including providing connections etc. as required. ( Model-V Guard VGB 500 or equivalent). | 10.00 | Meter | 10.00 | 4500.00 | 45000.00 | 3500.00 | 35000.00 | 4000.00 | 40000.00 | 35000.00 | NATIONAL SAFETY ENGINEERS
| Total in Figures |  |  |  |  | 1688010.00 |  | 1673250.00 |  | 1693669.00
Lowest Amount Quoted BY: NATIONAL SAFETY ENGINEERS(1673250.00)

## BOQ Summary
BOQ Summary Details Tender Title: Shifting of SMU NAV-AIDS from IGI Palam to RCDU Workshop Safdarjung Airport, New Delhi. SH Electrical Works. Tender ID: 2020_AAI_65702_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | NATIONAL SAFETY ENGINEERS | 1673250.00 | L1
| 2 | ANU ENGINEERING CORPORATION | 1688010.00 | L2
| 3 | MASTER ELECTRIC STORE | 1693669.00 | L3