## BoQ1
Government eProcurement System Created By: Chandrashekhar Sharma Created Date/Time: 15-Mar-2021 01:26 PM Tender Title: Establishment of roof top based Solar Power Plant (150 KWp) at C.A. Porbandar Tender ID: 2021_AAI_66812_1
Tender Inviting Authority: Asstt. General Manager (E-E)
Name of Work: Establishment of roof top based Solar Power Plant (150 KWp) at C.A.Porbandar.
Contract No: AAI/POR/AGM(E-E)/e-NIT-08/20-21 Tender ID: 2020_AAI_66812_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Emicon India Pvt Ltd(GSTN-07AABCE3574B1Z0) |  | Onix Structure Private limited(GSTN-24AADCE8197L1Z4) |  | M/s. Topsun Energy Limited(GSTN-24AACCT7455P1ZR) |  | SPJ SOLAR TECHNOLOGY PRIVET LIMITED(GSTN-09AAICA1590Q1Z2) |  | Metropolitan Infrabuild Development And Services Pvt Ltd(GSTN-09AAHCM2436Q1ZW) |  | CLASSIC SIGNAGES PVT LTD(GSTN-08AACCC1527D1Z6) |  | BOUNDLESS ENVIRONMEMNT RESOURCE SOLUTION PVT. LTD.(GSTN-07AAGCB6883K1Z5) |  | U R Energy India Pvt. Ltd.(GSTN-24AADCV8692D1Z4) |  | TROMINDUSTRIES LIMITED(GSTN-NA) |  | THANDON INFRASTRUCTURE PVT LTD(GSTN-NA) |  | starfield renewables pvt ltd(GSTN-NA) |  | FREYR ENERGY SERVICES PRIVATE LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing and Commissioning of ongrid Solar Photovoltaic Power Plant conforming to MNRE specifications as amended, consisting of Mono/Poly Crystalline silicon solar cells, net metering facility, necessary protections, earthing, mounted on Aluminium/GI structure of suitable strength with following components complete as required:- a) Solar Photovoltaic Module of capacity 330 Wp or above, manufactured in India, conforming to IS 14286/IEC 61215, IS/IEC 61730-Part-1, IS/IEC 61730-Part-2. Solar Photovoltaic Module conversion efficiency shall not be less than 16.5%. PV modules used in solar power plants/ systems must be warranted for their output peak watt capacity, which should not be less than 90% at the end of 10 years and 80% at the end of 25 years. b) Power Conditioning Unit (PCU) of 350-800 V DC Input voltage range and 400 V AC, three phase, 4 wire, 50Hz +/- 2.5 Hz, output voltage suitable to generate AC Power with efficiency not less than 97%, total harmonic distortion less than 3% and suitable for ambient temperature from 0 to 50 degree C. The PCU shall adjust the voltage and frequency level to suit the Grid Voltage Frequency. c) Data Monitoring System complete with accessories. d) Fixing of Array junction box & Main junction box with IP 65 protection and termination arrangement for incoming and outgoing cable along with glands, lugs and other accessories etc. as required. e) Lightning and surge voltage protection. f) Connections & Interconnections by supplying & fixing required size XLPE insulated copper conductor 1.1 kV grade armoured power and control cables between solar modules, main power cable to grid supply PCU unit along with supplying & fixing of necessary channel/conduit lugs and other accessories etc. complete with 5 years Comprehensive Maintenance Contract (i/c 2 years DLP) all as reqd. & as specified. (Capacity of Solar Plant=150 KWp) | 150.00 | Per KWp |  | 39000.00 | 5850000.00 | 50000.00 | 7500000.00 | 38210.00 | 5731500.00 | 38600.00 | 5790000.00 | 37550.00 | 5632500.00 | 42500.00 | 6375000.00 | 37000.00 | 5550000.00 | 47310.00 | 7096500.00 | 42500.00 | 6375000.00 | 45000.00 | 6750000.00 | 36370.00 | 5455500.00 | 50837.36 | 7625604.00 | 5455500.00 | starfield renewables pvt ltd
| Total in Figures |  |  |  |  | 5850000.00 |  | 7500000.00 |  | 5731500.00 |  | 5790000.00 |  | 5632500.00 |  | 6375000.00 |  | 5550000.00 |  | 7096500.00 |  | 6375000.00 |  | 6750000.00 |  | 5455500.00 |  | 7625604.00
Lowest Amount Quoted BY: starfield renewables pvt ltd(5455500.00)

## BOQ Summary
BOQ Summary Details Tender Title: Establishment of roof top based Solar Power Plant (150 KWp) at C.A. Porbandar Tender ID: 2021_AAI_66812_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | starfield renewables pvt ltd | 5455500.00 | L1
| 2 | BOUNDLESS ENVIRONMEMNT RESOURCE SOLUTION PVT. LTD. | 5550000.00 | L2
| 3 | Metropolitan Infrabuild Development And Services Pvt Ltd | 5632500.00 | L3
| 4 | M/s. Topsun Energy Limited | 5731500.00 | L4
| 5 | SPJ SOLAR TECHNOLOGY PRIVET LIMITED | 5790000.00 | L5
| 6 | Emicon India Pvt Ltd | 5850000.00 | L6
| 7 | CLASSIC SIGNAGES PVT LTD | 6375000.00 | L7
| 8 | TROMINDUSTRIES LIMITED | 6375000.00 | L7
| 9 | THANDON INFRASTRUCTURE PVT LTD | 6750000.00 | L8
| 10 | U R Energy India Pvt. Ltd. | 7096500.00 | L9
| 11 | Onix Structure Private limited | 7500000.00 | L10
| 12 | FREYR ENERGY SERVICES PRIVATE LIMITED | 7625604.00 | L11