## BoQ1
Government eProcurement System Created By: SUBBIAN VELUSWAMY SENTHIL KUMAR Created Date/Time: 22-Jan-2021 04:20 PM Tender Title: Replacement of Street Light cable of approach road of International Building at Vijayawada Airport Tender ID: 2021_AAI_66874_1
Tender Inviting Authority: Asst.General Manager [Engg-E], AAI, Vijayawada Airport
Name of Work: Replacement of Street Light cable of approach road of International Building at Vijayawada Airport.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | switchgearcontrols(GSTN-37AHSPG9876H2ZF) |  | SRI RAGHAVENDRA ELECTRICALS(GSTN-36AJHPP7899J1Z7) |  | DEEPAKELECTRICALS(GSTN-33ALUPD3531C1ZI) |  | NAGASURYA CONTRACTORS(GSTN-37BGAPR4634J1Z5) |  | Ruchira Associates(GSTN-37AAQFR2340N1ZO) |  | SREE KRISHNA ENTERPRISES(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of 1.1KV grade 4C 16 Sq.mm. armoured aluminium conductor XLPE insulated and PVC sheathed cable conforming to IS - 7098 (Part - I) 1988 respectively with upto date amendments. | 1000.00 | Mtrs. |  | 119.00 | 119000.00 | 116.00 | 116000.00 | 110.00 | 110000.00 | 118.00 | 118000.00 | 115.00 | 115000.00 | 110.00 | 110000.00 | 110000.00 | DEEPAKELECTRICALS, SREE KRISHNA ENTERPRISES
2.00 | Supply of 1.1KV grade 3C X2.5 Sq.mm. PVC Insulated Flexible PVC Round sheathed copper conductor conforming to IS - 694 respectively with upto date amendments. | 1000.00 | Mtrs. |  | 78.00 | 78000.00 | 80.00 | 80000.00 | 75.00 | 75000.00 | 82.00 | 82000.00 | 110.00 | 110000.00 | 75.00 | 75000.00 | 75000.00 | DEEPAKELECTRICALS, SREE KRISHNA ENTERPRISES
3.00 | Supply of 120W LED Street Light Fitting (Efficacy min. 110 Lumens/watt) housed in pressure Die-Cast/Aluminium Alloy, IP66 protection. 4KV Surge protection and suitable for operation on 230V, 50Hz AC supply complete as required. | 86.00 | Nos. |  | 7000.00 | 602000.00 | 2900.00 | 249400.00 | 8500.00 | 731000.00 | 5980.00 | 514280.00 | 7000.00 | 602000.00 | 5400.00 | 464400.00 | 249400.00 | SRI RAGHAVENDRA ELECTRICALS
4.00 | Supply of Single Pole, 6 amps to 32 amps rating, 240/ 415 volts, 10 kA, “C” curve,miniature circuit breakers. | 80.00 | Nos. |  | 120.00 | 9600.00 | 115.00 | 9200.00 | 175.00 | 14000.00 | 200.00 | 16000.00 | 130.00 | 10400.00 | 150.00 | 12000.00 | 9200.00 | SRI RAGHAVENDRA ELECTRICALS
5.00 | Replacement of Existing 2 Nos. 120 Watt LED street light fitting with new fittings on 9mtr. Height DOUBLE BRACKET street light pole including providing new 16 Sq.mm feed through connectors etc. Checking and replacement of MCB and trailing 3C 2.5 Sq.mm. cable, connection, testing and commissioning etc. as required. | 40.00 | Job |  | 450.00 | 18000.00 | 150.00 | 6000.00 | 400.00 | 16000.00 | 1000.00 | 40000.00 | 2500.00 | 100000.00 | 1500.00 | 60000.00 | 6000.00 | SRI RAGHAVENDRA ELECTRICALS
6.00 | Supplying and Laying of 63 mm OD HDPE pipe PN4,PE63 ISI marked conforming to IS 4984, Part II and Laying direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective convering with all accessories, cutting, jointing etc. complete as required. | 250.00 | Mtrs. |  | 150.00 | 37500.00 | 240.00 | 60000.00 | 250.00 | 62500.00 | 180.00 | 45000.00 | 85.00 | 21250.00 | 570.00 | 142500.00 | 21250.00 | Ruchira Associates
7.00 | Supplying and Laying of 40mm OD HDPE pipe PN4,PE63 ISI marked conforming to IS 4984, Part II and Laying direct in ground (30 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective convering with all accessories, cutting, jointing etc. complete as required. | 1000.00 | Mtrs |  | 100.00 | 100000.00 | 216.00 | 216000.00 | 180.00 | 180000.00 | 120.00 | 120000.00 | 45.00 | 45000.00 | 500.00 | 500000.00 | 45000.00 | Ruchira Associates
8.00 | Laying of one number XLPE insulated and PVC sheathed power cable of 1.1KV grade of size 35 sq. mm and upto 95 sq. mm in the existing RCC/ HUME/ METAL/HDPE pipe as required. | 100.00 | Mtrs. |  | 30.00 | 3000.00 | 30.00 | 3000.00 | 25.00 | 2500.00 | 10.00 | 1000.00 | 110.00 | 11000.00 | 50.00 | 5000.00 | 1000.00 | NAGASURYA CONTRACTORS
9.00 | Laying of one number XLPE insulated and PVC sheathed power cable of 1.1KV grade of size upto 35 sq.mm. in the existing RCC/ HUME/ METAL /HDPE pipe as required. | 1000.00 | Mtrs. |  | 30.00 | 30000.00 | 25.00 | 25000.00 | 25.00 | 25000.00 | 40.00 | 40000.00 | 75.00 | 75000.00 | 35.00 | 35000.00 | 25000.00 | SRI RAGHAVENDRA ELECTRICALS, DEEPAKELECTRICALS
10.00 | Laying of one number XLPE insulated and PVC sheathed power cable of 1.1 KV grade of size upto 35 sq. mm. in the existing masonry open duct as required. | 100.00 | Mtrs. |  | 25.00 | 2500.00 | 35.00 | 3500.00 | 25.00 | 2500.00 | 10.00 | 1000.00 | 70.00 | 7000.00 | 35.00 | 3500.00 | 1000.00 | NAGASURYA CONTRACTORS
11.00 | Laying and fixing of one number XLPE insulated and PVC sheathed power cable of 1.1 KV grade of following size Upto 35 sq. mm (clamped with 1mm thick saddle) on wall surface as required. | 100.00 | Mtrs. |  | 35.00 | 3500.00 | 40.00 | 4000.00 | 45.00 | 4500.00 | 10.00 | 1000.00 | 75.00 | 7500.00 | 35.00 | 3500.00 | 1000.00 | NAGASURYA CONTRACTORS
12.00 | Supply and Laying 50mm dia G.I. pipe (medium class) complete with G.I. fittings at a depth of 300mmm for road crossing including bitumin cutting, earth cutting and finished with concrete (1:2:4) of 150mm thick etc. as required. | 30.00 | Mtrs. |  | 900.00 | 27000.00 | 900.00 | 27000.00 | 650.00 | 19500.00 | 900.00 | 27000.00 | 200.00 | 6000.00 | 750.00 | 22500.00 | 6000.00 | Ruchira Associates
13.00 | Supply and Laying 150mm dia G.I. pipe (medium class) complete with G.I. fittings at a depth of 300mmm for road crossing including bitumin cutting, earth cutting and finished with concrete (1:2:4) of 150mm thick etc. as required. | 24.00 | Mtrs. |  | 2300.00 | 55200.00 | 2200.00 | 52800.00 | 2100.00 | 50400.00 | 1500.00 | 36000.00 | 400.00 | 9600.00 | 1500.00 | 36000.00 | 9600.00 | Ruchira Associates
14.00 | Supplying and making end termination with Double Compression Flame Proof brass gland for 3.5C 70Sq.mm. Size PVC/XLPE insulated and PVC sheathed armoured aluminium conductor cable of 1.1kv grade as required. | 4.00 | Nos. |  | 945.00 | 3780.00 | 1000.00 | 4000.00 | 500.00 | 2000.00 | 450.00 | 1800.00 | 450.00 | 1800.00 | 750.00 | 3000.00 | 1800.00 | NAGASURYA CONTRACTORS, Ruchira Associates
15.00 | Supplying and making end termination with Double Compression Flame Proof brass compression gland for 3.5C 35 Sq.mm. Size PVC/XLPE insulated and PVC sheathed armoured aluminium conductor cable of 1.1kv grade as required. | 6.00 | Nos. |  | 755.00 | 4530.00 | 700.00 | 4200.00 | 450.00 | 2700.00 | 450.00 | 2700.00 | 400.00 | 2400.00 | 350.00 | 2100.00 | 2100.00 | SREE KRISHNA ENTERPRISES
16.00 | Supplying and making end termination with Double Compression Flame Proof brass compression gland for 4C 16 Sq.mm. Size PVC/XLPE insulated and PVC sheathed armoured aluminium conductor cable of 1.1kv grade as required. | 4.00 | Nos. |  | 600.00 | 2400.00 | 500.00 | 2000.00 | 400.00 | 1600.00 | 450.00 | 1800.00 | 350.00 | 1400.00 | 200.00 | 800.00 | 800.00 | SREE KRISHNA ENTERPRISES
17.00 | Supply ,Installtion, Testing And commisioning of out door MV Feeder Pillar Panel ,double door type completely made up of 14 SWG CRCA sheet steel, door dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing, including providing and fixing 200 A Four Pole Aluminium Bus bar with all accessories suitable for operation at 415 V, 3 phase, 4 wire, 50 Hz, A.C. Power Supply System complete with all accessories, interconnection, connection, earthing, painting, grouting, Cable Entry provision, suitabele RCC fouundation etc. complete as required and comprising the following: a. 160A, 36 KA, 4P MCCB with Microprocessor based releases as incomer with R,Y,B,ON, OFF, Trip indication lamps, resin cast CT's with multifuction meter (Schheider EM 6459 or Equivalent)- 1 sets as incomer b. 32A, 25KA, 4P MCCB with TM based releases with ON, OFF, Trip indication lamps as outgoing - 4 Sets. As outgoing c) spare compartment for feature out goings (With out switch gear)-2 numbers d) with all necessary accessories etc. complete as required. | 1.00 | Nos. |  | 165500.00 | 165500.00 | 173000.00 | 173000.00 | 145000.00 | 145000.00 | 75000.00 | 75000.00 | 200000.00 | 200000.00 | 105000.00 | 105000.00 | 75000.00 | NAGASURYA CONTRACTORS
18.00 | Supply ,Installtion, Testing And commisioning of out door MV Feeder Pillar Panel ,double door type completely made up of 14 SWG CRCA sheet steel, door dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing, including providing and fixing 100 A Four Pole Aluminium Bus bar with all accessories suitable for operation at 415 V, 3 phase, 4 wire, 50 Hz, A.C. Power Supply System complete with all accessories, interconnection, connection, earthing, painting, grouting, Cable Entry provision, suitabele RCC fouundation etc. complete as required and comprising the following: a. 63 A, 36 KA, 4P MCCB with Microprocessor based releases as incomer with R,Y,B,ON, OFF, Trip indication lamps, resin cast CT's with multifuction meter (Schheider EM 6459 or Equivalent)- 1 sets as incomer b. 32A, 25KA, 4P MCCB with TM based releases with ON, OFF, Trip indication lamps as outgoing - 2 Sets. As outgoing c) spare compartment for feature out goings (With out switch gear)-2 sets d) with all necessary accessories etc. complete as required. | 1.00 | Nos. |  | 147500.00 | 147500.00 | 170000.00 | 170000.00 | 130000.00 | 130000.00 | 55000.00 | 55000.00 | 145000.00 | 145000.00 | 88500.00 | 88500.00 | 55000.00 | NAGASURYA CONTRACTORS
19.00 | Providing and Fixing 6 SWG dia G.I. wire for loop earthing along with existing cable as required. | 1000.00 | Mtr. |  | 30.00 | 30000.00 | 35.00 | 35000.00 | 36.00 | 36000.00 | 50.00 | 50000.00 | 10.00 | 10000.00 | 35.00 | 35000.00 | 10000.00 | Ruchira Associates
20.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 20.00 | Mtr. |  | 150.00 | 3000.00 | 150.00 | 3000.00 | 120.00 | 2400.00 | 150.00 | 3000.00 | 95.00 | 1900.00 | 150.00 | 3000.00 | 1900.00 | Ruchira Associates
21.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 20.00 | Mtr. |  | 100.00 | 2000.00 | 300.00 | 6000.00 | 130.00 | 2600.00 | 200.00 | 4000.00 | 105.00 | 2100.00 | 150.00 | 3000.00 | 2000.00 | switchgearcontrols
22.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc.as required. | 4.00 | Mtr. |  | 450.00 | 1800.00 | 500.00 | 2000.00 | 250.00 | 1000.00 | 460.00 | 1840.00 | 215.00 | 860.00 | 250.00 | 1000.00 | 860.00 | Ruchira Associates
23.00 | Earthing with GI earth pipe 4.5 meter long ,40 mm dia including accessories and providing masonary enclosure with cover plate having locking arrangemnt and watering pipe etc. with charcoal/coke and salt as required. | 4.00 | Nos. |  | 4375.00 | 17500.00 | 25000.00 | 100000.00 | 6500.00 | 26000.00 | 5500.00 | 22000.00 | 3500.00 | 14000.00 | 3500.00 | 14000.00 | 14000.00 | Ruchira Associates, SREE KRISHNA ENTERPRISES
24.00 | Supplying and Fixing Cable Route Marker with Cement concrete 1:2:4 (1 Cement: 2 Coarse Sand : 4 graded stone aggregate 20mm nominal size) of size 50cmx60cm at the bottom and 50cmx50cm at the top with a thickness of 10cm including inscription duly engraved as required. | 20.00 | Nos. |  | 365.00 | 7300.00 | 400.00 | 8000.00 | 400.00 | 8000.00 | 650.00 | 13000.00 | 1500.00 | 30000.00 | 250.00 | 5000.00 | 5000.00 | SREE KRISHNA ENTERPRISES
25.00 | Providing and fixing following capacity MCCB inside the existing panel board (including dismantling the existing MCCB if required) including drilling holes in cubicle panel, making connections, etc. as required. - 250 Amps,36 KA, 4P MCCB ,Micro processor based with rotary handle, spreader terminal and phase barriers etc. [Similar to L&T make: DN Series with MTX 1.0 or Its equivalent] | 2.00 | Nos. |  | 22178.00 | 44356.00 | 40000.00 | 80000.00 | 20000.00 | 40000.00 | 25000.00 | 50000.00 | 6000.00 | 12000.00 | 16500.00 | 33000.00 | 12000.00 | Ruchira Associates
26.00 | Repair/Modifiction of existing 9 mtr Octogonal pole junction box cover , inculding dismentling cover & making good in shape, re fixing with hinges, nut & bolt , making locking arrangemnt etc. as per site condition. | 50.00 | Nos. |  | 265.00 | 13250.00 | 300.00 | 15000.00 | 350.00 | 17500.00 | 500.00 | 25000.00 | 3500.00 | 175000.00 | 900.00 | 45000.00 | 13250.00 | switchgearcontrols
| Total in Figures |  |  |  |  | 1528216.00 |  | 1454100.00 |  | 1707700.00 |  | 1346420.00 |  | 1716210.00 |  | 1807800.00
Lowest Amount Quoted BY: NAGASURYA CONTRACTORS(1346420.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Street Light cable of approach road of International Building at Vijayawada Airport Tender ID: 2021_AAI_66874_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | NAGASURYA CONTRACTORS | 1346420.00 | L1
| 2 | SRI RAGHAVENDRA ELECTRICALS | 1454100.00 | L2
| 3 | switchgearcontrols | 1528216.00 | L3
| 4 | DEEPAKELECTRICALS | 1707700.00 | L4
| 5 | Ruchira Associates | 1716210.00 | L5
| 6 | SREE KRISHNA ENTERPRISES | 1807800.00 | L6