## BoQ1
Government eProcurement System Created By: Jyoti Prakash chauhan Created Date/Time: 17-Mar-2021 04:22 PM Tender Title: Augmentation of power supply system, substation and allied work at CATC Allahabad. SH-Replacement of existing LT Panels of 33 KV Substation Tender ID: 2021_AAI_66875_1
Tender Inviting Authority:- Sr. Manager (Engg-E), Airports Authority of India, Engineering Section, CATC, Prayagraj
Name of Work:- Augmentation of power supply system, substation and allied work at CATC Allahabad. SH:-Replacement of existing LT Panels of 33 KV Sub station
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ECS ENGINEERING PVT LTD(GSTN-09AABCE5944P1Z1) |  | SARASWAT ENGINEERING SERVICES(GSTN-27AAZFS6239C1ZO) |  | DOSHI ELECTRIC ENGG. CO.(GSTN-24AAEFD3355K1ZI) |  | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION(GSTN-09AOTPS2578C1ZC) |  | JITENDRA ELECTRICALS(GSTN-24AACFJ9752E1ZE) |  | MEC ENGINEERS(GSTN-09AABFM1296R1ZM) |  | TECHNISYS ENGINEERING PRIVATE LIMITED(GSTN-06AACCT8886E1ZZ) |  | Deora Electricals(GSTN-09ACWPD8018R1ZN) |  | Choubay And Co.(Agencies) Pvt.Ltd.(GSTN-09AAACC6073E1ZT) |  | Incotech Engineers Pvt Ltd(GSTN-19AAACI5242B1ZZ) |  | KRISHNA REFRIGERATION(GSTN-09AGYPK1790P1Z9) |  | Power And Instrumentation Guj Ltd(GSTN-24AACCP4292Q1ZW) |  | shiv electric(GSTN-07AACFS2722H1ZF) |  | Shekhawati Electrical Engineers(GSTN-08AGWPS9218G2ZK) |  | Manish Electricals(GSTN-22ABLPM9012E1ZY) |  | RASS CONTRACTOR AND ENGINEERS(GSTN-09AFIPR1600N1Z7) |  | Aditya Techno Products Private Limited(GSTN-NA) |  | Brilltech Engineers Pvt. Ltd.(GSTN-NA) |  | GAYATRI ELECTRICAL(GSTN-NA) |  | RISHA CONTROL ENGINEERS PRIVATE LIMITED(GSTN-NA) |  | Actech Engineers(GSTN-NA) |  | Jha power corporation(GSTN-NA) |  | Water Power Engg. Enterprises(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-A :- LT PANEL BOARD AND ACCESSORIES AT SUB STATION
2.00 | Design, manufacture supply, installation, testing and commissioning of Main LT Panel, as per IEC 61439, cubicle & modular type, made of 2 mm thick electro galvanized steel sheets /Aluzinc Sheet Steel for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 54, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing complete with 9 tank process, powder coated, painting, with front face having openable transparent tempered glass door with PU gasket complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Al.busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS. PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items and as per detailed technical specification: (For details please refer technical specifications) | 1.00 | Job | 10.00 | 2678000.00 | 2678000.00 | 4255000.00 | 4255000.00 | 3200000.00 | 3200000.00 | 2545000.00 | 2545000.00 | 2872000.00 | 2872000.00 | 2900000.00 | 2900000.00 | 3037107.00 | 3037107.00 | 4638501.00 | 4638501.00 | 4350000.00 | 4350000.00 | 3425435.00 | 3425435.00 | 2100000.00 | 2100000.00 | 4577304.00 | 4577304.00 | 3000000.00 | 3000000.00 | 6000000.00 | 6000000.00 | 4978500.00 | 4978500.00 | 2850000.00 | 2850000.00 | 3132000.00 | 3132000.00 | 3458376.00 | 3458376.00 | 4399999.00 | 4399999.00 | 3095000.00 | 3095000.00 | 3485000.00 | 3485000.00 | 3000000.00 | 3000000.00 | 4170000.00 | 4170000.00 | 2100000.00 | KRISHNA REFRIGERATION
3.00 | INCOMER
4.00 | 2500A 4P ACB with microprocessor based current metering & graphical display release , EDO, 65KA = Icu = Ics = Icw, with LSING Protection with Under voltage release, Shunt Release, Closing Release. ACB protection release shall have LCD display of current , shall be fully compatible and ready to use for measurement of Current, voltage, energy parameters & having modbus,RS 485 communication . ACB shall have electrical & mechanical key interlocking. Suitable links and bus duct entry flange shall be provided for 2500 A termination - 02 nos
5.00 | Indication Lamps, LED type for R,Y,B and breaker 'ON' , spring charge, healthy circuit 'OFF', 'TRIP' indications each with 2 Amp MCBs for protection for both incomers
6.00 | Breaker control switch (TNC switch)-02 nos
7.00 | Feeder protection relay (Numeric)-02 nos
8.00 | Metering & indications
9.00 | 96 mm square flush pattern digital Voltmeter(0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 2 Sets
10.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-2500A), for 3 phase 4 wire operation with LED display and selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 2 sets.
11.00 | Digital multi function digital meter to read V,A,KVA, KW, KVAR, KWH, PF, Hz etc with communication module (RS485) and LED display with 3 Nos CTs, 15 VA, class 1.0 and control circuit wiring with 2 Amp. SP MCBs.-2 sets.
12.00 | 3 Nos, 2500/5A, CL 0.5 , 15 VA, Cast Resin CTs for metering- 2 sets
13.00 | Breaker control switch (TNC switch)-02 nos
14.00 | BUS COUPLER
15.00 | 2500A, 4P, ACB with microprocessor based current metering & graphical display release , EDO, 65KA= Icu = Ics = Icw, with Under voltage release. ACB protection release shall have LCD display of current , shall be fully compatible and ready to use for measurement of Current, voltage, energy parameters & having modbus,RS 485 communication ACB shall have electrical & mechanical key interlocking -01 No
16.00 | Breaker control switch (TNC switch)-01 nos
17.00 | phase Indication Lamps, LED type for R,Y,B and breaker 'ON' , spring charge, healthy circuit 'OFF', 'TRIP' indications each with 2 Amp MCBs for protection.
18.00 | BUSBARS
19.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 2500 Amps capacity, TPN with heat shrinkable colored sleeves and ,non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
20.00 | Accessories for Electrical & Mechanical Interlocking
21.00 | Electrical & mechanical interlocking arrangement as per specifications among 2 nos. Incomers for transformers and 1 Bus coupler including interconnections etc. as required.
22.00 | OUTGOING
23.00 | 1600A 4P ACB with microprocessor based current metering & graphical display release , EDO, 50KA = Icu = Ics = Icw, with LSING Protection with Under voltage release, Closing Release, Shunt Release. CB protection release shall have LCD display of current , shall be fully compatible and ready to use for measurement of Current, voltage, energy parameters & having modbus,RS 485 communication. ACB shall have electrical & mechanical key interlocking- 02 nos
24.00 | 96 mm square flush pattern digital Voltmeter(0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 2 Sets
25.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-2500A), for 3 phase 4 wire operation with LED display and selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 2 sets.
26.00 | Digital multi function digital meter to read V,A,KVA, KW, KVAR, KWH, PF, Hz etc with communication module (RS485) and LED display with 3 Nos CTs, 15 VA, class 1.0 and control circuit wiring with 2 Amp. SP MCBs.-2 sets.
27.00 | 2 Nos, 2500/5A/5A, 15 VA, Cast Resin CTs accuracy class 0.5 for metering - 02 sets
28.00 | 2 Nos. of 800 A, FP, 50 kA, MCCB with Microprocessor based release having adjustable over load and adjustable short circuit, earth fault protection inbuilt with release
29.00 | 1 Nos. of 630 A, FP, 36 kA, MCCB with Microprocessor based release having adjustable over load and adjustable short circuit, earth fault protection inbuilt with release
30.00 | 4 Nos. of 400 A, FP, 36 kA, MCCB with Microprocessor based release having adjustable over load and adjustable short circuit, earth fault protection inbuilt with release
31.00 | 01 Nos. of 320 A, FP, 36 kA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit
32.00 | 09 Nos. of 200A, FP, 36 kA, MCCB with thermal magnetic release having adjustable over load and adjustable short circuit protection
33.00 | Note- All MCCBs should have (1) Ics = Icu at 415 V (2) Rotary operating mechanism and terminal extension / spreaders (3) ON/OFF Indication (4) All MCCBs shall be current limiting type
34.00 | MAIN ESSENTIAL (Synchronizing panel)
35.00 | Design, manufacture supply, installation, testing and commissioning of synchronizing cum LT Panel, as pr IEC 61439, cubicle & modular type, made of 2 mm thick electro galvanized steel sheets /Aluzinc Sheet Steel for frame work and covers, 3 mm thick for gland plates, totally enclosed, IP 54 , free standing, floor mounting, dust and vermin proof, indoor, compartmentalized, including cleaning & finishing complete with 9 tank process, powder coated, painting, with front face having openable transparent tempered glass door with PU gasket complete with handle and gasket, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Al.busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common earth bar of suitable size at the rear with 2 nos. earth stud, control wiring with FRLS. PVC insulated copper conductor, cable allays, cable gland plates in two half, interconnections including supply & installation of following items i/c providing & installation of suitable PLC as required and as per technical specification: (For details please refer technical specifications) | 1.00 | Job | 10.00 | 5733000.00 | 5733000.00 | 5692500.00 | 5692500.00 | 6500000.00 | 6500000.00 | 4857000.00 | 4857000.00 | 5940000.00 | 5940000.00 | 5200000.00 | 5200000.00 | 5691047.00 | 5691047.00 | 6971751.00 | 6971751.00 | 5767000.00 | 5767000.00 | 6325220.00 | 6325220.00 | 4926829.00 | 4926829.00 | 6115368.00 | 6115368.00 | 5800000.00 | 5800000.00 | 6500000.00 | 6500000.00 | 7682000.00 | 7682000.00 | 6750000.00 | 6750000.00 | 6050000.00 | 6050000.00 | 5376210.00 | 5376210.00 | 5837999.00 | 5837999.00 | 5070000.00 | 5070000.00 | 6165000.00 | 6165000.00 | 5500000.00 | 5500000.00 | 7550000.00 | 7550000.00 | 4857000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
36.00 | INCOMER
37.00 | 1600A 4 pole with neutral contactor ACB with microprocessor based current metering & graphical display release , EDO, 50KA = Icu = Ics = Icw, with LSING Protection with Under voltage release, Shunt Release, Closing Release. CB protection release shall have LCD display of current , shall be fully compatible and ready to use for measurement of Current, voltage, energy parameters & having modbus,RS 485 communication. ACB shall have electrical & mechanical key interlocking- 02 nos
38.00 | 1250A 3 pole with neutral contactor ACB with microprocessor based current metering & graphical display release , EDO, 50KA = Icu = Ics = Icw, with LSING Protection with Under voltage release, Shunt Release, Closing CB protection release shall have LCD display of current , shall be fully compatible and ready to use for measurement of Current, voltage, energy parameters & having modbus,RS 485 communication. ACB shall have electrical & mechanical key interlocking- 03 nos
39.00 | Indication Lamps, LED type for R,Y,B and breaker 'ON' , spring charge, healthy circuit 'OFF', 'TRIP' indications each with 2 Amp MCBs for protection for above breakers
40.00 | Breaker control switch (TNC switch) for above breakers
41.00 | Metering & indications
42.00 | 96 mm square flush pattern digital Voltmeter(0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 5 Sets
43.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-1600A), for 3 phase 4 wire operation with LED display and selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 5 sets.
44.00 | Digital multi function digital meter to read V,A,KVA, KW, KVAR, KWH, PF, Hz etc with communication module (RS485) and LED display with 3 Nos CTs, 15 VA, class 1.0 and control circuit wiring with 2 Amp. SP MCBs.-5 sets.
45.00 | 1600 or 1250/5A, CL 0.5 , 15 VA, Cast Resin CTs for metering- 5 sets
46.00 | BUS COUPLER
47.00 | 1600A 4 pole with neutral contactor ACB with microprocessor based current metering & graphical display release , EDO, 50KA = Icu = Ics = Icw, with LSING Protection with Under voltage release, Shunt Release, Closing Release.CB protection release shall have LCD display of current , shall be fully compatible and ready to use for measurement of Current, voltage, energy parameters & having modbus,RS 485 communication. ACB shall have electrical & mechanical key interlocking- 02 nos
48.00 | Breaker control switch (TNC switch)-02 nos
49.00 | phase Indication Lamps, LED type for R,Y,B and breaker 'ON' , spring charge, healthy circuit 'OFF', 'TRIP' indications each with 2 Amp MCBs for protection.
50.00 | BUSBARS
51.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 2500 Amps capacity, TPN with heat shrinkable colored sleeves andnon-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
52.00 | Accessories for Electrical & Mechanical Interlocking
53.00 | Electrical interlocking arrangement as per specifications among incoming & outgoing, bus couplers ACB including interconnections etc. as required.
54.00 | OUTGOING
55.00 | 1000A 4P ACB with microprocessor based release current metering & graphical LCD display , EDO, 50KA = Icu = Ics = Icw, with LSING Protection. - 01 nos
56.00 | 1250A 4P ACB with microprocessor based release current metering & graphical LCD display , EDO, 50KA = Icu = Ics = Icw, with LSING Protection. - 01 nos
57.00 | Indication Lamps, LED type for R,Y,B and breaker 'ON', spring charge, healthy circuit 'OFF', 'TRIP' indications each with 2 Amp MCBs for protection.- 02 set
58.00 | Breaker control switch (TNC switch)-02 nos
59.00 | 13 Nos. of 400 A, FP, 36 kA, MCCB with Microprocessor based release having adjustable over load and adjustable short circuit, earth fault protection inbuilt with release
60.00 | 14 Nos. of 320 A, FP, 36 kA, MCCB with thermal magnetic based release having adjustable over load and adjustable short circuit
61.00 | 11 Nos. of 250A, FP, 36 kA, MCCB with thermal magnetic release having adjustable over load and adjustable short circuit protection
62.00 | 09 Nos. of 200A, FP, 36 kA, MCCB with thermal magnetic release having adjustable over load and adjustable short circuit protection
63.00 | 02 Nos. of 125A, FP, 36 kA, MCCB with thermal magnetic release having adjustable over load and adjustable short circuit protection
64.00 | Note- All MCCBs should have (1) Ics = Icu at 415 V (2) Rotary operating mechanism and terminal extension / spreaders (3) ON/OFF Indication (4) All MCCBs shall be current limiting type
65.00 | CAPACITOR PANEL
66.00 | Design, supply, installation, testing and commissioning of Automatic Power Factor Corrector Panel, modular type 400 kVAR, 3ph, 4 wire, 415v, with capacitor duty contactor, totally enclosed, IP 42, free standing, floor mounting, dust and vermin proof, cubicle type to be fabricated out of min. 2 mm thick Sheet steel, with provision for capacitor mounting arrangement inside the panel with Aluminium Busbars, interconnections, adequate number of louvers and powder coated with approved shade including supply & installation of following components and as per detailed technical specifications: (For details please refer technical specifications) | 2.00 | Job | 10.00 | 450000.00 | 900000.00 | 456550.00 | 913100.00 | 484000.00 | 968000.00 | 500000.00 | 1000000.00 | 478000.00 | 956000.00 | 450000.00 | 900000.00 | 640164.00 | 1280328.00 | 830637.00 | 1661274.00 | 446000.00 | 892000.00 | 565192.00 | 1130384.00 | 578049.00 | 1156098.00 | 495780.00 | 991560.00 | 550000.00 | 1100000.00 | 525000.00 | 1050000.00 | 558786.00 | 1117572.00 | 525000.00 | 1050000.00 | 565000.00 | 1130000.00 | 400000.00 | 800000.00 | 501999.00 | 1003998.00 | 600000.00 | 1200000.00 | 485000.00 | 970000.00 | 650000.00 | 1300000.00 | 650000.00 | 1300000.00 | 800000.00 | Brilltech Engineers Pvt. Ltd.
67.00 | INCOMER
68.00 | 1 Nos. of 800 A, TP, Ics=Icu=36 kA, MCCB with Microprocessor based release having adjustable over load and adjustable short circuit-01No
69.00 | 96 mm square flush pattern digital Voltmeter(0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP MCBs.- 1 set
70.00 | 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-800A), for 3 phase 4 wire operation with LED display and selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 1 set.
71.00 | 1 Set of Microprocessor based intelligent, 16 step APFC relay with PF display with three CT sensing for better PF in case of unbalance systems along with auto/manual mode selection switch (refer detailed specification)
72.00 | 1 Set of Indication Lamps, LED type, R,Y,B each with 2 Amp. SP MCB for protection.
73.00 | 1 no. Intelligent multi function digital meter to read V, A, KVA, KW, KVAR, PF, Hz etc with communication facility (RS485 module) and LED display with CTs 800A/5A/5A, 15 VA burden, class 0.5 accuracy for metering and control circuit wiring with 2 Amp. SP MCBs for protection.
74.00 | BUSBARS
75.00 | 1 set of high conductivity Aluminium electrolytic grade, bus bars of minimum 800 Amps capacity, TPN with heat shrinkable colored sleeves and non-combustible, non-hygroscopic, high strength SMC/ DMC/Polymer material bus bars supports at required intervals.
76.00 | CAPACITORS- 400 KVAR
77.00 | 4 nos. 50 KVAR Heavy duty Metallised Poly Propylene Capacitor . Each with capacitor duty contactor , MCCB 100A,TP, 36 KA thermal release with adjustable O/L & Short circuit protection, spreaders, and rotary handle.
78.00 | 6 nos. 25 KVAR Heavy duty Metallised Poly Propylene Capacitor . Each with capacitor duty contactor, MCBs, 63A, TP, 10kA
79.00 | 2 nos. 12.5 KVAR Heavy duty Metallised Poly Propylene Capacitor . Each with capacitor duty contactor MCBs, 32A, TP, 10kA
80.00 | 2 nos. 10 KVAR Heavy duty Metallised Poly Propylene Capacitor . Each with capacitor duty contactor MCBs, 20A, TP, 10kA
81.00 | 1 nos. 5 KVAR Heavy duty Metallised Poly Propylene Capacitor . Each with capacitor duty contactor MCBs, 10A, TP, 10kA
82.00 | ON/OFF push button & ON/OFF LED type indication with 2 Amp SP MCB for protection for each capacitor bank
83.00 | Axial flow fans with thermostat.
84.00 | Note- Ics = Icu upto 415V for all MCCB. Rotary operating mechanism and terminal extension / spreaders shall be provided to all the MCCBs.
85.00 | SH-B
86.00 | Supplying, installing by suspension on ceiling, testing and commissioning of following capacity sandwich type Rising Mains as per IEC 61439 for use on 3 phase 4 pole , 50Hz A.C. supply with metal clad enclosure having IP-55 rating after fixing the tap off boxes and all accessories, made of 1.6 mm thick GI sheet duly powder coated in convenient sections complete with aluminium bus bars at nominal current rating, necessary joints, elbow joints & expansion joints and bends, provision of tapping at every metre, adopter box and copper flexible for joints, continuous earthing with 2 Nos aluminium strip of suitable size including, G.I. clamping brackets, suspenders, angle iron bracket, steel fasteners, connecting to earthing system etc. as required Note: The bus trunking shall be measured along the length of enclosure. The strips which will go inside LT panels & end termination boxes of transformer shall not be taken into measurement of bus trunking quantity. Job also includes dismantling the existing bus duct by removing the electrical connections, earthing, and shifting up to AAI store (For details please refer technical specifications)
87.00 | 2500 Amp, 50 KA, 4 pole sandwich type Bus Duct | 42.00 | Meter | 10.00 | 31600.00 | 1327200.00 | 35403.00 | 1486926.00 | 25000.00 | 1050000.00 | 28000.00 | 1176000.00 | 27800.00 | 1167600.00 | 34000.00 | 1428000.00 | 46682.00 | 1960644.00 | 36398.70 | 1528745.40 | 47000.00 | 1974000.00 | 40980.00 | 1721160.00 | 29878.00 | 1254876.00 | 28644.00 | 1203048.00 | 19000.00 | 798000.00 | 25000.00 | 1050000.00 | 30000.00 | 1260000.00 | 25500.00 | 1071000.00 | 32590.00 | 1368780.00 | 20702.00 | 869484.00 | 49999.00 | 2099958.00 | 26000.00 | 1092000.00 | 19000.00 | 798000.00 | 35000.00 | 1470000.00 | 40500.00 | 1701000.00 | 798000.00 | shiv electric, Actech Engineers
88.00 | Supply of following size 1.1 KV grade XLPE insulated, PVC sheathed, Aluminium conductor armoured power cable conforming to IS 7098 (Part 1) 1988 amended upto date.
89.00 | 3.5x400 sqmm | 120.00 | Meter | 10.00 | 1302.00 | 156240.00 | 1329.00 | 159480.00 | 1200.00 | 144000.00 | 1450.00 | 174000.00 | 1190.00 | 142800.00 | 1245.00 | 149400.00 | 1561.00 | 187320.00 | 1819.94 | 218392.80 | 1241.00 | 148920.00 | 1197.00 | 143640.00 | 1394.00 | 167280.00 | 1547.00 | 185640.00 | 1352.00 | 162240.00 | 1450.00 | 174000.00 | 1488.00 | 178560.00 | 1450.00 | 174000.00 | 1263.00 | 151560.00 | 1420.00 | 170400.00 | 1200.00 | 144000.00 | 1417.00 | 170040.00 | 1443.00 | 173160.00 | 1758.00 | 210960.00 | 1400.00 | 168000.00 | 142800.00 | JITENDRA ELECTRICALS
90.00 | 3.5x300 sqmm | 120.00 | Meter | 10.00 | 1020.00 | 122400.00 | 1042.00 | 125040.00 | 950.00 | 114000.00 | 1150.00 | 138000.00 | 940.00 | 112800.00 | 978.00 | 117360.00 | 1222.00 | 146640.00 | 1399.95 | 167994.00 | 972.00 | 116640.00 | 996.00 | 119520.00 | 1095.00 | 131400.00 | 1212.00 | 145440.00 | 1100.00 | 132000.00 | 1150.00 | 138000.00 | 1166.00 | 139920.00 | 1150.00 | 138000.00 | 990.00 | 118800.00 | 1212.00 | 145440.00 | 1000.00 | 120000.00 | 1193.00 | 143160.00 | 1160.00 | 139200.00 | 1377.00 | 165240.00 | 1100.00 | 132000.00 | 112800.00 | JITENDRA ELECTRICALS
91.00 | 3.5x240 sqmm | 500.00 | Meter | 10.00 | 848.00 | 424000.00 | 865.00 | 432500.00 | 750.00 | 375000.00 | 1000.00 | 500000.00 | 770.00 | 385000.00 | 790.00 | 395000.00 | 1016.00 | 508000.00 | 1166.63 | 583315.00 | 808.00 | 404000.00 | 828.00 | 414000.00 | 893.00 | 446500.00 | 880.00 | 440000.00 | 930.00 | 465000.00 | 950.00 | 475000.00 | 932.00 | 466000.00 | 950.00 | 475000.00 | 823.00 | 411500.00 | 941.00 | 470500.00 | 850.00 | 425000.00 | 991.00 | 495500.00 | 964.00 | 482000.00 | 1144.50 | 572250.00 | 990.00 | 495000.00 | 375000.00 | DOSHI ELECTRIC ENGG. CO.
92.00 | 3.5x185 sqmm | 200.00 | Meter | 10.00 | 662.00 | 132400.00 | 675.00 | 135000.00 | 600.00 | 120000.00 | 915.00 | 183000.00 | 610.00 | 122000.00 | 635.00 | 127000.00 | 794.00 | 158800.00 | 886.64 | 177328.00 | 632.00 | 126400.00 | 647.00 | 129400.00 | 710.00 | 142000.00 | 787.00 | 157400.00 | 740.00 | 148000.00 | 750.00 | 150000.00 | 758.00 | 151600.00 | 750.00 | 150000.00 | 643.00 | 128600.00 | 723.00 | 144600.00 | 700.00 | 140000.00 | 124.00 | 24800.00 | 753.00 | 150600.00 | 894.00 | 178800.00 | 780.00 | 156000.00 | 24800.00 | RISHA CONTROL ENGINEERS PRIVATE LIMITED
93.00 | 3.5x150 sqmm | 160.00 | Meter | 10.00 | 526.00 | 84160.00 | 536.00 | 85760.00 | 500.00 | 80000.00 | 850.00 | 136000.00 | 490.00 | 78400.00 | 506.00 | 80960.00 | 630.00 | 100800.00 | 699.98 | 111996.80 | 501.00 | 80160.00 | 513.00 | 82080.00 | 569.00 | 91040.00 | 624.00 | 99840.00 | 600.00 | 96000.00 | 600.00 | 96000.00 | 602.00 | 96320.00 | 600.00 | 96000.00 | 510.00 | 81600.00 | 573.00 | 91680.00 | 600.00 | 96000.00 | 614.00 | 98240.00 | 598.00 | 95680.00 | 709.50 | 113520.00 | 615.00 | 98400.00 | 78400.00 | JITENDRA ELECTRICALS
94.00 | 3.5x95 sqmm | 30.00 | Meter | 10.00 | 363.00 | 10890.00 | 370.00 | 11100.00 | 350.00 | 10500.00 | 600.00 | 18000.00 | 335.00 | 10050.00 | 348.00 | 10440.00 | 434.00 | 13020.00 | 559.98 | 16799.40 | 346.00 | 10380.00 | 347.00 | 10410.00 | 384.00 | 11520.00 | 430.00 | 12900.00 | 430.00 | 12900.00 | 500.00 | 15000.00 | 415.00 | 12450.00 | 450.00 | 13500.00 | 351.00 | 10530.00 | 395.00 | 11850.00 | 400.00 | 12000.00 | 423.00 | 12690.00 | 411.00 | 12330.00 | 489.00 | 14670.00 | 475.00 | 14250.00 | 10050.00 | JITENDRA ELECTRICALS
95.00 | 3.5x70 sqmm | 140.00 | Meter | 10.00 | 290.00 | 40600.00 | 295.00 | 41300.00 | 300.00 | 42000.00 | 310.00 | 43400.00 | 260.00 | 36400.00 | 285.00 | 39900.00 | 346.00 | 48440.00 | 373.32 | 52264.80 | 275.00 | 38500.00 | 283.00 | 39620.00 | 319.00 | 44660.00 | 343.00 | 48020.00 | 350.00 | 49000.00 | 350.00 | 49000.00 | 331.00 | 46340.00 | 350.00 | 49000.00 | 280.00 | 39200.00 | 321.00 | 44940.00 | 320.00 | 44800.00 | 338.00 | 47320.00 | 328.00 | 45920.00 | 390.00 | 54600.00 | 330.00 | 46200.00 | 36400.00 | JITENDRA ELECTRICALS
96.00 | 4x25 sqmm | 60.00 | Meter | 10.00 | 144.00 | 8640.00 | 147.00 | 8820.00 | 150.00 | 9000.00 | 150.00 | 9000.00 | 140.00 | 8400.00 | 145.00 | 8700.00 | 172.00 | 10320.00 | 233.33 | 13999.80 | 137.00 | 8220.00 | 255.00 | 15300.00 | 151.00 | 9060.00 | 170.00 | 10200.00 | 180.00 | 10800.00 | 150.00 | 9000.00 | 165.00 | 9900.00 | 200.00 | 12000.00 | 139.00 | 8340.00 | 162.00 | 9720.00 | 150.00 | 9000.00 | 155.00 | 9300.00 | 150.00 | 9000.00 | 193.50 | 11610.00 | 175.00 | 10500.00 | 8220.00 | Choubay And Co.(Agencies) Pvt.Ltd.
97.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of XLPE insulated PVC sheathed aluminium conductor cable of 1.1 kV grade as required.
98.00 | 3.5x400 sqmm | 6.00 | Each | 10.00 | 2200.00 | 13200.00 | 1978.00 | 11868.00 | 700.00 | 4200.00 | 350.00 | 2100.00 | 1500.00 | 9000.00 | 2200.00 | 13200.00 | 3045.00 | 18270.00 | 933.30 | 5599.80 | 1200.00 | 7200.00 | 2027.00 | 12162.00 | 1300.00 | 7800.00 | 1006.00 | 6036.00 | 1500.00 | 9000.00 | 1500.00 | 9000.00 | 1000.00 | 6000.00 | 1500.00 | 9000.00 | 2280.00 | 13680.00 | 2866.00 | 17196.00 | 1400.00 | 8400.00 | 2530.00 | 15180.00 | 1749.15 | 10494.90 | 1000.00 | 6000.00 | 1500.00 | 9000.00 | 2100.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
99.00 | 3.5x300 sqmm | 6.00 | Each | 10.00 | 1645.00 | 9870.00 | 1512.00 | 9072.00 | 650.00 | 3900.00 | 300.00 | 1800.00 | 1200.00 | 7200.00 | 2000.00 | 12000.00 | 2692.00 | 16152.00 | 933.30 | 5599.80 | 1200.00 | 7200.00 | 1911.00 | 11466.00 | 660.00 | 3960.00 | 809.00 | 4854.00 | 1300.00 | 7800.00 | 1200.00 | 7200.00 | 1000.00 | 6000.00 | 1250.00 | 7500.00 | 1833.00 | 10998.00 | 2168.00 | 13008.00 | 1100.00 | 6600.00 | 2145.00 | 12870.00 | 1187.55 | 7125.30 | 950.00 | 5700.00 | 1200.00 | 7200.00 | 1800.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
100.00 | 3.5x240 sqmm | 25.00 | Each | 10.00 | 1485.00 | 37125.00 | 1245.00 | 31125.00 | 600.00 | 15000.00 | 250.00 | 6250.00 | 1000.00 | 25000.00 | 1500.00 | 37500.00 | 1948.00 | 48700.00 | 933.30 | 23332.50 | 1000.00 | 25000.00 | 1564.00 | 39100.00 | 562.00 | 14050.00 | 678.00 | 16950.00 | 1200.00 | 30000.00 | 1000.00 | 25000.00 | 1000.00 | 25000.00 | 1050.00 | 26250.00 | 1093.00 | 27325.00 | 1849.00 | 46225.00 | 1000.00 | 25000.00 | 1793.00 | 44825.00 | 913.90 | 22847.50 | 900.00 | 22500.00 | 1000.00 | 25000.00 | 6250.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
101.00 | 3.5x185 sqmm | 10.00 | Each | 10.00 | 1145.00 | 11450.00 | 974.00 | 9740.00 | 550.00 | 5500.00 | 200.00 | 2000.00 | 850.00 | 8500.00 | 1300.00 | 13000.00 | 1552.00 | 15520.00 | 653.31 | 6533.10 | 800.00 | 8000.00 | 1217.00 | 12170.00 | 438.00 | 4380.00 | 524.00 | 5240.00 | 1000.00 | 10000.00 | 800.00 | 8000.00 | 900.00 | 9000.00 | 950.00 | 9500.00 | 1030.00 | 10300.00 | 1256.00 | 12560.00 | 750.00 | 7500.00 | 1320.00 | 13200.00 | 710.45 | 7104.50 | 900.00 | 9000.00 | 900.00 | 9000.00 | 2000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
102.00 | 3.5x150 sqmm | 8.00 | Each | 10.00 | 867.00 | 6936.00 | 715.00 | 5720.00 | 500.00 | 4000.00 | 200.00 | 1600.00 | 750.00 | 6000.00 | 1100.00 | 8800.00 | 1292.00 | 10336.00 | 466.65 | 3733.20 | 800.00 | 6400.00 | 1101.00 | 8808.00 | 438.00 | 3504.00 | 434.00 | 3472.00 | 900.00 | 7200.00 | 700.00 | 5600.00 | 900.00 | 7200.00 | 850.00 | 6800.00 | 878.00 | 7024.00 | 1114.00 | 8912.00 | 750.00 | 6000.00 | 869.00 | 6952.00 | 540.15 | 4321.20 | 850.00 | 6800.00 | 750.00 | 6000.00 | 1600.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
103.00 | 3.5x95 sqmm | 1.00 | Each | 10.00 | 600.00 | 600.00 | 541.00 | 541.00 | 450.00 | 450.00 | 180.00 | 180.00 | 700.00 | 700.00 | 850.00 | 850.00 | 1404.00 | 1404.00 | 466.65 | 466.65 | 600.00 | 600.00 | 811.00 | 811.00 | 241.00 | 241.00 | 357.00 | 357.00 | 700.00 | 700.00 | 500.00 | 500.00 | 800.00 | 800.00 | 750.00 | 750.00 | 622.00 | 622.00 | 933.00 | 933.00 | 600.00 | 600.00 | 638.00 | 638.00 | 347.10 | 347.10 | 800.00 | 800.00 | 630.00 | 630.00 | 180.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
104.00 | 3.5x70 sqmm | 7.00 | Each | 10.00 | 400.00 | 2800.00 | 498.00 | 3486.00 | 400.00 | 2800.00 | 180.00 | 1260.00 | 600.00 | 4200.00 | 700.00 | 4900.00 | 1384.00 | 9688.00 | 466.65 | 3266.55 | 600.00 | 4200.00 | 695.00 | 4865.00 | 202.00 | 1414.00 | 288.00 | 2016.00 | 400.00 | 2800.00 | 400.00 | 2800.00 | 800.00 | 5600.00 | 650.00 | 4550.00 | 525.00 | 3675.00 | 767.00 | 5369.00 | 300.00 | 2100.00 | 555.50 | 3888.50 | 280.15 | 1961.05 | 800.00 | 5600.00 | 520.00 | 3640.00 | 1260.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
105.00 | 3.5x50 sqmm | 1.00 | Each | 10.00 | 350.00 | 350.00 | 383.00 | 383.00 | 350.00 | 350.00 | 150.00 | 150.00 | 500.00 | 500.00 | 500.00 | 500.00 | 1384.00 | 1384.00 | 279.99 | 279.99 | 500.00 | 500.00 | 637.00 | 637.00 | 202.00 | 202.00 | 223.00 | 223.00 | 300.00 | 300.00 | 300.00 | 300.00 | 800.00 | 800.00 | 550.00 | 550.00 | 411.00 | 411.00 | 637.00 | 637.00 | 250.00 | 250.00 | 522.50 | 522.50 | 229.45 | 229.45 | 750.00 | 750.00 | 450.00 | 450.00 | 150.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
106.00 | 3.5x25 sqmm | 1.00 | Each | 10.00 | 300.00 | 300.00 | 299.00 | 299.00 | 300.00 | 300.00 | 120.00 | 120.00 | 400.00 | 400.00 | 400.00 | 400.00 | 1384.00 | 1384.00 | 279.99 | 279.99 | 400.00 | 400.00 | 521.00 | 521.00 | 118.00 | 118.00 | 157.00 | 157.00 | 300.00 | 300.00 | 100.00 | 100.00 | 300.00 | 300.00 | 450.00 | 450.00 | 298.00 | 298.00 | 391.00 | 391.00 | 200.00 | 200.00 | 407.00 | 407.00 | 146.25 | 146.25 | 600.00 | 600.00 | 320.00 | 320.00 | 100.00 | Shekhawati Electrical Engineers
107.00 | 4x25 sqmm | 2.00 | Each | 10.00 | 300.00 | 600.00 | 193.00 | 386.00 | 250.00 | 500.00 | 120.00 | 240.00 | 400.00 | 800.00 | 250.00 | 500.00 | 666.00 | 1332.00 | 186.66 | 373.32 | 400.00 | 800.00 | 521.00 | 1042.00 | 118.00 | 236.00 | 167.00 | 334.00 | 200.00 | 400.00 | 100.00 | 200.00 | 300.00 | 600.00 | 450.00 | 900.00 | 269.00 | 538.00 | 375.00 | 750.00 | 200.00 | 400.00 | 407.00 | 814.00 | 150.15 | 300.30 | 500.00 | 1000.00 | 350.00 | 700.00 | 200.00 | Shekhawati Electrical Engineers
108.00 | 4x16 sqmm | 1.00 | Each | 10.00 | 275.00 | 275.00 | 224.00 | 224.00 | 200.00 | 200.00 | 100.00 | 100.00 | 350.00 | 350.00 | 250.00 | 250.00 | 666.00 | 666.00 | 186.66 | 186.66 | 400.00 | 400.00 | 521.00 | 521.00 | 67.00 | 67.00 | 157.00 | 157.00 | 150.00 | 150.00 | 100.00 | 100.00 | 300.00 | 300.00 | 350.00 | 350.00 | 240.00 | 240.00 | 375.00 | 375.00 | 200.00 | 200.00 | 404.25 | 404.25 | 111.15 | 111.15 | 500.00 | 500.00 | 300.00 | 300.00 | 67.00 | KRISHNA REFRIGERATION
109.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
110.00 | 3.5x400 sqmm | 6.00 | Each | 10.00 | 5000.00 | 30000.00 | 5309.00 | 31854.00 | 2700.00 | 16200.00 | 5300.00 | 31800.00 | 9350.00 | 56100.00 | 5780.00 | 34680.00 | 4984.00 | 29904.00 | 9333.00 | 55998.00 | 3300.00 | 19800.00 | 6086.00 | 36516.00 | 4578.00 | 27468.00 | 6666.00 | 39996.00 | 4500.00 | 27000.00 | 5000.00 | 30000.00 | 4000.00 | 24000.00 | 5000.00 | 30000.00 | 2750.00 | 16500.00 | 5520.00 | 33120.00 | 7200.00 | 43200.00 | 7150.00 | 42900.00 | 4207.00 | 25242.00 | 5028.00 | 30168.00 | 3250.00 | 19500.00 | 16200.00 | DOSHI ELECTRIC ENGG. CO.
111.00 | 3.5x300 sqmm | 6.00 | Each | 10.00 | 4425.00 | 26550.00 | 4758.00 | 28548.00 | 2700.00 | 16200.00 | 5200.00 | 31200.00 | 9000.00 | 54000.00 | 4920.00 | 29520.00 | 4855.00 | 29130.00 | 9333.00 | 55998.00 | 2950.00 | 17700.00 | 5423.00 | 32538.00 | 3873.00 | 23238.00 | 5751.00 | 34506.00 | 4000.00 | 24000.00 | 5000.00 | 30000.00 | 3500.00 | 21000.00 | 4500.00 | 27000.00 | 2600.00 | 15600.00 | 5285.00 | 31710.00 | 5800.00 | 34800.00 | 5775.00 | 34650.00 | 4140.00 | 24840.00 | 5028.00 | 30168.00 | 2750.00 | 16500.00 | 15600.00 | Aditya Techno Products Private Limited
112.00 | 3.5x240 sqmm | 25.00 | Each | 10.00 | 4425.00 | 110625.00 | 4758.00 | 118950.00 | 2500.00 | 62500.00 | 4600.00 | 115000.00 | 8500.00 | 212500.00 | 4920.00 | 123000.00 | 4042.00 | 101050.00 | 9333.00 | 233325.00 | 2950.00 | 73750.00 | 5123.00 | 128075.00 | 3873.00 | 96825.00 | 5751.00 | 143775.00 | 4000.00 | 100000.00 | 4000.00 | 100000.00 | 3500.00 | 87500.00 | 4000.00 | 100000.00 | 2575.00 | 64375.00 | 5285.00 | 132125.00 | 5200.00 | 130000.00 | 5775.00 | 144375.00 | 3680.00 | 92000.00 | 4080.00 | 102000.00 | 2750.00 | 68750.00 | 62500.00 | DOSHI ELECTRIC ENGG. CO.
113.00 | 3.5x185 sqmm | 10.00 | Each | 10.00 | 3300.00 | 33000.00 | 3710.00 | 37100.00 | 2200.00 | 22000.00 | 4600.00 | 46000.00 | 6600.00 | 66000.00 | 3276.00 | 32760.00 | 3913.00 | 39130.00 | 6533.10 | 65331.00 | 2100.00 | 21000.00 | 3716.00 | 37160.00 | 2535.00 | 25350.00 | 3953.00 | 39530.00 | 3000.00 | 30000.00 | 4000.00 | 40000.00 | 3000.00 | 30000.00 | 3500.00 | 35000.00 | 2110.00 | 21100.00 | 5285.00 | 52850.00 | 5000.00 | 50000.00 | 4851.00 | 48510.00 | 3220.00 | 32200.00 | 4080.00 | 40800.00 | 1950.00 | 19500.00 | 19500.00 | Water Power Engg. Enterprises
114.00 | 3.5x150 sqmm | 8.00 | Each | 10.00 | 3100.00 | 24800.00 | 3365.00 | 26920.00 | 2200.00 | 17600.00 | 4200.00 | 33600.00 | 7400.00 | 59200.00 | 3276.00 | 26208.00 | 3710.00 | 29680.00 | 6533.10 | 52264.80 | 2100.00 | 16800.00 | 3691.00 | 29528.00 | 2535.00 | 20280.00 | 3953.00 | 31624.00 | 3000.00 | 24000.00 | 3000.00 | 24000.00 | 3000.00 | 24000.00 | 3000.00 | 24000.00 | 1823.00 | 14584.00 | 3410.00 | 27280.00 | 1900.00 | 15200.00 | 4620.00 | 36960.00 | 2875.00 | 23000.00 | 2472.00 | 19776.00 | 1425.00 | 11400.00 | 11400.00 | Water Power Engg. Enterprises
115.00 | 3.5x95 sqmm | 1.00 | Each | 10.00 | 2530.00 | 2530.00 | 2841.00 | 2841.00 | 1700.00 | 1700.00 | 4000.00 | 4000.00 | 7300.00 | 7300.00 | 2455.00 | 2455.00 | 3581.00 | 3581.00 | 4666.50 | 4666.50 | 2000.00 | 2000.00 | 2842.00 | 2842.00 | 1866.00 | 1866.00 | 2994.00 | 2994.00 | 2500.00 | 2500.00 | 2500.00 | 2500.00 | 2500.00 | 2500.00 | 2850.00 | 2850.00 | 1594.00 | 1594.00 | 3410.00 | 3410.00 | 4000.00 | 4000.00 | 4158.00 | 4158.00 | 2415.00 | 2415.00 | 2472.00 | 2472.00 | 1425.00 | 1425.00 | 1425.00 | Water Power Engg. Enterprises
116.00 | 3.5x70 sqmm | 7.00 | Each | 10.00 | 2530.00 | 17710.00 | 2611.00 | 18277.00 | 1500.00 | 10500.00 | 3800.00 | 26600.00 | 6800.00 | 47600.00 | 2455.00 | 17185.00 | 3073.00 | 21511.00 | 2799.86 | 19599.02 | 1400.00 | 9800.00 | 2716.00 | 19012.00 | 1866.00 | 13062.00 | 2904.00 | 20328.00 | 2000.00 | 14000.00 | 2500.00 | 17500.00 | 2500.00 | 17500.00 | 2550.00 | 17850.00 | 1569.00 | 10983.00 | 3410.00 | 23870.00 | 3800.00 | 26600.00 | 4042.50 | 28297.50 | 2185.00 | 15295.00 | 2472.00 | 17304.00 | 1425.00 | 9975.00 | 9800.00 | Choubay And Co.(Agencies) Pvt.Ltd.
117.00 | 3.5x50 sqmm | 1.00 | Each | 10.00 | 2530.00 | 2530.00 | 2023.00 | 2023.00 | 1500.00 | 1500.00 | 3500.00 | 3500.00 | 6700.00 | 6700.00 | 1895.00 | 1895.00 | 2639.00 | 2639.00 | 2799.90 | 2799.90 | 1200.00 | 1200.00 | 2353.00 | 2353.00 | 1409.00 | 1409.00 | 2250.00 | 2250.00 | 2000.00 | 2000.00 | 2000.00 | 2000.00 | 2000.00 | 2000.00 | 2250.00 | 2250.00 | 1021.00 | 1021.00 | 2640.00 | 2640.00 | 2200.00 | 2200.00 | 3465.00 | 3465.00 | 2070.00 | 2070.00 | 1800.00 | 1800.00 | 1050.00 | 1050.00 | 1021.00 | Aditya Techno Products Private Limited
118.00 | 3.5x25 sqmm | 1.00 | Each | 10.00 | 1900.00 | 1900.00 | 1678.00 | 1678.00 | 1500.00 | 1500.00 | 3000.00 | 3000.00 | 6700.00 | 6700.00 | 1895.00 | 1895.00 | 1928.00 | 1928.00 | 2799.90 | 2799.90 | 1200.00 | 1200.00 | 1882.00 | 1882.00 | 1409.00 | 1409.00 | 2190.00 | 2190.00 | 1500.00 | 1500.00 | 2000.00 | 2000.00 | 1000.00 | 1000.00 | 1250.00 | 1250.00 | 820.00 | 820.00 | 2640.00 | 2640.00 | 2200.00 | 2200.00 | 2887.50 | 2887.50 | 1380.00 | 1380.00 | 1800.00 | 1800.00 | 1050.00 | 1050.00 | 820.00 | Aditya Techno Products Private Limited
119.00 | 4x25 sqmm | 2.00 | Each | 10.00 | 1900.00 | 3800.00 | 1678.00 | 3356.00 | 1500.00 | 3000.00 | 3000.00 | 6000.00 | 6700.00 | 13400.00 | 1895.00 | 3790.00 | 1928.00 | 3856.00 | 2799.90 | 5599.80 | 950.00 | 1900.00 | 1882.00 | 3764.00 | 1409.00 | 2818.00 | 2190.00 | 4380.00 | 1500.00 | 3000.00 | 1000.00 | 2000.00 | 1000.00 | 2000.00 | 1250.00 | 2500.00 | 790.00 | 1580.00 | 1977.00 | 3954.00 | 2200.00 | 4400.00 | 2887.50 | 5775.00 | 1380.00 | 2760.00 | 1800.00 | 3600.00 | 1050.00 | 2100.00 | 1580.00 | Aditya Techno Products Private Limited
120.00 | 4x16 sqmm | 1.00 | Each | 10.00 | 1900.00 | 1900.00 | 1485.00 | 1485.00 | 1500.00 | 1500.00 | 2500.00 | 2500.00 | 6700.00 | 6700.00 | 1590.00 | 1590.00 | 1799.00 | 1799.00 | 2799.90 | 2799.90 | 950.00 | 950.00 | 1701.00 | 1701.00 | 1195.00 | 1195.00 | 1870.00 | 1870.00 | 1500.00 | 1500.00 | 1000.00 | 1000.00 | 1000.00 | 1000.00 | 1250.00 | 1250.00 | 790.00 | 790.00 | 1977.00 | 1977.00 | 2000.00 | 2000.00 | 2887.50 | 2887.50 | 1265.00 | 1265.00 | 1440.00 | 1440.00 | 900.00 | 900.00 | 790.00 | Aditya Techno Products Private Limited
121.00 | Laying and Fixing of one number XLPE/PVC insulated and PVC sheathed/XLPE aluminium/copper conductor armoured power cable of 1.1 KV grade of following sizes on surface/ cable tray/ wall etc as required.
122.00 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 20.00 | Meter | 10.00 | 50.00 | 1000.00 | 40.00 | 800.00 | 100.00 | 2000.00 | 120.00 | 2400.00 | 60.00 | 1200.00 | 70.00 | 1400.00 | 52.00 | 1040.00 | 93.33 | 1866.60 | 60.00 | 1200.00 | 46.00 | 920.00 | 85.00 | 1700.00 | 41.00 | 820.00 | 70.00 | 1400.00 | 70.00 | 1400.00 | 120.00 | 2400.00 | 55.00 | 1100.00 | 30.00 | 600.00 | 48.00 | 960.00 | 30.00 | 600.00 | 95.00 | 1900.00 | 100.00 | 2000.00 | 200.00 | 4000.00 | 50.00 | 1000.00 | 600.00 | Aditya Techno Products Private Limited, GAYATRI ELECTRICAL
123.00 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 45.00 | Meter | 10.00 | 60.00 | 2700.00 | 63.00 | 2835.00 | 150.00 | 6750.00 | 120.00 | 5400.00 | 75.00 | 3375.00 | 80.00 | 3600.00 | 137.00 | 6165.00 | 93.33 | 4199.85 | 80.00 | 3600.00 | 58.00 | 2610.00 | 146.00 | 6570.00 | 62.00 | 2790.00 | 70.00 | 3150.00 | 100.00 | 4500.00 | 150.00 | 6750.00 | 65.00 | 2925.00 | 59.00 | 2655.00 | 60.00 | 2700.00 | 40.00 | 1800.00 | 160.00 | 7200.00 | 150.00 | 6750.00 | 200.00 | 9000.00 | 125.00 | 5625.00 | 1800.00 | GAYATRI ELECTRICAL
124.00 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 90.00 | Meter | 10.00 | 70.00 | 6300.00 | 92.00 | 8280.00 | 175.00 | 15750.00 | 150.00 | 13500.00 | 100.00 | 9000.00 | 100.00 | 9000.00 | 161.00 | 14490.00 | 93.33 | 8399.70 | 90.00 | 8100.00 | 69.00 | 6210.00 | 183.00 | 16470.00 | 88.00 | 7920.00 | 70.00 | 6300.00 | 120.00 | 10800.00 | 210.00 | 18900.00 | 75.00 | 6750.00 | 94.00 | 8460.00 | 72.00 | 6480.00 | 70.00 | 6300.00 | 220.00 | 19800.00 | 220.00 | 19800.00 | 200.00 | 18000.00 | 150.00 | 13500.00 | 6210.00 | Incotech Engineers Pvt Ltd
125.00 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 185.00 | Meter | 10.00 | 100.00 | 18500.00 | 138.00 | 25530.00 | 200.00 | 37000.00 | 200.00 | 37000.00 | 150.00 | 27750.00 | 120.00 | 22200.00 | 240.00 | 44400.00 | 139.99 | 25898.15 | 100.00 | 18500.00 | 115.00 | 21275.00 | 293.00 | 54205.00 | 132.00 | 24420.00 | 70.00 | 12950.00 | 150.00 | 27750.00 | 210.00 | 38850.00 | 85.00 | 15725.00 | 158.00 | 29230.00 | 84.00 | 15540.00 | 105.00 | 19425.00 | 273.00 | 50505.00 | 270.00 | 49950.00 | 200.00 | 37000.00 | 220.00 | 40700.00 | 12950.00 | shiv electric
126.00 | Laying of one number XLPE/PVC insulated PVC sheathed aluminium/copper conductor armoured power cable of 1.1 KV grade of following sizes in the existing masonry open duct/ built in trench etc. as required.
127.00 | Upto 35 sq. mm | 35.00 | Meter | 10.00 | 50.00 | 1750.00 | 40.00 | 1400.00 | 40.00 | 1400.00 | 50.00 | 1750.00 | 60.00 | 2100.00 | 30.00 | 1050.00 | 58.00 | 2030.00 | 93.30 | 3265.50 | 20.00 | 700.00 | 29.00 | 1015.00 | 73.00 | 2555.00 | 30.00 | 1050.00 | 60.00 | 2100.00 | 40.00 | 1400.00 | 30.00 | 1050.00 | 45.00 | 1575.00 | 22.00 | 770.00 | 42.00 | 1470.00 | 30.00 | 1050.00 | 75.00 | 2625.00 | 115.00 | 4025.00 | 200.00 | 7000.00 | 31.00 | 1085.00 | 700.00 | Choubay And Co.(Agencies) Pvt.Ltd.
128.00 | Above 35 sq. mm and upto 95 sq. mm | 110.00 | Meter | 10.00 | 60.00 | 6600.00 | 58.00 | 6380.00 | 50.00 | 5500.00 | 100.00 | 11000.00 | 75.00 | 8250.00 | 40.00 | 4400.00 | 66.00 | 7260.00 | 93.32 | 10265.20 | 30.00 | 3300.00 | 52.00 | 5720.00 | 134.00 | 14740.00 | 48.00 | 5280.00 | 60.00 | 6600.00 | 50.00 | 5500.00 | 40.00 | 4400.00 | 55.00 | 6050.00 | 53.00 | 5830.00 | 54.00 | 5940.00 | 40.00 | 4400.00 | 105.00 | 11550.00 | 175.00 | 19250.00 | 200.00 | 22000.00 | 47.00 | 5170.00 | 3300.00 | Choubay And Co.(Agencies) Pvt.Ltd.
129.00 | Above 95 sq. mm and upto 185 sq. mm | 255.00 | Meter | 10.00 | 70.00 | 17850.00 | 81.00 | 20655.00 | 60.00 | 15300.00 | 100.00 | 25500.00 | 100.00 | 25500.00 | 50.00 | 12750.00 | 90.00 | 22950.00 | 93.32 | 23796.60 | 40.00 | 10200.00 | 63.00 | 16065.00 | 171.00 | 43605.00 | 66.00 | 16830.00 | 60.00 | 15300.00 | 70.00 | 17850.00 | 50.00 | 12750.00 | 65.00 | 16575.00 | 83.00 | 21165.00 | 66.00 | 16830.00 | 70.00 | 17850.00 | 160.00 | 40800.00 | 220.00 | 56100.00 | 200.00 | 51000.00 | 64.00 | 16320.00 | 10200.00 | Choubay And Co.(Agencies) Pvt.Ltd.
130.00 | Above 185 sq. mm and upto 400 sq. mm | 495.00 | Meter | 10.00 | 100.00 | 49500.00 | 104.00 | 51480.00 | 70.00 | 34650.00 | 100.00 | 49500.00 | 150.00 | 74250.00 | 60.00 | 29700.00 | 146.00 | 72270.00 | 93.32 | 46193.40 | 40.00 | 19800.00 | 115.00 | 56925.00 | 268.00 | 132660.00 | 96.00 | 47520.00 | 60.00 | 29700.00 | 100.00 | 49500.00 | 60.00 | 29700.00 | 75.00 | 37125.00 | 118.00 | 58410.00 | 78.00 | 38610.00 | 105.00 | 51975.00 | 210.00 | 103950.00 | 270.00 | 133650.00 | 200.00 | 99000.00 | 112.00 | 55440.00 | 19800.00 | Choubay And Co.(Agencies) Pvt.Ltd.
131.00 | Supplying and installing following size of perforated Hot Dipped Galvanized Iron cable tray cable tray with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required.
132.00 | 600 mm width X 75 mm depth X 2 mm thickness | 45.00 | Meter | 10.00 | 2150.00 | 96750.00 | 2210.00 | 99450.00 | 2000.00 | 90000.00 | 980.00 | 44100.00 | 1300.00 | 58500.00 | 1600.00 | 72000.00 | 2747.00 | 123615.00 | 466.64 | 20998.80 | 1175.00 | 52875.00 | 1286.00 | 57870.00 | 1295.00 | 58275.00 | 2292.00 | 103140.00 | 1500.00 | 67500.00 | 1250.00 | 56250.00 | 1950.00 | 87750.00 | 850.00 | 38250.00 | 1750.00 | 78750.00 | 1717.00 | 77265.00 | 1450.00 | 65250.00 | 1470.00 | 66150.00 | 1502.00 | 67590.00 | 1500.00 | 67500.00 | 1750.00 | 78750.00 | 20998.80 | Deora Electricals
133.00 | Supply and fixing of flame retardant electrical insulation mat of 3.0 mm +/-10% thick electric insulated synthetic conforming to IS 15652:2006 and meeting the requirements of IS : 5216 (part 1,2,3), IS :8437, IEC 479 pub-1 along with suitable adhesive and water proofing compound as per in service recommendations of annexure A clause C of IS 15652 and suitable for class C upto 33 KV with out trolley movement | 74.50 | mtr | 10.00 | 1200.00 | 89400.00 | 1415.00 | 105417.50 | 1000.00 | 74500.00 | 2800.00 | 208600.00 | 1120.00 | 83440.00 | 6500.00 | 484250.00 | 1141.00 | 85004.50 | 1866.60 | 139061.70 | 1200.00 | 89400.00 | 996.00 | 74202.00 | 1829.00 | 136260.50 | 1116.00 | 83142.00 | 1000.00 | 74500.00 | 1400.00 | 104300.00 | 1100.00 | 81950.00 | 1250.00 | 93125.00 | 800.00 | 59600.00 | 1200.00 | 89400.00 | 1200.00 | 89400.00 | 1050.00 | 78225.00 | 3500.00 | 260750.00 | 2500.00 | 186250.00 | 1500.00 | 111750.00 | 59600.00 | Aditya Techno Products Private Limited
134.00 | Supply and fixing of flame retardant electrical insulation mat of 2.0 mm +/-10% thick electric insulated synthetic conforming to IS 15652:2006 and meeting the requirements of IS : 5216 (part 1,2,3), IS :8437, IEC 479 pub-1 along with suitable adhesive and water proofing compound as per in service recommendations of annexure A clause C of IS 15652 and suitable for class A upto 3.3 KV AC & 240V DC with HT trolley movement | 152.50 | mtr | 10.00 | 1000.00 | 152500.00 | 1118.00 | 170495.00 | 800.00 | 122000.00 | 2200.00 | 335500.00 | 830.00 | 126575.00 | 4500.00 | 686250.00 | 953.00 | 145332.50 | 1866.60 | 284656.50 | 900.00 | 137250.00 | 732.00 | 111630.00 | 1585.00 | 241712.50 | 738.00 | 112545.00 | 900.00 | 137250.00 | 1000.00 | 152500.00 | 900.00 | 137250.00 | 950.00 | 144875.00 | 610.00 | 93025.00 | 960.00 | 146400.00 | 1100.00 | 167750.00 | 630.00 | 96075.00 | 2200.00 | 335500.00 | 2000.00 | 305000.00 | 1500.00 | 228750.00 | 93025.00 | Aditya Techno Products Private Limited
135.00 | Supply & fixing following danger notice plate made of mild steel sheet of at least 2mm thick & vitreous enameled white on both sides and with inscription in signal red colour on front side as required.
136.00 | Danger / Caution board for 33KV size 250mm x 200mm. | 10.00 | Each | 10.00 | 300.00 | 3000.00 | 460.00 | 4600.00 | 300.00 | 3000.00 | 1500.00 | 15000.00 | 500.00 | 5000.00 | 250.00 | 2500.00 | 539.00 | 5390.00 | 466.66 | 4666.60 | 350.00 | 3500.00 | 265.00 | 2650.00 | 610.00 | 6100.00 | 180.00 | 1800.00 | 500.00 | 5000.00 | 250.00 | 2500.00 | 300.00 | 3000.00 | 500.00 | 5000.00 | 120.00 | 1200.00 | 175.00 | 1750.00 | 120.00 | 1200.00 | 315.00 | 3150.00 | 350.00 | 3500.00 | 1000.00 | 10000.00 | 150.00 | 1500.00 | 1200.00 | Aditya Techno Products Private Limited, GAYATRI ELECTRICAL
137.00 | Danger /Caution board for 433V size 200mm x 150mm . | 10.00 | Each | 10.00 | 300.00 | 3000.00 | 403.00 | 4030.00 | 200.00 | 2000.00 | 1500.00 | 15000.00 | 500.00 | 5000.00 | 200.00 | 2000.00 | 477.00 | 4770.00 | 466.66 | 4666.60 | 300.00 | 3000.00 | 265.00 | 2650.00 | 732.00 | 7320.00 | 180.00 | 1800.00 | 500.00 | 5000.00 | 250.00 | 2500.00 | 250.00 | 2500.00 | 500.00 | 5000.00 | 120.00 | 1200.00 | 175.00 | 1750.00 | 120.00 | 1200.00 | 260.00 | 2600.00 | 300.00 | 3000.00 | 1000.00 | 10000.00 | 200.00 | 2000.00 | 1200.00 | Aditya Techno Products Private Limited, GAYATRI ELECTRICAL
138.00 | Supply and fixing glass framed standard shock treatment chart in two different languages as per BIS 1986. | 4.00 | Each | 10.00 | 1500.00 | 6000.00 | 1265.00 | 5060.00 | 700.00 | 2800.00 | 1200.00 | 4800.00 | 2000.00 | 8000.00 | 2200.00 | 8800.00 | 4005.00 | 16020.00 | 466.66 | 1866.64 | 350.00 | 1400.00 | 1495.00 | 5980.00 | 610.00 | 2440.00 | 1080.00 | 4320.00 | 500.00 | 2000.00 | 500.00 | 2000.00 | 400.00 | 1600.00 | 1500.00 | 6000.00 | 2850.00 | 11400.00 | 1100.00 | 4400.00 | 80.00 | 320.00 | 2100.00 | 8400.00 | 800.00 | 3200.00 | 2000.00 | 8000.00 | 2000.00 | 8000.00 | 320.00 | GAYATRI ELECTRICAL
139.00 | Supplying of Rubber hand gloves suitable for use in 33 KV power supply. | 4.00 | Each | 10.00 | 1000.00 | 4000.00 | 1150.00 | 4600.00 | 1200.00 | 4800.00 | 1000.00 | 4000.00 | 1500.00 | 6000.00 | 650.00 | 2600.00 | 875.00 | 3500.00 | 466.66 | 1866.64 | 600.00 | 2400.00 | 1150.00 | 4600.00 | 610.00 | 2440.00 | 600.00 | 2400.00 | 500.00 | 2000.00 | 500.00 | 2000.00 | 700.00 | 2800.00 | 1500.00 | 6000.00 | 1500.00 | 6000.00 | 300.00 | 1200.00 | 400.00 | 1600.00 | 525.00 | 2100.00 | 1200.00 | 4800.00 | 1500.00 | 6000.00 | 200.00 | 800.00 | 800.00 | Water Power Engg. Enterprises
140.00 | Supply of First Aid Box containing material as prescribed by St. John Ambulance brigade OR Indian Red Cross conforming to IS 2217-1963. | 4.00 | Each | 10.00 | 2000.00 | 8000.00 | 1265.00 | 5060.00 | 2000.00 | 8000.00 | 1200.00 | 4800.00 | 3000.00 | 12000.00 | 2000.00 | 8000.00 | 3126.00 | 12504.00 | 466.66 | 1866.64 | 1500.00 | 6000.00 | 2300.00 | 9200.00 | 610.00 | 2440.00 | 1440.00 | 5760.00 | 500.00 | 2000.00 | 1000.00 | 4000.00 | 3500.00 | 14000.00 | 1500.00 | 6000.00 | 3500.00 | 14000.00 | 900.00 | 3600.00 | 400.00 | 1600.00 | 3675.00 | 14700.00 | 700.00 | 2800.00 | 15000.00 | 60000.00 | 500.00 | 2000.00 | 1600.00 | GAYATRI ELECTRICAL
141.00 | Supply and fixing of chequered plate of 6 mm thick including cutting to required size using gas cutter and lay the same over the trench, fixing of angle and supports for chequered plate, related civil works, finishing etc. and painting with two coats of enamel paint over one coat of Zinchromate primer as required. | 2800.00 | Kgs. | 10.00 | 112.00 | 313600.00 | 132.00 | 369600.00 | 90.00 | 252000.00 | 120.00 | 336000.00 | 125.00 | 350000.00 | 90.00 | 252000.00 | 124.00 | 347200.00 | 88.67 | 248276.00 | 82.00 | 229600.00 | 100.00 | 280000.00 | 1524.00 | 4267200.00 | 112.00 | 313600.00 | 85.00 | 238000.00 | 95.00 | 266000.00 | 90.00 | 252000.00 | 90.00 | 252000.00 | 105.00 | 294000.00 | 130.00 | 364000.00 | 100.00 | 280000.00 | 120.00 | 336000.00 | 100.00 | 280000.00 | 70.00 | 196000.00 | 100.00 | 280000.00 | 196000.00 | Jha power corporation
142.00 | Supply and fixing single line diagram, schematic diagrams etc. of 2mtrx1.5mtr size on suitable sheet including lamination etc. as required complete on wall. | 1.00 | Job | 10.00 | 2500.00 | 2500.00 | 1495.00 | 1495.00 | 3000.00 | 3000.00 | 5000.00 | 5000.00 | 5000.00 | 5000.00 | 1500.00 | 1500.00 | 4767.00 | 4767.00 | 1866.60 | 1866.60 | 3500.00 | 3500.00 | 2300.00 | 2300.00 | 14634.00 | 14634.00 | 1320.00 | 1320.00 | 2500.00 | 2500.00 | 2000.00 | 2000.00 | 3000.00 | 3000.00 | 1500.00 | 1500.00 | 12500.00 | 12500.00 | 3100.00 | 3100.00 | 1500.00 | 1500.00 | 10000.00 | 10000.00 | 3000.00 | 3000.00 | 50000.00 | 50000.00 | 2000.00 | 2000.00 | 1320.00 | Power And Instrumentation Guj Ltd
143.00 | Earthing with Copper earth plate 600mm X 600mm X 3 mm thick including accessories and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 mtr long etc with charcoal or coke and salt complete as required | 4.00 | Set | 10.00 | 14000.00 | 56000.00 | 13800.00 | 55200.00 | 14000.00 | 56000.00 | 9800.00 | 39200.00 | 13500.00 | 54000.00 | 12000.00 | 48000.00 | 29491.00 | 117964.00 | 11199.60 | 44798.40 | 13000.00 | 52000.00 | 15210.00 | 60840.00 | 31098.00 | 124392.00 | 12507.00 | 50028.00 | 9000.00 | 36000.00 | 10000.00 | 40000.00 | 17000.00 | 68000.00 | 15000.00 | 60000.00 | 12995.00 | 51980.00 | 21000.00 | 84000.00 | 17000.00 | 68000.00 | 13125.00 | 52500.00 | 8500.00 | 34000.00 | 45000.00 | 180000.00 | 11000.00 | 44000.00 | 34000.00 | Actech Engineers
144.00 | Providing and fixing 50 mm X 5 mm Copper strip on surface or in recess for connections etc. as required | 60.00 | Meter | 10.00 | 1727.00 | 103620.00 | 2191.00 | 131460.00 | 1800.00 | 108000.00 | 450.00 | 27000.00 | 1830.00 | 109800.00 | 1565.00 | 93900.00 | 2532.00 | 151920.00 | 1120.00 | 67200.00 | 1650.00 | 99000.00 | 2513.00 | 150780.00 | 805.00 | 48300.00 | 1806.00 | 108360.00 | 1500.00 | 90000.00 | 1500.00 | 90000.00 | 980.00 | 58800.00 | 1250.00 | 75000.00 | 1705.00 | 102300.00 | 2075.00 | 124500.00 | 2000.00 | 120000.00 | 1750.00 | 105000.00 | 1505.00 | 90300.00 | 2000.00 | 120000.00 | 1400.00 | 84000.00 | 27000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
145.00 | Providing and fixing 50mm x 5mm copper strip at 0.50 m. below ground level for connections ,termination with nut bolt etc as required | 36.00 | Meter | 10.00 | 1775.00 | 63900.00 | 2306.00 | 83016.00 | 2000.00 | 72000.00 | 500.00 | 18000.00 | 1860.00 | 66960.00 | 1558.00 | 56088.00 | 2283.00 | 82188.00 | 1213.00 | 43668.00 | 1650.00 | 59400.00 | 2559.00 | 92124.00 | 805.00 | 28980.00 | 1866.00 | 67176.00 | 1600.00 | 57600.00 | 1700.00 | 61200.00 | 850.00 | 30600.00 | 1250.00 | 45000.00 | 1759.00 | 63324.00 | 1777.00 | 63972.00 | 2000.00 | 72000.00 | 1850.00 | 66600.00 | 1555.00 | 55980.00 | 2000.00 | 72000.00 | 1400.00 | 50400.00 | 18000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
146.00 | Providing and fixing 50 mm X 5 mm copper. strip in 65 mm dia B class G.I. pipe from earth electrode including connection with nut, bolt, spring, washer excavation and re-filling etc. as required. | 36.00 | Meter | 10.00 | 2470.00 | 88920.00 | 3171.00 | 114156.00 | 2500.00 | 90000.00 | 500.00 | 18000.00 | 2450.00 | 88200.00 | 2156.00 | 77616.00 | 3265.00 | 117540.00 | 1586.61 | 57117.96 | 2250.00 | 81000.00 | 3500.00 | 126000.00 | 805.00 | 28980.00 | 2298.00 | 82728.00 | 2300.00 | 82800.00 | 2100.00 | 75600.00 | 1250.00 | 45000.00 | 1850.00 | 66600.00 | 2344.00 | 84384.00 | 2404.00 | 86544.00 | 2200.00 | 79200.00 | 3412.50 | 122850.00 | 2142.00 | 77112.00 | 2000.00 | 72000.00 | 2000.00 | 72000.00 | 18000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
147.00 | Earthing with GI earth plate 600mm X 600mm X 6 mm thick including accessories and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 mtr long etc with charcoal or coke and salt complete as required | 6.00 | Set | 10.00 | 6000.00 | 36000.00 | 11500.00 | 69000.00 | 6000.00 | 36000.00 | 6500.00 | 39000.00 | 9500.00 | 57000.00 | 6500.00 | 39000.00 | 18520.00 | 111120.00 | 5133.15 | 30798.90 | 7650.00 | 45900.00 | 8507.00 | 51042.00 | 7256.00 | 43536.00 | 6215.00 | 37290.00 | 6000.00 | 36000.00 | 5500.00 | 33000.00 | 7000.00 | 42000.00 | 6500.00 | 39000.00 | 7817.00 | 46902.00 | 9800.00 | 58800.00 | 8500.00 | 51000.00 | 9975.00 | 59850.00 | 2800.00 | 16800.00 | 10000.00 | 60000.00 | 7000.00 | 42000.00 | 16800.00 | Actech Engineers
148.00 | Supplying and laying 25 mm X 5 mm G.l strip at 0.50 meter below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. | 120.00 | Meter | 10.00 | 200.00 | 24000.00 | 251.00 | 30120.00 | 150.00 | 18000.00 | 400.00 | 48000.00 | 145.00 | 17400.00 | 116.00 | 13920.00 | 518.00 | 62160.00 | 233.32 | 27998.40 | 175.00 | 21000.00 | 322.00 | 38640.00 | 80.00 | 9600.00 | 206.00 | 24720.00 | 150.00 | 18000.00 | 150.00 | 18000.00 | 550.00 | 66000.00 | 125.00 | 15000.00 | 173.00 | 20760.00 | 154.00 | 18480.00 | 150.00 | 18000.00 | 190.00 | 22800.00 | 102.00 | 12240.00 | 350.00 | 42000.00 | 100.00 | 12000.00 | 9600.00 | KRISHNA REFRIGERATION
149.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required | 120.00 | Meter | 10.00 | 145.00 | 17400.00 | 193.00 | 23160.00 | 125.00 | 15000.00 | 350.00 | 42000.00 | 145.00 | 17400.00 | 116.00 | 13920.00 | 518.00 | 62160.00 | 233.32 | 27998.40 | 160.00 | 19200.00 | 282.00 | 33840.00 | 80.00 | 9600.00 | 146.00 | 17520.00 | 150.00 | 18000.00 | 150.00 | 18000.00 | 400.00 | 48000.00 | 125.00 | 15000.00 | 110.00 | 13200.00 | 154.00 | 18480.00 | 150.00 | 18000.00 | 160.00 | 19200.00 | 61.00 | 7320.00 | 350.00 | 42000.00 | 100.00 | 12000.00 | 7320.00 | Actech Engineers
150.00 | Providing and fixing 25 mm x 5 mm G. I. strip in 40 mm dia. G. I. pipe from earth electrode as required. | 60.00 | Meter | 10.00 | 575.00 | 34500.00 | 537.00 | 32220.00 | 350.00 | 21000.00 | 250.00 | 15000.00 | 575.00 | 34500.00 | 298.00 | 17880.00 | 1151.00 | 69060.00 | 373.32 | 22399.20 | 525.00 | 31500.00 | 905.00 | 54300.00 | 80.00 | 4800.00 | 464.00 | 27840.00 | 400.00 | 24000.00 | 500.00 | 30000.00 | 700.00 | 42000.00 | 450.00 | 27000.00 | 439.00 | 26340.00 | 522.00 | 31320.00 | 180.00 | 10800.00 | 415.00 | 24900.00 | 460.00 | 27600.00 | 350.00 | 21000.00 | 450.00 | 27000.00 | 4800.00 | KRISHNA REFRIGERATION
151.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand :4 graded stone aggregate 20 mm nominal size) in foundation of pump, DG set etc including form work etc as required. | 6.00 | Cum | 10.00 | 7500.00 | 45000.00 | 9200.00 | 55200.00 | 6000.00 | 36000.00 | 1050.00 | 6300.00 | 10000.00 | 60000.00 | 9060.00 | 54360.00 | 17939.00 | 107634.00 | 4666.50 | 27999.00 | 9400.00 | 56400.00 | 7429.00 | 44574.00 | 9756.00 | 58536.00 | 9600.00 | 57600.00 | 5500.00 | 33000.00 | 6000.00 | 36000.00 | 7000.00 | 42000.00 | 7500.00 | 45000.00 | 7250.00 | 43500.00 | 6500.00 | 39000.00 | 3800.00 | 22800.00 | 12500.00 | 75000.00 | 8950.00 | 53700.00 | 10000.00 | 60000.00 | 5500.00 | 33000.00 | 6300.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
152.00 | Provision of SCADA system for electrical parameter recording and monitoring system and associated wiring works software, hardware, integration, desktop computer etc complete as required (for 11 points/feeders only) | 1.00 | Job | 10.00 | 300000.00 | 300000.00 | 750088.00 | 750088.00 | 500000.00 | 500000.00 | 1500000.00 | 1500000.00 | 2500000.00 | 2500000.00 | 4600000.00 | 4600000.00 | 1715875.00 | 1715875.00 | 186660.00 | 186660.00 | 450000.00 | 450000.00 | 148740.00 | 148740.00 | 628049.00 | 628049.00 | 720000.00 | 720000.00 | 450000.00 | 450000.00 | 500000.00 | 500000.00 | 385000.00 | 385000.00 | 250000.00 | 250000.00 | 850000.00 | 850000.00 | 550000.00 | 550000.00 | 300000.00 | 300000.00 | 580000.00 | 580000.00 | 425000.00 | 425000.00 | 1000000.00 | 1000000.00 | 250000.00 | 250000.00 | 148740.00 | Incotech Engineers Pvt Ltd
153.00 | Dismantling of existing 415 volt, 50Hz LT panels/AMF with accessories by disconnecting electrical connections, earthing connections of panels and transporting the upto AAI store (not more than 50 mtrs) by engaging skilled and unskilled manpower, mechanical means with required T & P etc complete as required.
154.00 | Non Essential Panel (approx. size 11x2.3x1.2 mtr) | 1.00 | Job | 10.00 | 60000.00 | 60000.00 | 11500.00 | 11500.00 | 20000.00 | 20000.00 | 15000.00 | 15000.00 | 35000.00 | 35000.00 | 4000.00 | 4000.00 | 54155.00 | 54155.00 | 46665.00 | 46665.00 | 20000.00 | 20000.00 | 11500.00 | 11500.00 | 6707.00 | 6707.00 | 72000.00 | 72000.00 | 20000.00 | 20000.00 | 100000.00 | 100000.00 | 90000.00 | 90000.00 | 15000.00 | 15000.00 | 30000.00 | 30000.00 | 25000.00 | 25000.00 | 20000.00 | 20000.00 | 40000.00 | 40000.00 | 8000.00 | 8000.00 | 50000.00 | 50000.00 | 10000.00 | 10000.00 | 4000.00 | MEC ENGINEERS
155.00 | Essential Panel (approx. size 13.2x2.4x1.0 mtr ) | 1.00 | Job | 10.00 | 70000.00 | 70000.00 | 13800.00 | 13800.00 | 25000.00 | 25000.00 | 22000.00 | 22000.00 | 35000.00 | 35000.00 | 4000.00 | 4000.00 | 54155.00 | 54155.00 | 46665.00 | 46665.00 | 20000.00 | 20000.00 | 11500.00 | 11500.00 | 6707.00 | 6707.00 | 84000.00 | 84000.00 | 20000.00 | 20000.00 | 100000.00 | 100000.00 | 110000.00 | 110000.00 | 15000.00 | 15000.00 | 35000.00 | 35000.00 | 25000.00 | 25000.00 | 20000.00 | 20000.00 | 40000.00 | 40000.00 | 10000.00 | 10000.00 | 50000.00 | 50000.00 | 15000.00 | 15000.00 | 4000.00 | MEC ENGINEERS
156.00 | AMF panel/ LT panels/capacitor panels (approx. size 2.3x2.1x1.1 mtr ) | 9.00 | Job | 10.00 | 5000.00 | 45000.00 | 4600.00 | 41400.00 | 3000.00 | 27000.00 | 25000.00 | 225000.00 | 3000.00 | 27000.00 | 3000.00 | 27000.00 | 18954.00 | 170586.00 | 9333.00 | 83997.00 | 5000.00 | 45000.00 | 2300.00 | 20700.00 | 3049.00 | 27441.00 | 13200.00 | 118800.00 | 20000.00 | 180000.00 | 15000.00 | 135000.00 | 15000.00 | 135000.00 | 6500.00 | 58500.00 | 3000.00 | 27000.00 | 3500.00 | 31500.00 | 20000.00 | 180000.00 | 10000.00 | 90000.00 | 5000.00 | 45000.00 | 50000.00 | 450000.00 | 5000.00 | 45000.00 | 20700.00 | Incotech Engineers Pvt Ltd
157.00 | Provision of standby power supply /mobile DG sets to meet out power supply requirements of hostel and institute block during panel ITC works at 33 KV sub station
158.00 | 125 KVA DG Set | 80.00 | Hrs | 10.00 | 3500.00 | 280000.00 | 2688.00 | 215040.00 | 1200.00 | 96000.00 | 20000.00 | 1600000.00 | 3000.00 | 240000.00 | 5000.00 | 400000.00 | 2241.00 | 179280.00 | 2613.00 | 209040.00 | 2588.00 | 207040.00 | 2274.00 | 181920.00 | 1335.00 | 106800.00 | 3573.00 | 285840.00 | 1000.00 | 80000.00 | 3000.00 | 240000.00 | 900.00 | 72000.00 | 3500.00 | 280000.00 | 2200.00 | 176000.00 | 25000.00 | 2000000.00 | 2000.00 | 160000.00 | 2000.00 | 160000.00 | 650.00 | 52000.00 | 1875.00 | 150000.00 | 2500.00 | 200000.00 | 52000.00 | Actech Engineers
159.00 | 82.5 KVA DG Set | 120.00 | Hrs | 10.00 | 2100.00 | 252000.00 | 1917.00 | 230040.00 | 1000.00 | 120000.00 | 14500.00 | 1740000.00 | 2500.00 | 300000.00 | 4000.00 | 480000.00 | 1726.00 | 207120.00 | 1866.60 | 223992.00 | 2120.00 | 254400.00 | 1702.00 | 204240.00 | 890.00 | 106800.00 | 2248.00 | 269760.00 | 1000.00 | 120000.00 | 2000.00 | 240000.00 | 750.00 | 90000.00 | 2400.00 | 288000.00 | 1677.00 | 201240.00 | 20000.00 | 2400000.00 | 1800.00 | 216000.00 | 1600.00 | 192000.00 | 450.00 | 54000.00 | 1250.00 | 150000.00 | 2000.00 | 240000.00 | 54000.00 | Actech Engineers
160.00 | Providing arrangements of electrical connections of LT load side with proper protection standards during transition period removal (existing LT panels) and installation of (new LT panels). The arrangement also includes provision of required rating switchgear, busbar, enclosure and suitable size of LT cables etc as required during execution of ITC LT panels. (any assistance or clarification shall be with the approval of EIC) | 1.00 | Job | 10.00 | 300000.00 | 300000.00 | 120750.00 | 120750.00 | 200000.00 | 200000.00 | 100000.00 | 100000.00 | 150000.00 | 150000.00 | 200000.00 | 200000.00 | 152385.00 | 152385.00 | 186660.00 | 186660.00 | 42000.00 | 42000.00 | 304750.00 | 304750.00 | 609756.00 | 609756.00 | 372000.00 | 372000.00 | 25000.00 | 25000.00 | 105911.00 | 105911.00 | 225000.00 | 225000.00 | 350000.00 | 350000.00 | 550000.00 | 550000.00 | 200000.00 | 200000.00 | 50000.00 | 50000.00 | 60000.00 | 60000.00 | 225000.00 | 225000.00 | 196800.00 | 196800.00 | 50000.00 | 50000.00 | 25000.00 | shiv electric
161.00 | Dismantling of following LT cables from open masonry duct and relaying the same cable on cable tray/open duct etc as required.
162.00 | up to 95 sqmm | 455.00 | Mtr | 10.00 | 100.00 | 45500.00 | 92.00 | 41860.00 | 30.00 | 13650.00 | 145.00 | 65975.00 | 40.00 | 18200.00 | 40.00 | 18200.00 | 302.00 | 137410.00 | 46.66 | 21230.30 | 30.00 | 13650.00 | 23.00 | 10465.00 | 195.00 | 88725.00 | 90.00 | 40950.00 | 60.00 | 27300.00 | 100.00 | 45500.00 | 30.00 | 13650.00 | 50.00 | 22750.00 | 75.00 | 34125.00 | 25.00 | 11375.00 | 50.00 | 22750.00 | 160.00 | 72800.00 | 65.00 | 29575.00 | 150.00 | 68250.00 | 30.00 | 13650.00 | 10465.00 | Incotech Engineers Pvt Ltd
163.00 | Above 95 sq. mm and upto 185 sq. mm | 450.00 | Mtr | 10.00 | 120.00 | 54000.00 | 161.00 | 72450.00 | 40.00 | 18000.00 | 245.00 | 110250.00 | 60.00 | 27000.00 | 50.00 | 22500.00 | 382.00 | 171900.00 | 46.66 | 20997.00 | 40.00 | 18000.00 | 35.00 | 15750.00 | 256.00 | 115200.00 | 120.00 | 54000.00 | 60.00 | 27000.00 | 200.00 | 90000.00 | 60.00 | 27000.00 | 65.00 | 29250.00 | 110.00 | 49500.00 | 35.00 | 15750.00 | 60.00 | 27000.00 | 257.00 | 115650.00 | 170.00 | 76500.00 | 150.00 | 67500.00 | 50.00 | 22500.00 | 15750.00 | Brilltech Engineers Pvt. Ltd., Incotech Engineers Pvt Ltd
164.00 | Above 185 sq. mm and upto 400 sq. mm | 555.00 | Mtr | 10.00 | 200.00 | 111000.00 | 207.00 | 114885.00 | 50.00 | 27750.00 | 300.00 | 166500.00 | 80.00 | 44400.00 | 60.00 | 33300.00 | 542.00 | 300810.00 | 46.66 | 25896.30 | 50.00 | 27750.00 | 58.00 | 32190.00 | 341.00 | 189255.00 | 198.00 | 109890.00 | 60.00 | 33300.00 | 250.00 | 138750.00 | 70.00 | 38850.00 | 75.00 | 41625.00 | 160.00 | 88800.00 | 45.00 | 24975.00 | 70.00 | 38850.00 | 321.00 | 178155.00 | 240.00 | 133200.00 | 150.00 | 83250.00 | 100.00 | 55500.00 | 24975.00 | Brilltech Engineers Pvt. Ltd.
| Total in Figures |  |  |  |  | 14726171.00 |  | 16784914.50 |  | 14983750.00 |  | 18014475.00 |  | 17123100.00 |  | 19531322.00 |  | 18475640.00 |  | 18928653.96 |  | 16300585.00 |  | 16199360.00 |  | 17985646.00 |  | 17686918.00 |  | 14063340.00 |  | 18825511.00 |  | 18742812.00 |  | 15522350.00 |  | 16048118.00 |  | 18605223.00 |  | 16912224.00 |  | 14845651.75 |  | 15492337.70 |  | 16982778.00 |  | 18188180.00
Lowest Amount Quoted BY: shiv electric(14063340.00)

## BOQ Summary
BOQ Summary Details Tender Title: Augmentation of power supply system, substation and allied work at CATC Allahabad. SH-Replacement of existing LT Panels of 33 KV Substation Tender ID: 2021_AAI_66875_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | shiv electric | 14063340.00 | L1
| 2 | ECS ENGINEERING PVT LTD | 14726171.00 | L2
| 3 | RISHA CONTROL ENGINEERS PRIVATE LIMITED | 14845651.75 | L3
| 4 | DOSHI ELECTRIC ENGG. CO. | 14983750.00 | L4
| 5 | Actech Engineers | 15492337.70 | L5
| 6 | RASS CONTRACTOR AND ENGINEERS | 15522350.00 | L6
| 7 | Aditya Techno Products Private Limited | 16048118.00 | L7
| 8 | Incotech Engineers Pvt Ltd | 16199360.00 | L8
| 9 | Choubay And Co.(Agencies) Pvt.Ltd. | 16300585.00 | L9
| 10 | SARASWAT ENGINEERING SERVICES | 16784914.50 | L10
| 11 | GAYATRI ELECTRICAL | 16912224.00 | L11
| 12 | Jha power corporation | 16982778.00 | L12
| 13 | JITENDRA ELECTRICALS | 17123100.00 | L13
| 14 | Power And Instrumentation Guj Ltd | 17686918.00 | L14
| 15 | KRISHNA REFRIGERATION | 17985646.00 | L15
| 16 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION | 18014475.00 | L16
| 17 | Water Power Engg. Enterprises | 18188180.00 | L17
| 18 | TECHNISYS ENGINEERING PRIVATE LIMITED | 18475640.00 | L18
| 19 | Brilltech Engineers Pvt. Ltd. | 18605223.00 | L19
| 20 | Manish Electricals | 18742812.00 | L20
| 21 | Shekhawati Electrical Engineers | 18825511.00 | L21
| 22 | Deora Electricals | 18928653.96 | L22
| 23 | MEC ENGINEERS | 19531322.00 | L23