## BoQ1
Government eProcurement System Created By: Malkit Singh Created Date/Time: 08-Feb-2021 11:29 AM Tender Title: Construction of 50 KL capacity RCC Overhead water tank for Firefighting Services at Dehradun Airport Tender ID: 2021_AAI_67820_1
Tender Inviting Authority: Asstt. General Manager (E-C), AAI, Dehradun Airport
Name of Work: Construction of 50 KL capacity RCC Overhead water tank for Firefighting Services at Dehradun Airport.
Contract No: 2021_AAI_67538_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ESS KAY CONSTRUCTIONS(GSTN-07AABFE6199D1ZF) |  | POONAM ENTERPRISES(GSTN-NA) |  | Umang Enterprises(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Earth work in excavation by mechanical means (Hydraulic excavator)/manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in-charge. | 105.00 | Cum |  | 300.00 | 31500.00 | 250.00 | 26250.00 | 240.00 | 25200.00 | 25200.00 | Umang Enterprises
2.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :1:5:10(1 Cement :5 coarse sand : 10 graded stone aggregate 40 mm nominal size) | 5.00 | cum |  | 5500.00 | 27500.00 | 7000.00 | 35000.00 | 4700.00 | 23500.00 | 23500.00 | Umang Enterprises
3.00 | Providing and laying in position machine batched and machine mixed design mix M-25 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing and reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer-in-charge. (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately). All works upto plinth level | 22.00 | cum |  | 8500.00 | 187000.00 | 8000.00 | 176000.00 | 6600.00 | 145200.00 | 145200.00 | Umang Enterprises
4.00 | Providing and laying in position machine batched and machine mixed design mix M-25 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing and reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer-in-charge. (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately). All works above plinth level upto floor V level | 36.00 | cum |  | 8500.00 | 306000.00 | 8000.00 | 288000.00 | 7600.00 | 273600.00 | 273600.00 | Umang Enterprises
5.00 | Extra for providing richer mixes at all floor levels. Note:- Excess/less cement over the specified cement content used is payable /recoverable separately. Providing M-30 grade concrete instead of M-25 grade BMC/RMC. (Note:- Cement content considered in M-30 is @ 340 kg/cum) | 58.00 | cum |  | 350.00 | 20300.00 | 100.00 | 5800.00 | 61.00 | 3538.00 | 3538.00 | Umang Enterprises
6.00 | Extra for providing and mixing water proofing material in cement concrete work in doses by weight of cement as per manufacturer's specification | 120.00 | per 50kg cement |  | 120.00 | 14400.00 | 80.00 | 9600.00 | 51.00 | 6120.00 | 6120.00 | Umang Enterprises
7.00 | Centering and shuttering including strutting, propping etc. and removal of form for : Foundations, footings, bases of columns, etc. for mass concrete | 20.00 | sqm |  | 500.00 | 10000.00 | 600.00 | 12000.00 | 240.00 | 4800.00 | 4800.00 | Umang Enterprises
8.00 | Centering and shuttering including strutting, propping etc. and removal of form for : Suspended floors, roofs, landings, balconies and access platform | 60.00 | sqm |  | 780.00 | 46800.00 | 500.00 | 30000.00 | 550.00 | 33000.00 | 30000.00 | POONAM ENTERPRISES
9.00 | Centering and shuttering including strutting, propping etc. and removal of form for : Lintels, beams, plinth beams, girders, bressumers and cantilevers | 60.00 | sqm |  | 750.00 | 45000.00 | 400.00 | 24000.00 | 460.00 | 27600.00 | 24000.00 | POONAM ENTERPRISES
10.00 | Centering and shuttering including strutting, propping etc. and removal of form for : Columns, Pillars, Piers, Abutments, Posts and Struts | 115.00 | sqm |  | 750.00 | 86250.00 | 500.00 | 57500.00 | 570.00 | 65550.00 | 57500.00 | POONAM ENTERPRISES
11.00 | Extra for shuttering in circular work (20% of respective centering and shuttering items) | 12.00 | sqm |  | 300.00 | 3600.00 | 280.00 | 3360.00 | 20.00 | 240.00 | 240.00 | Umang Enterprises
12.00 | Extra for additional height in centering, shuttering where ever required with adequate bracing, propping etc., including cost of de-shuttering and decentering at all levels, over a height of 3.5 m, for every additional height of 1 metre or part thereof (Plan area to be measured). Suspended floors, roofs, landing, beams and balconies (Plan area to be measured) | 390.00 | sqm |  | 750.00 | 292500.00 | 200.00 | 78000.00 | 230.00 | 89700.00 | 78000.00 | POONAM ENTERPRISES
13.00 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto and above plinth level. Thermo-Mechanically Treated bars of grade Fe-500D or more. | 9110.00 | Kg |  | 90.00 | 819900.00 | 80.00 | 728800.00 | 62.50 | 569375.00 | 569375.00 | Umang Enterprises
14.00 | Providing and fixing G.I. pipes complete with G.I. fittings including trenching and refilling etc. 80 mm dia nominal bore | 50.00 | metre |  | 900.00 | 45000.00 | 900.00 | 45000.00 | 500.00 | 25000.00 | 25000.00 | Umang Enterprises
15.00 | Providing and fixing G.I. Union in G.I. pipe including cutting and threading the pipe and making long screws etc. complete (New work) : 80 mm nominal bore | 2.00 | Each |  | 1000.00 | 2000.00 | 2000.00 | 4000.00 | 890.00 | 1780.00 | 1780.00 | Umang Enterprises
16.00 | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) : 80 mm nominal bore | 2.00 | each |  | 6500.00 | 13000.00 | 2000.00 | 4000.00 | 1950.00 | 3900.00 | 3900.00 | Umang Enterprises
17.00 | 6 mm cement plaster of mix : 1:3 (1 cement : 3 fine sand) | 255.00 | sqm |  | 450.00 | 114750.00 | 250.00 | 63750.00 | 180.00 | 45900.00 | 45900.00 | Umang Enterprises
18.00 | Neat cement punning. | 255.00 | sqm |  | 50.00 | 12750.00 | 80.00 | 20400.00 | 55.00 | 14025.00 | 12750.00 | ESS KAY CONSTRUCTIONS
19.00 | Steel work welded in built up sections/ framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer using structural steel etc. as required. In gratings, frames, guard bar, ladder, railings, brackets, gates and similar works | 1310.00 | kg |  | 140.00 | 183400.00 | 80.00 | 104800.00 | 115.00 | 150650.00 | 104800.00 | POONAM ENTERPRISES
20.00 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade : Two or more coats on new work | 125.00 | Sqm |  | 120.00 | 15000.00 | 200.00 | 25000.00 | 155.00 | 19375.00 | 15000.00 | ESS KAY CONSTRUCTIONS
21.00 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/10 sqm) | 95.00 | sqm |  | 120.00 | 11400.00 | 100.00 | 9500.00 | 144.00 | 13680.00 | 9500.00 | POONAM ENTERPRISES
22.00 | Supplying and fixing C.I. cover without frame for manholes : 455x610 mm rectangular C.I. cover (light duty) the weight of the cover to be not less than 23 kg | 1.00 | each |  | 4500.00 | 4500.00 | 5000.00 | 5000.00 | 1166.00 | 1166.00 | 1166.00 | Umang Enterprises
23.00 | Providing and submitting the structural design & drawing for the proposed construction of R.C.C Over Head Tank. The structural design and drawing shall be done by a structural consultant and the contractor shall submit the design and drawing to Engineer-in-charge after vetting from IIT/NIT. In case any clarification/ alteration in design is made by Engineer-in-charge, it will be made by the consultant for which nothing shall be paid extra. Total 5 (Five) sets of Design and drawing showing all relevant details shall be submitted to E.I.C. Note :- The contractor shall appoint the consultant for soil investigation and structural design with prior approval of Engineer-in-charge. | 1.00 | Job |  | 300000.00 | 300000.00 | 356000.00 | 356000.00 | 50000.00 | 50000.00 | 50000.00 | Umang Enterprises
| Total in Figures |  |  |  |  | 2592550.00 |  | 2111760.00 |  | 1592899.00
Lowest Amount Quoted BY: Umang Enterprises(1592899.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of 50 KL capacity RCC Overhead water tank for Firefighting Services at Dehradun Airport Tender ID: 2021_AAI_67820_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Umang Enterprises | 1592899.00 | L1
| 2 | POONAM ENTERPRISES | 2111760.00 | L2
| 3 | ESS KAY CONSTRUCTIONS | 2592550.00 | L3