## BoQ1
Government eProcurement System Created By: D Boominathan Created Date/Time: 12-Feb-2021 12:43 PM Tender Title: Retrofitting of Air Circuit breakers and MCCBs in the Existing Essential LT panels at Trichy Airport Tender ID: 2021_AAI_68448_1
Tender Inviting Authority: Assistant General Manager (E-E)
Name of Work: Retrofitting of Air Circuit breakers and MCCBs in the Existing Essential LT panels at Trichy Airport
Contract No: CW-10/TRY/20-21 Tender ID: 2021_AAI_68448_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | jaydeep agency corporation(GSTN-24ACIPP6157B1ZQ) |  | ECS ENGINEERING PVT LTD(GSTN-09AABCE5944P1Z1) |  | Kontact Consortium India Pvt Ltd(GSTN-33AADCK6124H1ZT) |  | vk sam engineering(GSTN-33AMZPS4037L1ZA) |  | ESSENN POWER CONTROLS PVT LTD(GSTN-33AAACE9380J1ZZ) |  | CHENNAI ENGINEERING SERVICES(GSTN-33AADFC4373K1ZH)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying and fixing/retro fitting of 4Pole, 415V, 2500Amps, Icu=Ics=65kA, breaking capacity ACB with IP53 protection, having microprocessor based release with EDO type, draw-out version, provision with shunt trip coil of 230V AC, under voltage release of 220V AC, rear terminals, base for draw-out device, Automatic / Manual spring charging system with all accessories with meeting technical specification of ACB suitable for AMF operation of 1010KVA DG set and to fix in the existing LT panel (Essential) with required modification in panel if any including dismantling of existing ACB, installing new ACB, connection with incoming & outgoing bus bars by modification, interconnection with AMF relays, contactors by using the same control wirings / replacement of control cables if required, providing mechanical and Electrical interlocking system with DG set ACB, EB Incomer ACB and bus coupler ACB of the same section, modifying/replacing the door in same finish of existing one etc., as per the direction of the Engineer-In-charge and its equivallent to Make: ABB, Model: New EMax PR123/EMax2.0/ Make: L&T Model: Omega MTX 3.5 | 6.00 | Each |  | 348000.00 | 2088000.00 | 273000.00 | 1638000.00 | 285000.00 | 1710000.00 | 245250.00 | 1471500.00 | 285136.00 | 1710816.00 | 269999.00 | 1619994.00 | 1471500.00 | vk sam engineering
2.00 | Supplying and fixing/retro fitting of 4Pole, 415V, 2500Amps, Icu=Ics=65kA, breaking capacity ACB with IP53 protection, having microprocessor based release with EDO type, draw-out version, provision with shunt trip coil of 230V AC, under voltage release of 220V AC, rear terminals, base for draw-out device, Automatic / Manual spring charging system with all accessories with meeting technical specification of ACB to fix in the existing LT panel (Essential) with required modification in panel if any including dismantling of existing ACB, installing new ACB, connection with incoming & outgoing bus bars by modification, interconnection with other relays, contactors by using the same control wirings / replacement of control cables if required, modifying/replacing the door in same finish of existing one etc., as per the direction of the Engineer-In-charge and its equivallent to Make: ABB, Model: New EMax PR123/EMax2.0/ Make: L&T Model: Omega MTX 3.5 | 4.00 | Each |  | 348000.00 | 1392000.00 | 268000.00 | 1072000.00 | 285000.00 | 1140000.00 | 245250.00 | 981000.00 | 285186.00 | 1140744.00 | 269999.00 | 1079996.00 | 981000.00 | vk sam engineering
3.00 | Supplying and fixing/retro fitting of 4Pole, 415V, 1250Amps, Icu=Ics=50kA, breaking capacity ACB with IP53 protection, having microprocessor based release with MDO type, draw-out version, provision with shunt trip coil of 230V AC, rear terminals, base for draw-out device, Manual spring charging system with all accessories with meeting technical specification of ACB to fix in the existing LT panel (Essential) with required modification in panel including dismantling of existing ACB, installing new ACB, connection with incoming & outgoing bus bars by modification, interconnection with other relays, contactors by using the same control wirings / replacement of control cables if required, providing mechanical and Electrical interlocking system with other Incomer ACBs and bus coupler ACB of the same section, modifying/replacing the door in same finish of existing one etc., as per the direction of the Engineer-In-charge and its equivallent to Make: ABB, Model: New EMax PR123/EMax2.0/ Make: L&T Model: Omega MTX 3.5 | 4.00 | Each |  | 150000.00 | 600000.00 | 153000.00 | 612000.00 | 225000.00 | 900000.00 | 188200.00 | 752800.00 | 173497.00 | 693988.00 | 244999.00 | 979996.00 | 600000.00 | jaydeep agency corporation
4.00 | Supply, Fixing/retrofitting, Testing and commissioning 630 Amps, Four Pole Moulded Case Circuit Breaker (MCCB) having adjustable Thermal ( 80% - 100% ) and Fixed Magnetic Release with Rotary handle and the Breaking capacity Icu=Ics = 100%Icu at 415 V, 36 kA in existing cubicle LT panel with required modification in panel including dismantling of existing 630A FSU's, Fixing MCCB, connection with incoming & outgoing bus bars by modification, providing mechanical interlocking system with other Incomer MCCBs and bus coupler MCCBs of the same panel, modifying the door in same finish of existing one etc., as per the direction of the Engineer-In-charge and its equivallent to Make: ABB, Model: New EMax PR123/EMax2.0/ Make: L&T Model: Omega MTX 3.5 | 18.00 | Each |  | 49000.00 | 882000.00 | 40102.00 | 721836.00 | 30000.00 | 540000.00 | 54600.00 | 982800.00 | 45400.00 | 817200.00 | 44999.00 | 809982.00 | 540000.00 | Kontact Consortium India Pvt Ltd
5.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on the surface as required. Above 185 sq. mm and upto 400 sq.mm mm | 180.00 | Mtrs |  | 50.00 | 9000.00 | 80.00 | 14400.00 | 200.00 | 36000.00 | 75.00 | 13500.00 | 98.00 | 17640.00 | 99.00 | 17820.00 | 9000.00 | jaydeep agency corporation
6.00 | Supplying and making end termination with aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 300 sq. mm (70mm) | 12.00 | Set |  | 1000.00 | 12000.00 | 2000.00 | 24000.00 | 1500.00 | 18000.00 | 1300.00 | 15600.00 | 1759.00 | 21108.00 | 749.00 | 8988.00 | 8988.00 | CHENNAI ENGINEERING SERVICES
| Total in Figures |  |  |  |  | 4983000.00 |  | 4082236.00 |  | 4344000.00 |  | 4217200.00 |  | 4401496.00 |  | 4516776.00
Lowest Amount Quoted BY: ECS ENGINEERING PVT LTD(4082236.00)

## BOQ Summary
BOQ Summary Details Tender Title: Retrofitting of Air Circuit breakers and MCCBs in the Existing Essential LT panels at Trichy Airport Tender ID: 2021_AAI_68448_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | ECS ENGINEERING PVT LTD | 4082236.00 | L1
| 2 | vk sam engineering | 4217200.00 | L2
| 3 | Kontact Consortium India Pvt Ltd | 4344000.00 | L3
| 4 | ESSENN POWER CONTROLS PVT LTD | 4401496.00 | L4
| 5 | CHENNAI ENGINEERING SERVICES | 4516776.00 | L5
| 6 | jaydeep agency corporation | 4983000.00 | L6