## BoQ1
Government eProcurement System Created By: SREEDHAR P V Created Date/Time: 18-Feb-2021 03:08 PM Tender Title: Extension of Fire suppression system at GAGAN Complex, AAI, Bangalore Tender ID: 2021_AAI_68789_1
Tender Inviting Authority: Asst.General Manager (Engg. – Electrical), AAI, Bangalore
Name of Work: EXTENSION OF FIRE SUPPRESSION SYSTEM AT GAGAN COMPLEX, BANGALORE
Contract No: 2021_AAI_68789_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | OASIS ENGINEERS(GSTN-27AKCPD8929P1ZK) |  | CENTRE TAP ENGINEERING(GSTN-24AGPPP8172K1ZP) |  | Ponmani International (India) Pvt Ltd(GSTN-33AADCP6242R2ZZ) |  | GLYPTIC(GSTN-19AAMFG0478J1ZY) |  | Fitech Engineers Pvt. Ltd.(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying, installation and testin and commissioning of 80 litre capacity, seamless, high pressure, cylinder assembly, conforming to IS - 7285 ( PT-2): 2004 or UL - 2166 etc. complete as required including valve, bracket assembly and 2 inch flexible discharge hose etc. complete as required. | 1.00 | Each |  | 112500.00 | 112500.00 | 96000.00 | 96000.00 | 85000.00 | 85000.00 | 140000.00 | 140000.00 | 90000.00 | 90000.00 | 85000.00 | Ponmani International (India) Pvt Ltd
2.00 | Supplying and filling of clean, odourless, colour less, UL listed and suitable for fire class - A, B & C fire suppression agent ( Novec 1230 fire protection fluid) etc. complete as required. | 46.00 | Kg |  | 2600.00 | 119600.00 | 2400.00 | 110400.00 | 2950.00 | 135700.00 | 3150.00 | 144900.00 | 2700.00 | 124200.00 | 110400.00 | CENTRE TAP ENGINEERING
3.00 | Supplying, installation, testing and commissioning of 24 V DC, electric actuator for triggering the cylinder assembly etc. complete as required. | 1.00 | Each |  | 26000.00 | 26000.00 | 19200.00 | 19200.00 | 45000.00 | 45000.00 | 27000.00 | 27000.00 | 49500.00 | 49500.00 | 19200.00 | CENTRE TAP ENGINEERING
4.00 | Supplying, installation, testing and commissioning of Local manual / pneumatic actuator for triggering the cylinder assembly complete as required. | 1.00 | Each |  | 16000.00 | 16000.00 | 9000.00 | 9000.00 | 35000.00 | 35000.00 | 32044.00 | 32044.00 | 8500.00 | 8500.00 | 8500.00 | Fitech Engineers Pvt. Ltd.
5.00 | Supplying, installation, testing and commissioning of Low pressure switch for the cylinder assembly etc. complete as required. | 1.00 | Each |  | 14000.00 | 14000.00 | 16650.00 | 16650.00 | 15000.00 | 15000.00 | 21454.00 | 21454.00 | 9000.00 | 9000.00 | 9000.00 | Fitech Engineers Pvt. Ltd.
6.00 | Supplying, installation, testing and commissioning of Manual Gas Release Station etc. complete as required. | 3.00 | Each |  | 1200.00 | 3600.00 | 2250.00 | 6750.00 | 1520.00 | 4560.00 | 1200.00 | 3600.00 | 900.00 | 2700.00 | 2700.00 | Fitech Engineers Pvt. Ltd.
7.00 | Supplying, installation, testing and commissioning of Manual Gas Abort Station etc. complete as required. | 3.00 | Each |  | 1200.00 | 3600.00 | 2250.00 | 6750.00 | 1520.00 | 4560.00 | 1200.00 | 3600.00 | 900.00 | 2700.00 | 2700.00 | Fitech Engineers Pvt. Ltd.
8.00 | Supllying and fixing of suitable size ( as per hydraulic flow calculation ) nozzle with orfices etc. complete as required. | 3.00 | Each |  | 6200.00 | 18600.00 | 4500.00 | 13500.00 | 4950.00 | 14850.00 | 3562.00 | 10686.00 | 3600.00 | 10800.00 | 10686.00 | GLYPTIC
9.00 | Supply of 2 Core X 1.5 Sq.mm FRLS Cable for Detector loop wiring | 200.00 | Mtr. |  | 98.00 | 19600.00 | 108.00 | 21600.00 | 99.00 | 19800.00 | 110.00 | 22000.00 | 90.00 | 18000.00 | 18000.00 | Fitech Engineers Pvt. Ltd.
10.00 | Supply Installation Testing and Commissioning of 02 Zone conventional Gas Release panel equivalent to Ravel make RE120 GR etc. as required. | 4.00 | Each |  | 12000.00 | 48000.00 | 13500.00 | 54000.00 | 22900.00 | 91600.00 | 11200.00 | 44800.00 | 18000.00 | 72000.00 | 44800.00 | GLYPTIC
11.00 | Extension of existing MS pipe line of gas suppression system on wall/ceiling by supplying and fixing 50mm dia ASTM A53, Grade B or ASTM A 106, Grade B MS pipe line on wall/ ceiling and making interconnections i/c Tee, Bend etc.as required. | 96.00 | Mtr. |  | 1500.00 | 144000.00 | 900.00 | 86400.00 | 1050.00 | 100800.00 | 200.00 | 19200.00 | 450.00 | 43200.00 | 19200.00 | GLYPTIC
12.00 | Changing the detector wiring loop from the connected loop to other existing loop by laying the already supplied 2 Core X 1.5 Sq.mm wire on wall/ceiling and making interconnections etc.as required. | 150.00 | Mtr. |  | 98.00 | 14700.00 | 108.00 | 16200.00 | 45.00 | 6750.00 | 35.00 | 5250.00 | 45.00 | 6750.00 | 5250.00 | GLYPTIC
13.00 | Programming of existing centralized Notifier panel for the changed loop and existing loop, testing, commissioning of all the loops etc.as required. NFS-3030D and NFS 3030ND | 1.00 | Each |  | 15000.00 | 15000.00 | 27000.00 | 27000.00 | 5000.00 | 5000.00 | 44000.00 | 44000.00 | 36000.00 | 36000.00 | 5000.00 | Ponmani International (India) Pvt Ltd
14.00 | Supply, Installation, testing and commissioning of Notifier zone monitor module for indication of gas release panel in main fire alarm control panel | 1.00 | Each |  | 7000.00 | 7000.00 | 4500.00 | 4500.00 | 3500.00 | 3500.00 | 6500.00 | 6500.00 | 5670.00 | 5670.00 | 3500.00 | Ponmani International (India) Pvt Ltd
15.00 | Supply, Installation, testing and commissioning of conventional smoke detector for new area | 8.00 | Each |  | 1600.00 | 12800.00 | 2000.00 | 16000.00 | 1150.00 | 9200.00 | 1265.00 | 10120.00 | 1260.00 | 10080.00 | 9200.00 | Ponmani International (India) Pvt Ltd
16.00 | Supply, Installation, testing and commissioning of flasher sounder for new area | 1.00 | Each |  | 1500.00 | 1500.00 | 3000.00 | 3000.00 | 1450.00 | 1450.00 | 2130.00 | 2130.00 | 900.00 | 900.00 | 900.00 | Fitech Engineers Pvt. Ltd.
| Total in Figures |  |  |  |  | 576500.00 |  | 506950.00 |  | 577770.00 |  | 537284.00 |  | 490000.00
Lowest Amount Quoted BY: Fitech Engineers Pvt. Ltd.(490000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Extension of Fire suppression system at GAGAN Complex, AAI, Bangalore Tender ID: 2021_AAI_68789_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Fitech Engineers Pvt. Ltd. | 490000.00 | L1
| 2 | CENTRE TAP ENGINEERING | 506950.00 | L2
| 3 | GLYPTIC | 537284.00 | L3
| 4 | OASIS ENGINEERS | 576500.00 | L4
| 5 | Ponmani International (India) Pvt Ltd | 577770.00 | L5