## BoQ1
Government eProcurement System Created By: Lakhan Pal Singh Solanki Created Date/Time: 26-Mar-2021 12:43 PM Tender Title: Construction Of Cargo Complex At Srinagar Intl Airport, Srinagar (SH Electrical Works) Tender ID: 2021_AAI_69146_1
Tender Inviting Authority: AGM (ENGG-ELECT), AAI, SRINAGAR INTERNATIONAL AIRPORT, SRINAGAR, J&K-190007.
Name of Work: CONSTRUCTION OF CARGO COMPLEX AT Srinagar Int'l Airport,Srinagar. SH: ELECTRICAL WORKS.
Contract No: <Enter Contract No Details>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED(GSTN-07ABDCS2796Q1ZH) |  | HLK Infrastructure Pvt Ltd(GSTN-07AACCH5773N1Z2) |  | JCC ENGINEERS PRIVATE LIMITED(GSTN-NA) |  | CIS GLOBAL INFRATECH PRIVATE LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I: INTERNAL & EXTERNAL ELECTRICAL INSTALLATIONS
2.00 | Supply of 2'X2' recess/ surface mounting 34/36W full window LED light fixture having white powder coated CRCA housing with heat sink, driver and front frame with translucent cover complete with all accessories as per technical specifications of tender document. | 125.00 | Nos. |  | 1286.25 | 160781.25 | 4250.00 | 531250.00 | 800.00 | 100000.00 | 950.00 | 118750.00 | 100000.00 | JCC ENGINEERS PRIVATE LIMITED
3.00 | Supply of 60W Highbay fitting made of powder coated Aluminium housing having operating Voltage Range of 140 to 270V AC supply complete with all accessories as per technical specifications of tender document. | 15.00 | Nos. |  | 3057.00 | 45855.00 | 13850.00 | 207750.00 | 3000.00 | 45000.00 | 1850.00 | 27750.00 | 27750.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
4.00 | Supply of 80W Highbay fitting made of powder coated Aluminium housing having operating Voltage Range of 140 to 270V AC supply complete with all accessories as per technical specifications of tender document. | 60.00 | Nos. |  | 3431.25 | 205875.00 | 15600.00 | 936000.00 | 3000.00 | 180000.00 | 2250.00 | 135000.00 | 135000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
5.00 | Supply of 100W Highbay fitting made of powder coated Aluminium housing having operating Voltage Range of 140 to 270V AC supply complete with all accessories as per technical specifications of tender document. | 20.00 | Nos. |  | 3339.00 | 66780.00 | 17000.00 | 340000.00 | 3500.00 | 70000.00 | 2800.00 | 56000.00 | 56000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
6.00 | Supply of 15/ 18 watt round/square shape recess mounted LED Down lighter complete with all accessories as per technical specifications of tender document. | 20.00 | Nos. |  | 397.50 | 7950.00 | 1450.00 | 29000.00 | 400.00 | 8000.00 | 850.00 | 17000.00 | 7950.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
7.00 | Supply of 18/20 watt LED Batten of 4ft complete with aluminimum extruded LED tube complete with all accessories as per technical specifications of tender document. | 20.00 | Nos. |  | 219.75 | 4395.00 | 620.00 | 12400.00 | 300.00 | 6000.00 | 450.00 | 9000.00 | 4395.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
8.00 | Supply of 10W Mirror LED Light luminaire complete with all accessories as per technical specifications of tender document. | 10.00 | Nos. |  | 180.75 | 1807.50 | 2250.00 | 22500.00 | 200.00 | 2000.00 | 350.00 | 3500.00 | 1807.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
9.00 | Supply of 70 watt LED Street light with pressure die- cast aluminium cover on both side for holding extruded aluminium heat sink, with heat resistant toughened glass with control gear complete with all accessories as per technical specifications of tender document. . | 20.00 | Nos. |  | 2214.75 | 44295.00 | 6279.00 | 125580.00 | 2000.00 | 40000.00 | 2500.00 | 50000.00 | 40000.00 | JCC ENGINEERS PRIVATE LIMITED
10.00 | Supply of 1200mm dia sweep ceiling fan copper wound with double ball bearings, blades white in color, ISI marked complete with capacitor, down rod, split pin , reel but without regulator complete as required. | 5.00 | Nos. |  | 1545.00 | 7725.00 | 2250.00 | 11250.00 | 1800.00 | 9000.00 | 2250.00 | 11250.00 | 7725.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
11.00 | Supply of 300mm dia sweep wall fan with Oscillating type complete with built in String type speed regulator and mounting arrangement. (Similar to Havells make - SWING HS or equivalent) | 25.00 | Nos. |  | 1703.25 | 42581.25 | 1850.00 | 46250.00 | 2000.00 | 50000.00 | 1850.00 | 46250.00 | 42581.25 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
12.00 | Supply of 450mm dia sweep Heavy duty wall mounted air circulator oscillating type, Hi speed with 3 speed push buttons, RPM>=1400, with guard and mounting arrangement. (Similar to Bajaj make - Supreme plus air circulator 450 mm wall or equivalent) | 20.00 | Nos. |  | 3006.75 | 60135.00 | 4200.00 | 84000.00 | 3000.00 | 60000.00 | 2800.00 | 56000.00 | 56000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
13.00 | Supply of 300 mm Exhaust Fan suitable for operation on 230 volt AC supply | 12.00 | Nos. |  | 1084.50 | 13014.00 | 1850.00 | 22200.00 | 1200.00 | 14400.00 | 2800.00 | 33600.00 | 13014.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
14.00 | Supply of 450mm dia heavy duty exhaust fan having 1400 rpm suitable for operation on 230 volt AC supply . | 6.00 | Nos. |  | 2336.25 | 14017.50 | 3450.00 | 20700.00 | 3000.00 | 18000.00 | 3800.00 | 22800.00 | 14017.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
15.00 | Supply of 35 Ltr Capacity storage type Geyser ABS body suitable for 230V single phase 50Hz A.C supply with all accessories. (Make-Havells/Bajaj or Equivalent) | 4.00 | Nos. |  | 7365.00 | 29460.00 | 14499.00 | 57996.00 | 9000.00 | 36000.00 | 35000.00 | 140000.00 | 29460.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
16.00 | Installation, testing and commissioning of pre-wired, LED fitting with driver/ fluorescent fitting / compact fluorescent / street light on Pole & Boundary light with L shape bracket/ fitting of all types, complete with all accessories . directly on ceiling/ wall/ surface, including connections with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 290.00 | Each |  | 147.00 | 42630.00 | 150.00 | 43500.00 | 100.00 | 29000.00 | 1250.00 | 362500.00 | 29000.00 | JCC ENGINEERS PRIVATE LIMITED
17.00 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable etc. as required. | 5.00 | Each |  | 149.25 | 746.25 | 171.00 | 855.00 | 100.00 | 500.00 | 3200.00 | 16000.00 | 500.00 | JCC ENGINEERS PRIVATE LIMITED
18.00 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required.
18.10 | Upto 450 mm sweep | 18.00 | Nos. |  | 317.25 | 5710.50 | 363.00 | 6534.00 | 400.00 | 7200.00 | 400.00 | 7200.00 | 5710.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
19.00 | Installation of Bracket mounted/Wall mounted fan in wall/Pillers i/c connection, testing, commissioning etc. as required.
19.10 | Upto 450 mm sweep | 45.00 | Nos |  | 15.00 | 675.00 | 150.00 | 6750.00 | 50.00 | 2250.00 | 210.00 | 9450.00 | 675.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
20.00 | Installation, Testing & commissioning of existing 35 Ltr storage type Geyser etc as reqd. | 4.00 | Nos |  | 400.00 | 1600.00 | 250.00 | 1000.00 | 500.00 | 2000.00 | 1000.00 | 4000.00 | 1000.00 | HLK Infrastructure Pvt Ltd
21.00 | Supply of following size of 1.1 kv grade multicore aluminium conductor, XLPE insulated and PVC sheathed armoured cable as per IS: 7098:1988 (Part-I) with upto date amendments.
21.10 | 4core x 10 sqmm | 210.00 | Mtr. |  | 92.25 | 19372.50 | 141.00 | 29610.00 | 120.00 | 25200.00 | 190.00 | 39900.00 | 19372.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
21.20 | 4 core x 16 Sq.mm. | 240.00 | Mtr. |  | 109.50 | 26280.00 | 167.00 | 40080.00 | 130.00 | 31200.00 | 210.00 | 50400.00 | 26280.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
21.30 | 3.5 core x 25 Sq.mm | 486.00 | Mtr. |  | 132.75 | 64516.50 | 203.00 | 98658.00 | 140.00 | 68040.00 | 250.00 | 121500.00 | 64516.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
21.40 | 3.5 core x 50 Sq.mm. | 135.00 | Mtr. |  | 215.25 | 29058.75 | 329.00 | 44415.00 | 200.00 | 27000.00 | 390.00 | 52650.00 | 27000.00 | JCC ENGINEERS PRIVATE LIMITED
21.50 | 3.5core x 400 Sq.mm. | 2500.00 | Mtr. |  | 1299.00 | 3247500.00 | 1780.00 | 4450000.00 | 1500.00 | 3750000.00 | 2350.00 | 5875000.00 | 3247500.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
22.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/PVC pipe as required
22.10 | Upto 35 sq. mm | 200.00 | Mtr |  | 27.00 | 5400.00 | 31.00 | 6200.00 | 20.00 | 4000.00 | 135.00 | 27000.00 | 4000.00 | JCC ENGINEERS PRIVATE LIMITED
22.20 | Above 95 sq. mm and upto 185 sq. mm | 100.00 | Mtr |  | 56.25 | 5625.00 | 37.00 | 3700.00 | 30.00 | 3000.00 | 295.00 | 29500.00 | 3000.00 | JCC ENGINEERS PRIVATE LIMITED
22.30 | Above 185 sq. mm and upto 400 sq. mm | 2300.00 | Mtr |  | 98.25 | 225975.00 | 98.00 | 225400.00 | 30.00 | 69000.00 | 350.00 | 805000.00 | 69000.00 | JCC ENGINEERS PRIVATE LIMITED
23.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
23.10 | Upto 35 sq. mm | 145.00 | Mtr |  | 20.25 | 2936.25 | 38.00 | 5510.00 | 20.00 | 2900.00 | 120.00 | 17400.00 | 2900.00 | JCC ENGINEERS PRIVATE LIMITED
23.20 | Above 95 sq. mm and upto 185 sq. mm | 20.00 | Mtr |  | 45.75 | 915.00 | 52.00 | 1040.00 | 30.00 | 600.00 | 280.00 | 5600.00 | 600.00 | JCC ENGINEERS PRIVATE LIMITED
23.30 | Above 185 sq. mm and upto 400 sq. mm | 80.00 | Mtr |  | 84.00 | 6720.00 | 96.00 | 7680.00 | 30.00 | 2400.00 | 330.00 | 26400.00 | 2400.00 | JCC ENGINEERS PRIVATE LIMITED
24.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc. as required.
24.10 | Upto 35 sq. mm | 20.00 | Mtr |  | 146.25 | 2925.00 | 167.00 | 3340.00 | 200.00 | 4000.00 | 190.00 | 3800.00 | 2925.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
24.20 | Above 95 sq. mm and upto 185 sq. mm | 20.00 | Mtr |  | 171.00 | 3420.00 | 181.00 | 3620.00 | 250.00 | 5000.00 | 350.00 | 7000.00 | 3420.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
24.30 | Above 185 sq. mm and upto 400 sq. mm | 20.00 | Mtr |  | 209.25 | 4185.00 | 239.00 | 4780.00 | 300.00 | 6000.00 | 400.00 | 8000.00 | 4185.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
25.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Tagging on both the ends will be done with aluminium tags etc. complete as required.
25.10 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 360.00 | Mtr |  | 28.50 | 10260.00 | 39.00 | 14040.00 | 50.00 | 18000.00 | 85.00 | 30600.00 | 10260.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
26.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
26.10 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 155.00 | Mtr |  | 33.75 | 5231.25 | 39.00 | 6045.00 | 50.00 | 7750.00 | 95.00 | 14725.00 | 5231.25 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
26.20 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 10.00 | Mtr |  | 106.50 | 1065.00 | 122.00 | 1220.00 | 100.00 | 1000.00 | 155.00 | 1550.00 | 1000.00 | JCC ENGINEERS PRIVATE LIMITED
26.30 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 40.00 | Mtr |  | 159.00 | 6360.00 | 182.00 | 7280.00 | 100.00 | 4000.00 | 250.00 | 10000.00 | 4000.00 | JCC ENGINEERS PRIVATE LIMITED
27.00 | Supplying and making indoor end termination with brass single compression gland (Heavy duty type) and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor armoured cable of 1.1 KV grade as required.
27.10 | 4 core x 10 Sq.mm. | 20.00 | Set |  | 191.25 | 3825.00 | 219.00 | 4380.00 | 200.00 | 4000.00 | 750.00 | 15000.00 | 3825.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
27.20 | 4 core x 16 Sq.mm. | 10.00 | Set |  | 218.25 | 2182.50 | 250.00 | 2500.00 | 200.00 | 2000.00 | 850.00 | 8500.00 | 2000.00 | JCC ENGINEERS PRIVATE LIMITED
27.30 | 3.5core X 25 Sq.mm. | 10.00 | Set |  | 218.25 | 2182.50 | 250.00 | 2500.00 | 200.00 | 2000.00 | 950.00 | 9500.00 | 2000.00 | JCC ENGINEERS PRIVATE LIMITED
27.40 | 3.5core X 50 Sq.mm. | 6.00 | Set |  | 288.00 | 1728.00 | 329.00 | 1974.00 | 300.00 | 1800.00 | 1200.00 | 7200.00 | 1728.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
27.50 | 3.5 core X 400 Sq.mm. | 8.00 | Set |  | 1056.75 | 8454.00 | 1209.00 | 9672.00 | 1000.00 | 8000.00 | 2500.00 | 20000.00 | 8000.00 | JCC ENGINEERS PRIVATE LIMITED
28.00 | Supply & Laying of following sizes HDPE pipe ISI marked conforming to IS 14930, Part-II along with all acessories like socket, bend, couplers etc complete with fitting and cutting, jointing etc direct in ground (75 cm below ground level) including excavation & refilling the trench with same excavated earth but excluding sand cushioning and protective covering etc. , complete as required.
28.10 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 150.00 | Mtr |  | 183.00 | 27450.00 | 197.00 | 29550.00 | 200.00 | 30000.00 | 850.00 | 127500.00 | 27450.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
29.00 | Supply & Laying of 150 mm (OD) / 135 mm (ID) (nominal) dia, PN8 HDPE pipe as per IS 14930 through trenchless technology by drilling the bore of suitable dia directly in ground upto the depth of 3 meters from the ground level including necessary joining, coupling, splicing etc complete as required | 2300.00 | Mtr |  | 1430.00 | 3289000.00 | 395.00 | 908500.00 | 1400.00 | 3220000.00 | 2250.00 | 5175000.00 | 908500.00 | HLK Infrastructure Pvt Ltd
30.00 | Supply and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size PVC insulated and PVC sheathed/XLPE aluminum conductor cable, etc complete as required.
30.10 | 3.5 X 400 sq. mm | 4.00 | Set |  | 5772.75 | 23091.00 | 4500.00 | 18000.00 | 6000.00 | 24000.00 | 7200.00 | 28800.00 | 18000.00 | HLK Infrastructure Pvt Ltd
31.00 | Providing an laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) etc. including form work etc. as required in excavated trench for road crossing of cable in pipe. | 3.00 | Cum |  | 6386.25 | 19158.75 | 6614.00 | 19842.00 | 7500.00 | 22500.00 | 2000.00 | 6000.00 | 6000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
32.00 | Supplying and fixing cable route marker with 10cmx10cmx 5 mm thick GI Plate with inscription thereon , bolted/ welded to 35x35x6 mm angle iron of 60 cm long and fixing the same in ground as required. | 20.00 | Each |  | 263.25 | 5265.00 | 383.00 | 7660.00 | 500.00 | 10000.00 | 450.00 | 9000.00 | 5265.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
33.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
33.10 | 150 mm width X 50 mm depth X 1.6 mm thickness | 100.00 | Mtr |  | 563.25 | 56325.00 | 610.00 | 61000.00 | 1000.00 | 100000.00 | 540.00 | 54000.00 | 54000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
33.20 | 300 mm width X 50 mm depth X 1.6 mm thickness | 25.00 | Mtr |  | 765.00 | 19125.00 | 875.00 | 21875.00 | 1200.00 | 30000.00 | 740.00 | 18500.00 | 18500.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
34.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "bends" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required.
34.10 | 150 mm width X 50 mm depth X 1.6 mm thickness | 10.00 | Each |  | 1021.50 | 10215.00 | 1168.00 | 11680.00 | 1500.00 | 15000.00 | 450.00 | 4500.00 | 4500.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
34.20 | 300 mm width X 50 mm depth X 1.6 mm thickness | 2.00 | Each |  | 1497.75 | 2995.50 | 1713.00 | 3426.00 | 1600.00 | 3200.00 | 600.00 | 1200.00 | 1200.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
35.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "Tee" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc. as required
35.10 | 150 mm width X 50 mm depth X 1.6 mm thickness | 2.00 | Each |  | 1113.75 | 2227.50 | 1274.00 | 2548.00 | 1500.00 | 3000.00 | 450.00 | 900.00 | 900.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
35.20 | 300 mm width X 50 mm depth X 1.6 mm thickness | 2.00 | Each |  | 1746.00 | 3492.00 | 1997.00 | 3994.00 | 2000.00 | 4000.00 | 600.00 | 1200.00 | 1200.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
36.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "Cross member"(galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required
36.10 | 150 mm width X 50 mm depth X 1.6 mm thickness | 1.00 | Each |  | 1110.00 | 1110.00 | 1274.00 | 1274.00 | 1500.00 | 1500.00 | 500.00 | 500.00 | 500.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
36.20 | 300 mm width X 50 mm depth X 1.6 mm thickness | 1.00 | Each |  | 1900.00 | 1900.00 | 2194.00 | 2194.00 | 2000.00 | 2000.00 | 500.00 | 500.00 | 500.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
37.00 | Galvanised Iron cable tray "Reducer" (galvanisation not less than 50 microns) with perforation not more than17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required.
37.10 | 150 mm width X 50 mm depth X 1.6 mm thickness | 2.00 | Each |  | 1554.75 | 3109.50 | 1500.00 | 3000.00 | 2000.00 | 4000.00 | 750.00 | 1500.00 | 1500.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
37.20 | 300 mm width X 50 mm depth X 1.6 mm thickness | 2.00 | Each |  | 2289.00 | 4578.00 | 2400.00 | 4800.00 | 2500.00 | 5000.00 | 750.00 | 1500.00 | 1500.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
38.00 | Supplying and fixing 6 way, polycarbonate type SPN with Acrylic door , MCB distribution board,230 V, on surface, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, including earthing etc. as required. (But without MCB/RCCB/ Isolator) | 11.00 | Each |  | 1452.00 | 15972.00 | 1450.00 | 15950.00 | 2000.00 | 22000.00 | 900.00 | 9900.00 | 9900.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
39.00 | Supplying and fixing 25 A rating, Single pole and neutral, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 11.00 | Each |  | 475.50 | 5230.50 | 1150.00 | 12650.00 | 300.00 | 3300.00 | 175.00 | 1925.00 | 1925.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
40.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/ Isolator)
40.10 | 6 way (4+18), Double door | 2.00 | Each |  | 3228.75 | 6457.50 | 3693.00 | 7386.00 | 3000.00 | 6000.00 | 2400.00 | 4800.00 | 4800.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
41.00 | Supplying and fixing 5 amps to 32 amps rating, 240 volts miniature circuite breaker suitable for lighting and other loads of following poles in the existing MCB DB complete with connection, testing and commissioning etc. as required.
41.10 | Single Pole 'C' series | 342.00 | Each |  | 174.00 | 59508.00 | 199.00 | 68058.00 | 200.00 | 68400.00 | 250.00 | 85500.00 | 59508.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
42.00 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required
42.10 | 40 Amps | 5.00 | Each |  | 727.50 | 3637.50 | 832.00 | 4160.00 | 500.00 | 2500.00 | 550.00 | 2750.00 | 2500.00 | JCC ENGINEERS PRIVATE LIMITED
42.20 | 63 Amps | 7.00 | Each |  | 733.50 | 5134.50 | 839.00 | 5873.00 | 600.00 | 4200.00 | 550.00 | 3850.00 | 3850.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
43.00 | Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps “C” curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 15.00 | Nos |  | 1077.00 | 16155.00 | 1232.00 | 18480.00 | 1200.00 | 18000.00 | 450.00 | 6750.00 | 6750.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
44.00 | Wiring for circuit/submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/recess steel conduit as reqd.
44.10 | 2 x 1.5 sq.mm. + 1 x 1.5 sq. mm. earth wire | 100.00 | Mtr |  | 181.50 | 18150.00 | 185.00 | 18500.00 | 200.00 | 20000.00 | 205.00 | 20500.00 | 18150.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
44.20 | 2 x 2.5 sq.mm. + 1 x 2.5 sq. mm. earth wire | 100.00 | Mtr |  | 200.25 | 20025.00 | 205.00 | 20500.00 | 225.00 | 22500.00 | 225.00 | 22500.00 | 20025.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
44.30 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 100.00 | Mtr |  | 230.25 | 23025.00 | 235.00 | 23500.00 | 250.00 | 25000.00 | 260.00 | 26000.00 | 23025.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
44.40 | 4 X 2.5 sq. mm + 2 X 2.5 sq. mm earth wire | 100.00 | Mtr |  | 296.25 | 29625.00 | 295.00 | 29500.00 | 300.00 | 30000.00 | 340.00 | 34000.00 | 29500.00 | HLK Infrastructure Pvt Ltd
44.50 | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | 100.00 | Mtr |  | 354.75 | 35475.00 | 340.00 | 34000.00 | 400.00 | 40000.00 | 405.00 | 40500.00 | 34000.00 | HLK Infrastructure Pvt Ltd
45.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required.
45.10 | Group C | 100.00 | Point |  | 1060.50 | 106050.00 | 1060.00 | 106000.00 | 1000.00 | 100000.00 | 966.00 | 96600.00 | 96600.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
46.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required Group C | 30.00 | Point |  | 618.00 | 18540.00 | 550.00 | 16500.00 | 600.00 | 18000.00 | 700.00 | 21000.00 | 16500.00 | HLK Infrastructure Pvt Ltd
47.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in existing surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required Group C | 50.00 | Point |  | 318.75 | 15937.50 | 550.00 | 27500.00 | 400.00 | 20000.00 | 700.00 | 35000.00 | 15937.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
48.00 | Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. | 5.00 | Point |  | 1128.00 | 5640.00 | 1150.00 | 5750.00 | 1200.00 | 6000.00 | 1200.00 | 6000.00 | 5640.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
49.00 | S/F light plug point Modular type accessories: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. | 50.00 | Each |  | 350.25 | 17512.50 | 385.00 | 19250.00 | 400.00 | 20000.00 | 401.00 | 20050.00 | 17512.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
50.00 | S/F power plug point modular type accessories: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 30.00 | Nos |  | 432.75 | 12982.50 | 450.00 | 13500.00 | 500.00 | 15000.00 | 495.00 | 14850.00 | 12982.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
51.00 | Supplying and fixing call bell(Ding-Dong) suitable for A.C. single phase, 230 volts, complete as required. | 13.00 | Nos |  | 80.25 | 1043.25 | 650.00 | 8450.00 | 100.00 | 1300.00 | 92.00 | 1196.00 | 1043.25 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
52.00 | Supplying and fixing following size/modules,GI box alongwith modular base & cover plate for modular switches in recess etc. as required
52.10 | 1 or 2 Module (75 mm X 75 mm) | 55.00 | Nos |  | 150.00 | 8250.00 | 220.00 | 12100.00 | 200.00 | 11000.00 | 240.00 | 13200.00 | 8250.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
52.20 | 6 Module (200mmX75mm) (Computer Point) | 30.00 | Nos |  | 450.00 | 13500.00 | 289.00 | 8670.00 | 300.00 | 9000.00 | 330.00 | 9900.00 | 8670.00 | HLK Infrastructure Pvt Ltd
53.00 | Supplying and fixing following modular type switch/socket on the existing switch box/cover including connections etc. as required.
53.10 | Telephone socket outlet with shutter | 25.00 | Nos |  | 104.25 | 2606.25 | 105.00 | 2625.00 | 100.00 | 2500.00 | 55.00 | 1375.00 | 1375.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
53.20 | TV antenna socket outlet | 5.00 | Nos |  | 104.25 | 521.25 | 105.00 | 525.00 | 100.00 | 500.00 | 55.00 | 275.00 | 275.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
53.30 | RJ-45 socket outlet with shutter | 25.00 | Nos |  | 357.00 | 8925.00 | 385.00 | 9625.00 | 400.00 | 10000.00 | 82.00 | 2050.00 | 2050.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
53.40 | 5/6 A switch | 60.00 | Nos |  | 74.25 | 4455.00 | 81.00 | 4860.00 | 100.00 | 6000.00 | 45.00 | 2700.00 | 2700.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
53.50 | 3 pin 5/6 A socket | 60.00 | Nos |  | 96.75 | 5805.00 | 97.00 | 5820.00 | 100.00 | 6000.00 | 55.00 | 3300.00 | 3300.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
53.60 | 15/16 A switch | 40.00 | Nos |  | 115.50 | 4620.00 | 125.00 | 5000.00 | 100.00 | 4000.00 | 110.00 | 4400.00 | 4000.00 | JCC ENGINEERS PRIVATE LIMITED
53.70 | 6 pin 15/16 amp socket outlet | 40.00 | Nos |  | 153.00 | 6120.00 | 155.00 | 6200.00 | 200.00 | 8000.00 | 125.00 | 5000.00 | 5000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
54.00 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required | 55.00 | Nos |  | 27.75 | 1526.25 | 32.00 | 1760.00 | 30.00 | 1650.00 | 8.00 | 440.00 | 440.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
55.00 | Supplying and fixing two module stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required | 5.00 | Nos |  | 299.25 | 1496.25 | 342.00 | 1710.00 | 250.00 | 1250.00 | 342.00 | 1710.00 | 1250.00 | JCC ENGINEERS PRIVATE LIMITED
56.00 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
56.10 | 3x 1.5 sq. mm | 400.00 | Mtr |  | 47.25 | 18900.00 | 51.00 | 20400.00 | 100.00 | 40000.00 | 50.00 | 20000.00 | 18900.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
56.20 | 6 x 1.5 sq. mm | 600.00 | Mtr |  | 75.00 | 45000.00 | 90.00 | 54000.00 | 120.00 | 72000.00 | 100.00 | 60000.00 | 45000.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
56.30 | 3 x 2.5 sq. mm | 400.00 | Mtr |  | 65.25 | 26100.00 | 70.00 | 28000.00 | 100.00 | 40000.00 | 75.00 | 30000.00 | 26100.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
56.40 | 6 x 2.5 sq. mm | 600.00 | Mtr |  | 106.50 | 63900.00 | 125.00 | 75000.00 | 150.00 | 90000.00 | 142.00 | 85200.00 | 63900.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
56.50 | 3 x 4 sq. mm | 500.00 | Mtr |  | 102.00 | 51000.00 | 105.00 | 52500.00 | 150.00 | 75000.00 | 115.00 | 57500.00 | 51000.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
56.60 | 6 x 4 sq. mm | 500.00 | Mtr |  | 193.50 | 96750.00 | 189.00 | 94500.00 | 225.00 | 112500.00 | 220.00 | 110000.00 | 94500.00 | HLK Infrastructure Pvt Ltd
56.70 | 3x 6 sq. mm | 100.00 | Mtr |  | 146.25 | 14625.00 | 155.00 | 15500.00 | 200.00 | 20000.00 | 165.00 | 16500.00 | 14625.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
56.80 | 6x 6 sq. mm | 100.00 | Mtr |  | 244.50 | 24450.00 | 289.00 | 28900.00 | 400.00 | 40000.00 | 320.00 | 32000.00 | 24450.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
57.00 | Providing 15mm thick cement plaster of mix 1:4 (1 cement : 4 fine sand) at all levels | 10.00 | Cum |  | 267.75 | 2677.50 | 1800.00 | 18000.00 | 300.00 | 3000.00 | 3750.00 | 37500.00 | 2677.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
58.00 | Providing brick work (in width 225 mm or more) with F.P.S. bricks of class designation 7.5 in cement mortar 1:4 (1 cement : 4 coarse sand) at all levels. | 15.00 | Cum |  | 5562.00 | 83430.00 | 6600.00 | 99000.00 | 6000.00 | 90000.00 | 5600.00 | 84000.00 | 83430.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
59.00 | Supplying and drawing co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with Al. foil & Al. braid and protected with PVC sheath in the existing surface/ recessed steel/ PVC conduit as required. | 50.00 | Mtr |  | 28.50 | 1425.00 | 33.00 | 1650.00 | 50.00 | 2500.00 | 30.00 | 1500.00 | 1425.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
60.00 | Supplying and fixing of suitable size of telephone distribution (DP) boxes made of 2 mm thick GI sheet, powder coated including krone modules with all mounting accessories including necessary termination.
60.10 | 20 Pair | 2.00 | Nos |  | 561.00 | 1122.00 | 18500.00 | 37000.00 | 1000.00 | 2000.00 | 1200.00 | 2400.00 | 1122.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
61.00 | Suppply & laying, connection, testing & commissioning of following multi core copper conductor of 0.50 mm nominal dia telephone armoured cable conforming to IS:1554(Part-1)
61.10 | 20 Pair | 125.00 | Mtr |  | 133.50 | 16687.50 | 125.00 | 15625.00 | 200.00 | 25000.00 | 45.00 | 5625.00 | 5625.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
62.00 | Supplying and drawing following pair 0.5 mm dia FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required.
62.10 | 4 Pair | 500.00 | Mtr |  | 25.50 | 12750.00 | 45.00 | 22500.00 | 30.00 | 15000.00 | 9.00 | 4500.00 | 4500.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
63.00 | Supplying and drawing of UTP 4 pair CAT 6 LAN Cable in the existing surface/ recessed Steel/ PVC conduit as required.
63.10 | 1 run of Cable | 50.00 | Mtr |  | 42.75 | 2137.50 | 45.00 | 2250.00 | 60.00 | 3000.00 | 50.00 | 2500.00 | 2137.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
63.20 | 2 run of Cable | 100.00 | Mtr |  | 72.00 | 7200.00 | 74.00 | 7400.00 | 100.00 | 10000.00 | 80.00 | 8000.00 | 7200.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
63.30 | 3 run of Cable | 100.00 | Mtr |  | 99.75 | 9975.00 | 107.00 | 10700.00 | 150.00 | 15000.00 | 100.00 | 10000.00 | 9975.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
64.00 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
64.10 | 20 mm | 200.00 | Mtr |  | 127.50 | 25500.00 | 132.00 | 26400.00 | 150.00 | 30000.00 | 50.00 | 10000.00 | 10000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
64.20 | 25 mm | 200.00 | Mtr |  | 144.00 | 28800.00 | 149.00 | 29800.00 | 200.00 | 40000.00 | 85.00 | 17000.00 | 17000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
64.30 | 32 mm | 100.00 | Mtr |  | 177.75 | 17775.00 | 183.00 | 18300.00 | 225.00 | 22500.00 | 105.00 | 10500.00 | 10500.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
65.00 | Supply of 08 meters height GI OCTAGONAL pole continuously tapered galvanised street light pole with maximum 1.5 meter long single arm GI bracket (length of bracket shall be based on design) for installation of LED street light luminaire and fabricated out of 3 mm MS plate in single section, suitable for installation on a precast foundation with supply of 4 nos. of foundation bolt & anchor plate, rigid flange plate (200x200x12mm min.) welded with the base of pole for fixing on foundation bolts complete as reqd. for structural stability as specified, weather proof and vandal resistant door flush with the exterior surface containing a terminal plate of 5 mm thick backlite sheet with 32 Amp heavy duty connector for loop in loop out cable terminations suitable for upto two numbers 4 core 06 Sq.mm cables & 0.5A DP MCB for each fixture connections, earthing bolts for continuous earth connection complete as required & as specified. | 10.00 | Nos |  | 11843.25 | 118432.50 | 22500.00 | 225000.00 | 18000.00 | 180000.00 | 17500.00 | 175000.00 | 118432.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
66.00 | Erection of metallic/OCTAGONAL pole of length 08 meter in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation including i/c making the foundation, excavation and refilling etc. as required. | 10.00 | Nos |  | 8029.50 | 80295.00 | 18500.00 | 185000.00 | 5000.00 | 50000.00 | 3000.00 | 30000.00 | 30000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
67.00 | LT Panel Design, fabrication, assembling, supply, installation, testing and commissioning of cubicle type TTA LT panels, suitable for 415 V 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentised design from CRCA sheet steel of 2 mm thick for frame work IP 42 and covers,3 mm thick for gland plates i/c cleaning and finishing complete with powder coating in approved shade, extendable type TPN aluminium alloy busbars of high condectivity, DMC/SMC busbar supports, with 2 Nos. earth studs, solid connection from main busbar to switchgears with require size of aluminium busbar & control wiring with 1.5 sqmm FRLS insulated copper conductor cable, cable alleys, cable gland plates i/c accessrories as per tender technical specifications and providing following switchgears, metering instruments etc. as detailed below; (a) INCOMER :- (i) 2 Nos. MCCB, 400A, 35 kA, Four Pole , with thermal magnetic adjustable release having adjustable over Current, adjustable Short Circuit, (Ics=Icu) along with Direct Rotary handle and spreader link. (ii) 1 nos. Digital Voltmeter of suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with suitable no. of 2 Amp. SP MCBs. (iii) 1 Set Indication Lamps, LED type, R,Y,B and breaker 'ON', 'OFF', 'TRIP' lamps each with 2 Amp. SP MCB. (iv) 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-400A), for 3 phase 4 wire operation with LED display and selector switch with 3 nubmers suitable range CTs. of class 1.0 accuracy, 15 VA burden - 1 set. (b) BUS- COUPLER (i) 1 Nos. MCCB, 400A, 35 kA, Four Pole , without thermal magnetic adjustable release having adjustable over Current, adjustable Short Circuit, (Ics=Icu) along with Direct Rotary handle and spreader link. (ii) 1 Set Indication Lamps, LED type, breaker 'ON' & 'OFF', SP MCB. (c) . Busbar:- 415 V, 500 Amps, TPN Aluminium Busbars with Heat shrinkable color coded insulation sleeves. (d) Outgoing:- (i) (i) 2Nos. of 100 Amps, 415V, 35 kA, FP MCCB with Thermal magnetic Based releases having O/C, S/C along with following (ii) 8 Nos. of 63 Amps, 415V, 35 kA, FP MCCB with Thermal magnetic Based releases having O/C, S/C along with following (iii) 8 Nos. of 40 Amps, 415V, 35 kA, FP MCCB with Thermal magnetic Based releases having O/C, S/C along with following | 1.00 | Nos |  | 576510.00 | 576510.00 | 485000.00 | 485000.00 | 500000.00 | 500000.00 | 125000.00 | 125000.00 | 125000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
68.00 | High Mast: Design, Supply, installation, testing and commissioning of 16M high mast shaft in two section suitable for 55 m/sec wind speed along with head frame, luminaires carriage suitable for 8 luminaires in symmetrical arrangement and other accessories manufactured in factory with the following accessories etc, as required as per the additional specification. (i) Raising lowering system comprising double drum winch, 6mm diameter SS wire rope, trailing cable, connector, integral power tool motor, manual handle, junction box, lightning finial. (Wiring material from JB to individual lumi (ii) Foundation bolts manufactured from special steel along with nuts, washers, anchor plate and common template including RCC/CC foundation as recommended by the OEM for installation of above high mast. (iii) Supply & installation of 08 nos. 200W LED Flood Light having Lumen output minimum 24000 Lumens, IP 66, IK08 (iv) Supply & Installation of LED type single dome aviation obstruction light. (v) SITC of outdoor stand mounted feeder pillar with 32A TPN MCB incomer, single dial time switch, 25A TP contactor for the automatic switching of luminaries, power tool control with 2 no 9A contactors and raise lower push button, Incoming 35 sq. mm and out going 16 & 2.5 sq. mm terminals. | 1.00 | Job |  | 304984.50 | 304984.50 | 185000.00 | 185000.00 | 300000.00 | 300000.00 | 485000.00 | 485000.00 | 185000.00 | HLK Infrastructure Pvt Ltd
69.00 | SH-II: EARTHING, LIGHTINING ARRESTER & SURGE PROTECTION
70.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 8.00 | Set |  | 3525.75 | 28206.00 | 5308.00 | 42464.00 | 6000.00 | 48000.00 | 4200.00 | 33600.00 | 28206.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
71.00 | Supplying and laying 6 SWG G.I. wire at 0.50 meter below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | 50.00 | Mtr |  | 38.25 | 1912.50 | 44.00 | 2200.00 | 50.00 | 2500.00 | 22.00 | 1100.00 | 1100.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
72.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 meter below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50 mm) | 50.00 | Mtr |  | 114.75 | 5737.50 | 131.00 | 6550.00 | 150.00 | 7500.00 | 60.00 | 3000.00 | 3000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
73.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required | 40.00 | Mtr |  | 422.25 | 16890.00 | 483.00 | 19320.00 | 500.00 | 20000.00 | 60.00 | 2400.00 | 2400.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
74.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required | 50.00 | Mtr |  | 180.00 | 9000.00 | 206.00 | 10300.00 | 200.00 | 10000.00 | 60.00 | 3000.00 | 3000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
75.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required | 200.00 | Mtr |  | 49.50 | 9900.00 | 57.00 | 11400.00 | 50.00 | 10000.00 | 60.00 | 12000.00 | 9900.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
76.00 | Supply & Installation of 8mm Aluminum Solid Round Conductor to make horizontal air terminal at terrace, grid size shall be as per drawing to meet the requirements for IS/IEC 62305 and IEC 62561-2. Conductor should be tested for its Electrical, Mechanical and Chemical properties as per IEC 62561. test certificate should be provided by the manufacturer. | 250.00 | Mtr |  | 192.75 | 48187.50 | 150.00 | 37500.00 | 250.00 | 62500.00 | 75.00 | 18750.00 | 18750.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
77.00 | Supply & Installation of aluminium ferrule for extension of 8 mm solid aluminium conductors . | 15.00 | Nos |  | 116.25 | 1743.75 | 450.00 | 6750.00 | 150.00 | 2250.00 | 45.00 | 675.00 | 675.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
78.00 | Supply & Installation of stainless steel holder at every one metre for roof and wall (sheer area)suitable 8 / 10 mm round conductor for Metal Roof sheet components are meet the requirements for IS/IEC 62305 and should be tested for its Electrical, Mechanical and Chemical properties as per IEC 62561. test certificate shold be provided by the manufacturer. | 250.00 | Nos |  | 330.75 | 82687.50 | 75.00 | 18750.00 | 400.00 | 100000.00 | 65.00 | 16250.00 | 16250.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
79.00 | Supply & Installation of heavy duty adhensive glue to stainless steel roof conductor holder on Metal Roof sheet for horizontal Air terminal. | 2.00 | bottle |  | 4919.25 | 9838.50 | 1550.00 | 3100.00 | 6000.00 | 12000.00 | 870.00 | 1740.00 | 1740.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
80.00 | Supply & Installation of Stainless steel cross connector suitable for 8 / 10 mm round conductor ,components meet the requirements for IS/IEC 62305 and should be tested for its Electrical,Mechanical and Chemical properties as per IEC 62561. test certificate shold be provided by the manufacturer. | 50.00 | Each |  | 602.25 | 30112.50 | 250.00 | 12500.00 | 700.00 | 35000.00 | 245.00 | 12250.00 | 12250.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
81.00 | Supply & Installation of Expansion Piece with ferrule to compensate the expansion and contraction of Solid Round Al. Conductor during temperature variations, to be provided on conductors length over 20 meters or as per drawing, components are to meet the requirements for IS/IEC 62305.Tested for its Electrical, Mechanical and Chemical properties as per IEC 62561. | 20.00 | Nos |  | 492.00 | 9840.00 | 350.00 | 7000.00 | 600.00 | 12000.00 | 1870.00 | 37400.00 | 7000.00 | HLK Infrastructure Pvt Ltd
82.00 | Supply & Installation of bridging cable to connect horizontal air terminal to connect with the metal column all components are to meet the requirements for IS/IEC 62305.Tested for its Electrical, Mechanical and Chemical properties as per IEC 62561. | 20.00 | Nos |  | 891.00 | 17820.00 | 1550.00 | 31000.00 | 1000.00 | 20000.00 | 2250.00 | 45000.00 | 17820.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
83.00 | Supply & Installation of Stainless steel Conductor Holder for holding the down conductor on the bricks wall at every one metre, meet the requirements of IS/IEC 62305.Tested for its Electrical,Mechanical and Chemical properties as per IEC 62561. | 20.00 | Nos |  | 282.00 | 5640.00 | 250.00 | 5000.00 | 350.00 | 7000.00 | 2500.00 | 50000.00 | 5000.00 | HLK Infrastructure Pvt Ltd
84.00 | Supply & Installation of Lightnig counter - LCD screen shows the number of lightning strikes, hour and date of lightning events Buttons enable TIME/DATE setting and log viewing. Replaceable battery, working life minimum five years, meet the requirements for IS/IEC 62305 and IEC 62561-2.Tested for Electrical ,Mechanical and Chemical as per IEC 62561. | 1.00 | Nos |  | 30512.25 | 30512.25 | 45000.00 | 45000.00 | 35000.00 | 35000.00 | 35000.00 | 35000.00 | 30512.25 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
85.00 | Supply & Installation of 10mm copper bonded steel solid conductor for ring Earthing, all down conductor shall connected with Ring earthing , Conductor should be minim 100 micron copper bonded and CPRI Tested for short circuit current min 12 kA peak. Conductor shall be horizontal laid in soil at min. 600mm below ground level and 1 metre distance from the building wall, components should tomeet the requirements of IS/ IEC 62305 and IEC 62561-2 | 80.00 | Mtr |  | 626.25 | 50100.00 | 1250.00 | 100000.00 | 850.00 | 68000.00 | 210.00 | 16800.00 | 16800.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
86.00 | Supply & Installation of UL listed maintenance free copper coated earth rod with 250 micron copper coating with clamp made of stainless steel for terminating cable / flat conductor. PP material inspection pit which can handle 5 kN point load. Earth enhancing mineral (PROSAN) compound tested for Leaching & TCLP with NABL accredited lab. The systems shall be conforming to IS 3043, IS / IEC 62305, IEC 61643-5-54, UL 467 and the rod tested for dimention, marking, tensile strength, salt mist, coating thickness, electrical resistivity test before and after corresion test etc as per IEC 62561-2. Set Consist of following BOM (1) Earth rod of 3 mtr length having the dia of 14.2 mm (2) 12.5 Kg bag x 2 nos (3) Universal Clamp SS (4) Chamber Inspection Pit) made up of PP material. | 14.00 | Set |  | 12525.75 | 175360.50 | 18500.00 | 259000.00 | 15000.00 | 210000.00 | 20000.00 | 280000.00 | 175360.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
87.00 | Supply & installation of Testing & commissioning of Type 1 SPD according to EN 61643-11, Lightning current & Surge Protection Device at mains LT panel (3 phase, 415 V) for (LN) Single-pole combined lightning current and surge arrester with Follow current extinguishing capability: up to 100 kArms;Energy-coordinated according to IEC 62305-4 with arresters of the Red/Line series and terminal equipment,Temporary overvoltage (TOV) 440 V /120 min. withstand, remot signalling P/N: 961205. and Type 1 SPD according to EN 61643-11, Lightning current & Surge Protection Device at mains LT panel (3 phase, 415 V) for (NPE) Single-pole combined lightning current arrester, Lightning impulse current (10/350): 100 kA;Follow current extinguishing capability: 100 Arms at 255 V a.c.,TOV resistance: 1200 V/200 ms; with remote signalling with MCB 4 Pole 63 amp Heavy duty transparient enclosure IP-67. and KEMA Approved P/N:961185 Make Dehn. | 1.00 | Set |  | 66243.75 | 66243.75 | 85000.00 | 85000.00 | 75000.00 | 75000.00 | 15000.00 | 15000.00 | 15000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
88.00 | Supply, Installation, testing and commissioning of 240 kA 3 phase 4 wire Digital Portable Low Impedance equipment Grounding & bonding system with built in 100% Lightning and Surges suppressor, static charge, Noises, ESD, EPR and abnormal electrical characteristics eliminator which enter from power and other service lines and ensuring clear bonding potential (earth to Neutral voltage) less than 1.0V, a digital 6 digit lightening surge counter, self health visual status indicator, built in Aerosol based fire Extinguisher and ON-LINE remote monitoring facility of Earth-Neutral voltage in a Pre-wired pulverulent body painted metal enclosure to be connected in parallel to the power supply circuit, Conforming to IEC , CE Marked, CPRI tested & ISO 9000 & ISO 14001-2015 certified. Make in India, Model: DSP-Prime-MII-3P4-240 | 1.00 | Job |  | 194775.00 | 194775.00 | 95000.00 | 95000.00 | 200000.00 | 200000.00 | 15000.00 | 15000.00 | 15000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
89.00 | Supply & Installation of Self actuated (thermaly & Electrically non pressurized, Strong & Light weight, impulse dry power Module suitable for extinguish A,B,C & E type of fire for the protection of 15 cu. mtrs volume Model : Buran 2.5 of EPTOS or equivalent of FCDT SOYUZ/Pyrogen to be installed in Switch room | 1.00 | Job |  | 18682.50 | 18682.50 | 185000.00 | 185000.00 | 20000.00 | 20000.00 | 12000.00 | 12000.00 | 12000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
90.00 | Supply & Installation of Thermal Activation Device (TAD) Model USP 101 or equivalent | 1.00 | Job |  | 10891.50 | 10891.50 | 150000.00 | 150000.00 | 12000.00 | 12000.00 | 8760.00 | 8760.00 | 8760.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
91.00 | Supply of Self Operated Aerosol based fire Extinguisher for the protection of 0.1 cubic mtrs of enclosed space using 8 gms. of Aerosol Model :Tor-02A of EPOTOS or equivalent of FCDT SOYUZ /Pyrogen | 16.00 | Each |  | 3418.50 | 54696.00 | 25000.00 | 400000.00 | 4000.00 | 64000.00 | 3800.00 | 60800.00 | 54696.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
92.00 | SH-III: FIRE FIGHTING & HYDRANT SYSTEM
93.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required :
93.10 | 25 mm dia. | 100.00 | RM |  | 385.50 | 38550.00 | 604.00 | 60400.00 | 433.00 | 43300.00 | 450.00 | 45000.00 | 38550.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
93.20 | 80 mm dia. | 150.00 | RM |  | 783.00 | 117450.00 | 1086.00 | 162900.00 | 1000.00 | 150000.00 | 1527.00 | 229050.00 | 117450.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
93.30 | 100 mm dia. | 350.00 | RM |  | 945.75 | 331012.50 | 1707.00 | 597450.00 | 1300.00 | 455000.00 | 1910.00 | 668500.00 | 331012.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
93.40 | 150 mm dia. | 25.00 | RM |  | 1725.00 | 43125.00 | 2432.00 | 60800.00 | 1900.00 | 47500.00 | 2789.00 | 69725.00 | 43125.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
94.00 | Providing laying, testing & commissioning of 'C' class heavy duty MS Pipe conforming to IS 1239/3589 i/c fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. in ground including welding, excavation & providing cement concrete blocks as supports, anticorrosive treatment with coaltar/asphalt tape as per IS 10221, refilling the trench etc. of following sizes complete as required.
94.10 | 150 mm dia. | 250.00 | RM |  | 1902.00 | 475500.00 | 2188.00 | 547000.00 | 2300.00 | 575000.00 | 3679.00 | 919750.00 | 475500.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
95.00 | Supplying, fixing, testing and commissioning of butterfly valve of PN1.6 rating with bronze / gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required :
95.10 | 80 mm dia | 2.00 | Set |  | 2552.25 | 5104.50 | 5233.00 | 10466.00 | 5000.00 | 10000.00 | 8852.00 | 17704.00 | 5104.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
95.20 | 150 mm dia | 3.00 | Set |  | 3776.25 | 11328.75 | 8699.00 | 26097.00 | 8000.00 | 24000.00 | 14765.00 | 44295.00 | 11328.75 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
96.00 | Providing and fixing ball valve (brass) of approved quality, High or low pressure, with plastic floats complete :
96.10 | 25 mm nominal bore | 2.00 | Each |  | 755.25 | 1510.50 | 10500.00 | 21000.00 | 400.00 | 800.00 | 2230.00 | 4460.00 | 800.00 | JCC ENGINEERS PRIVATE LIMITED
97.00 | Providing and fixing in position the industrial type pressure gauges with gun metal / brass valves complete as required. | 1.00 | Nos |  | 620.25 | 620.25 | 2357.50 | 2357.50 | 1000.00 | 1000.00 | 1200.00 | 1200.00 | 620.25 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
98.00 | Providing & fixing of pressure switch in M.S. pipe line including connection etc. as required. | 3.00 | Nos |  | 1318.50 | 3955.50 | 2932.50 | 8797.50 | 1500.00 | 4500.00 | 3870.00 | 11610.00 | 3955.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
99.00 | Providing & fixing flow switch in following sizes M.S. pipe including connection etc as required. a) 100 mm dia | 1.00 | Nos |  | 6436.50 | 6436.50 | 7475.00 | 7475.00 | 6000.00 | 6000.00 | 5590.00 | 5590.00 | 5590.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
100.00 | Providing and fixing gunmetal single acting air release valve with screwed inlet 25 mm dia.. | 1.00 | Nos |  | 1154.25 | 1154.25 | 2587.50 | 2587.50 | 1500.00 | 1500.00 | 850.00 | 850.00 | 850.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
101.00 | Providing, installation, testing and commissioning of non-return valve of following sizes confirming to IS: 5312 complete with rubber gasket, GI bolts, nuts, washers etc.as required :
101.10 | 80 mm dia | 1.00 | Set |  | 2508.00 | 2508.00 | 5232.50 | 5232.50 | 3000.00 | 3000.00 | 31760.00 | 31760.00 | 2508.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
101.20 | 150 mm dia | 1.00 | Set |  | 4301.25 | 4301.25 | 8200.00 | 8200.00 | 5000.00 | 5000.00 | 52875.00 | 52875.00 | 4301.25 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
103.00 | Supplying and fixing air vessel made of 250 mm dia, 8 mm thick MS sheet, 1200 mm in height with air release valve on top and flanged connection to riser, drain arrangement with 25 mm dia gun metal wheel valve with required accessories, pressure gauge and painting with synthetic enamel paint of approved shade as required. | 1.00 | Set |  | 13117.50 | 13117.50 | 24500.00 | 24500.00 | 15000.00 | 15000.00 | 30348.00 | 30348.00 | 13117.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
104.00 | Supplying, laying/ fixing, testing and commissioning of following thickness resin bonded fiber glass pipe section insulation having density 80 kg/cum or mineral wool (non combustible) having density of 144 Kg/ cu m duly covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) on existing pipe and finally applying 0.63mm aluminium sheet cladding complete with type3 , grade 1 roofing feltstrip(as per IS:1322 as amended up to date ) at joints etc. as per specifications and as required.
104.10 | 25 mm | 10.00 | Sq. mm |  | 3577.50 | 35775.00 | 4100.00 | 41000.00 | 4500.00 | 45000.00 | 950.00 | 9500.00 | 9500.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
105.00 | Supplying and fixing single headed internal hydrant valve with instantaneous Gunmetal coupling of 63 mm dia with cast iron wheel ISI marked conforming to IS 5290 (Type -A) with blank Gunmetal/Stainless Steel cap and chain as required :
105.10 | Single headed Gunmetal | 8.00 | Set |  | 5049.75 | 40398.00 | 7800.00 | 62400.00 | 7000.00 | 56000.00 | 8230.00 | 65840.00 | 40398.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
106.00 | Supplying and fixing Single headed external yard hydrant valve with 1 No. 63 mm dia instantaneous FM Gunmetal coupling and cast iron wheel, ISI marked, conforming to IS 5290 (type A) with blank Gunmetal/Stainless Steel cap and chain as required :
106.10 | Single headed Gunmetal | 4.00 | Set |  | 5049.75 | 20199.00 | 9500.00 | 38000.00 | 7000.00 | 28000.00 | 7578.00 | 30312.00 | 20199.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
107.00 | Supplying and fixing first-aid Hose Reel with MS construction spray painted in post office red, conforming to IS 884 complete with the following as required. 20 mm nominal internal dia water hose thermoplastic (Textile reinforced) type -2 as per IS: 12585 20 mm nominal internal dia gun metal globe valve & nozzle. Drum and brackets for fixing the equipmets on wall. Connections from riser with 25 mm dia stop gun metal valve & M.S. Pipe and socket.
107.10 | 30 m | 4.00 | Set |  | 7355.25 | 29421.00 | 9500.00 | 38000.00 | 10000.00 | 40000.00 | 12739.00 | 50956.00 | 29421.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
108.00 | Supplying and fixing of 63 mm dia, 15 m long RRL hose pipe with 63 mm dia male and female couplings duly bound with GI wire, rivets etc. conforming to IS 636 (type-A) as required :
108.10 | Gun Metal | 16.00 | Set |  | 3486.00 | 55776.00 | 4560.00 | 72960.00 | 4000.00 | 64000.00 | 4990.00 | 79840.00 | 55776.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
109.00 | Supplying & fixing 63 mm dia gun metal short branch pipe with 20 mm nominal internal diameter size nozzle conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling as required :
109.10 | Gun Metal | 8.00 | Set |  | 1788.75 | 14310.00 | 2150.00 | 17200.00 | 2500.00 | 20000.00 | 3500.00 | 28000.00 | 14310.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
110.00 | Supplying and fixing of fire brigade connection of cast iron body with gun metal male instantaneous inlet couplings complete with cap and chain as reqd. for suitable dia MS pipe connection conforming to IS 904 as required 4 way - 150 mm dia M.S. Pipe | 1.00 | Each |  | 7830.75 | 7830.75 | 12500.00 | 12500.00 | 10000.00 | 10000.00 | 15423.00 | 15423.00 | 7830.75 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
111.00 | Supplying and fixing of Fire Hose Cabinet (External) 900mm x 600 mm x 500 mm made of 2mm thick MS sheet with 6 mm thick glazed glass doors i/c necessary locking arrangements suitable to accommodate external yard hydrant with butterfly valve, 2Nos. 15mtr.long Hose pipe, 1No. branch pipe, mounted on wall OR raised brick platform & duly painted with post office red externally and white internally with synthetic enamel paint complete in all respect, for external hydrant, as required. | 4.00 | Nos |  | 5847.75 | 23391.00 | 11500.00 | 46000.00 | 7000.00 | 28000.00 | 8800.00 | 35200.00 | 23391.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
112.00 | Providing and fixing Fire Hose Cabinet (Internal) fabricated from 16 gauge M.S. Sheet with single or double glazed front door and locking arrangement, painted "Fire Red" with powder coated paint "Fire Hose" written on front including suitable supports to place 900 mm above ground level, approximately size (minimum) 1200x900x450 mm deep, suitable to house following; (i) Single Headed Outlet - 2Nos. (ii) First Aid Hose Reel (Length of pipe shall be such that nozzle of the hose can be taken into every room and within 6 Mtrs. of any part of the rooms keeping in view layout and obstruction.) - 1 No. (iii) Hose pipe 63 mm dia 15m long with male and female coupling at both ends. - 2 Nos. (iv) Branch pipe 63 mm dia with 20 mm (nominal internal diameter) nozzle and suitable for instantaneous connection - 1 No | 4.00 | Nos |  | 7155.00 | 28620.00 | 25000.00 | 100000.00 | 9000.00 | 36000.00 | 12500.00 | 50000.00 | 28620.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
113.00 | Supplying and fixing orifice plate made out of 6 mm thick stainless steel (Grade 304) with orifice of required size to be fitted between flange & landing valve of external and internal hydrants to reduce pressure at the outlet to the level of 3.5 kg/cm2 complete as required | 4.00 | Each |  | 779.25 | 3117.00 | 1291.00 | 5164.00 | 1000.00 | 4000.00 | 2900.00 | 11600.00 | 3117.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
114.00 | Providing, installation, testing and commissioning of stainless steel Y-strainer fabricated out of 1.6 mm thick stainless steel, Grade 304, sheet with 3 mm dia holes with stainless steel flange.
114.10 | 150 mm dia. | 1.00 | Each |  | 6996.00 | 6996.00 | 10925.00 | 10925.00 | 9000.00 | 9000.00 | 24500.00 | 24500.00 | 6996.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
115.00 | Providing, fixing, testing & commissioning of 15mm dia quartzoid bulb type sprinklers of rating 68 degree centigrade with required accessories :
115.10 | Pendent Sprinkler | 60.00 | Nos |  | 250.50 | 15030.00 | 546.25 | 32775.00 | 300.00 | 18000.00 | 320.00 | 19200.00 | 15030.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
116.00 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes complete as required
116.10 | 1000mm long | 20.00 | Each |  | 781.50 | 15630.00 | 2127.50 | 42550.00 | 1000.00 | 20000.00 | 570.00 | 11400.00 | 11400.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
117.00 | Electric driven Main Fire Pump: Supplying, installation, testing and commissioning of Electric driven Main Fire Pump suitable for automatic operation and consisting of following, complete in all respects, as required : Horizontal type, multistage, centrifugal, split casing pump of cast iron body & bronze impeller with stainless steel shaft, mechanical seal conforming to IS 1520. Suitable HP Squirrel cage induction motor, TEFC, synchronous speed 1500 RPM, suitable for operation on 415 volts, 3 phase 50 Hz, AC supply with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS-325. M.S. fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required. Suitable cement concrete foundation duly plastered with anti vibration pads. 2280 lpm at 56 m Head Note: *The head of the pump is selected in a manner so as to give a minimum 3.5kgf/cm 2 pressure at the highest/farthest point. | 1.00 | Set |  | 187509.00 | 187509.00 | 259325.00 | 259325.00 | 300000.00 | 300000.00 | 510000.00 | 510000.00 | 187509.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
118.00 | Diesel Driven Pump: Supplying, installation, testing and commissioning of diesel engine driven main fire pump suitable for automatic operation and consisting of following, complete in all respects, as required : Horizontal type, multistage, centrifugal pump of cast of iron body and bronze impeller with stainless steel shaft, mechanical seal conforming to IS 1520. Suitable HP, 1500 RPM water cooled with radiator, diesel engine conforming to relevant IS standard complete with auto starting mechanism, 12 /24 volts electric starting equipment, diesel tank, exhaust pipe extended upto 10 m outside pump house duly insulated with 50 mm thick glass wool with 1.0 mm thick aluminium sheet cladding, residential silencer, instruments and protection as per standard specification, stop solenoid for auto stop in the event of fault with audio indications, painted with post office red colour etc. as required. M.S fabricated, common base plate, coupling, coupling guard, foundation bolts etc. as required. Suitable cement concrete foundation duly plastered and with anti vibration pads. 2280 lpm at 56 m Head Note: *The head of the pump is selected in a manner so as to give a minimum 3.5kgf/cm 2 pressure at the highest/farthest point. | 1.00 | Set |  | 385861.50 | 385861.50 | 485000.00 | 485000.00 | 500000.00 | 500000.00 | 650000.00 | 650000.00 | 385861.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
119.00 | Jockey Pump: Supplying, installation, testing and commissioning of electric driven pressurisation pump suitable for automatic operation and consisting of following, complete in all respects, as required : Horizontal type, multistage, centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal conforming to IS : 1520. Suitable HP squirell cage induction motor TEFC type suitable for operation on 415 volts, 3 phase 50 Hz AC supply with IP 55 class of protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS : 325. M.S.fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required. Suitable cement concrete foundation duly plastered and with anti vibration pads. 180 lpm at 56 m Head | 1.00 | Set |  | 91584.00 | 91584.00 | 109825.00 | 109825.00 | 75000.00 | 75000.00 | 152786.00 | 152786.00 | 75000.00 | JCC ENGINEERS PRIVATE LIMITED
120.00 | Fabrication, supply, Insallation testing & commissioning of Electrical control panel of cubical construction, floor mounted type, fabricated out of 2mm thick CRCA sheet, compartmentalised with hinged lockable doors, dust and vermin proof, powder coated of approved shade after 7 tank treatment process, cable alley, interconnection with suitable size copper conductor cable/solid copper strip, having switchgears and accessories, mountings and internal wiring, earth terminals, numbering etc. complete in all respect, suitable for main fire pump, pressurisation pump & diesel pump set complete as per CPWD specification with following in coming and Outgoings, suitable for operation on 415V, 3 phase, 50Hz Ac Supply with enclosure protection class IP 42 as required : INCOMING 250A, 50kA 4 Pole MCCB, Ics=100% Icu rating Digital Voltmeter 0-500V with selector switch Digital Ammeter (0-250 A) with selector swtich & CTs etc. LED type RYB phase indicating lamps, ON, OFF, trip indicating lamps Bus Bar: Set of Copper Bus Bar 300A OUTGOING ( Note : All outgoing feeders for pumps should have digital Ammeter with selector switches, and LED type ON, OFF, trip indicating lamps) Main Fire Pump 125 A, 50kA TPN MCCB, Ics=100% Icu, with fully automatic Star/Delta starter suitable for 60 HP pump with overload protection, current sensing type single phase preventor complete with all acceessories and internal wiring required for automatic operation, selector switch for local/remote, auto/manual/OFF operation. | 1.00 | Set |  | 123066.00 | 123066.00 | 259325.00 | 259325.00 | 150000.00 | 150000.00 | 500000.00 | 500000.00 | 123066.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
120.10 | Jockey Pump 63 A, 50kA TPN MCCB, Ics=100% Icu, with suitable HP fully automatic Star/Delta starter with overload protection, current sensing type single phase preventor complete with all acceessories and internal wiring required for automatic operation, selector switch for local/remote, auto/manual/OFF operation.
120.20 | DIESEL ENGINE CONTROL Control for diesel engine comprising Automatic/Manual selctor switch & 3 attempts starting device, timers and relays as required, push buttons, start/stop in manual mode Indicating lamp for high/ Low Lub. Oil pressure, High Water Temp and Engine on indication Battery charger suitbale for 12V/24 V DC with boost and trickle selector switch, 0-30 V DC volt meter, and 020 A DC Ammeter All standard relays and accessories for automatic operation of diesel engine. System Controller Designing, Supply, Installation, Testing and commissioning of system controller to control operation of main electric fire pump, diesel pump, Pressurization pump, Terrace pump in sequence as per specification consisting of relays, timers. Sensors, annunciation window for fault indication, complete as per specification.
121.00 | Supply, installation, testing and commissioning ISI marked (IS:15683) Fire Extinguisher, Carbon-di-oxide type capacity 4.5 Kg. Flat base including valve, discharge hose of not less than 10 mm dia, 1M long and complete in all respects including initial fill with CO2 gas conforming to IS:307-1966 and walll suspension braket complete as required & as per specifications. | 5.00 | Nos |  | 6837.00 | 34185.00 | 9890.00 | 49450.00 | 9000.00 | 45000.00 | 11900.00 | 59500.00 | 34185.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
122.00 | Supply, installation, testing and commissioning ISI marked (IS:15683) portable fire extinguisher, water (gas pressure) type capacity 9 kg with gun metal cap and nozzle and complete in all respects including initial fill and wall suspension brackets complete as required & as per specifications. | 4.00 | Nos |  | 2757.00 | 11028.00 | 9200.00 | 36800.00 | 3000.00 | 12000.00 | 4500.00 | 18000.00 | 11028.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
123.00 | Supply, installation, testing and commissioning of 6kg ABC (Powder Type) Fire Extinguisher, Mild Steel Cylinders ISI marked fitted with pressure indicating gauge, internal tube, squeeze lever type valve fully charged with ABC 90 powder (Mono Ammonium Phosphate) pressured by Nitrogen complete in all respects including wall suspension bracket complete and conforming to IS:15683 as required and as per specifications | 5.00 | Nos |  | 2611.50 | 13057.50 | 5439.50 | 27197.50 | 3000.00 | 15000.00 | 3650.00 | 18250.00 | 13057.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
124.00 | Providing & fixing a set of 4 Nos. 9.5 Liter capacity GI bucket painted in post office red colour and written with white paint 'Fire' and mounted on MS angle iron frame with bracket of appropriate size and capacity including filling sand complete as required. | 4.00 | Job |  | 3378.75 | 13515.00 | 747.50 | 2990.00 | 4000.00 | 16000.00 | 1800.00 | 7200.00 | 2990.00 | HLK Infrastructure Pvt Ltd
125.00 | SH-IV: FIRE ALARM AND DETECTION SYSTEM
126.00 | Supply, Installation, Testing & Commissioning of Networkable Microprocessor based intelligent analog Addressable Type Fire Alarm Control Panel of 2 loop Expandable upto 6 Loop, with minimum 320 character graphics / 15000 Pixel / LCD / LED display with touch screen or other keypad and minimum 1000 events history log in the non volatile memory (EPROM) ,The panel should be equiped with loop capacity to take minimum 240 intelligent addressable detectors/ devices (In any combination ) in one loop. Four access levels, capable of taking Protocol Devices, Graphical Display, sufficient number of programmable relay controls for controlling pressurization fans, ventilation fans, fire pump room, monitoring of fire sprinkler and fire hydrant pump etc, suitable for operation at 230 volts, 50 Hz AC power supply including automatic battery charger, 24 volts sealed maintenance free lead acid batteries sufficient for 2 hours normal working and shall be capable of operating the system for 30 minutes during an emergency / fault conditions in addition as required. The panel shall be UL/EN listed (Latest Version). It shall have facility to interfac (BACNET/ MODBUS/ Open protocol gateway) with Building Management System complete as required. | 1.00 | Each |  | 147075.00 | 147075.00 | 320000.00 | 320000.00 | 150000.00 | 150000.00 | 920508.00 | 920508.00 | 147075.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
127.00 | Supply, Installation, Testing & commissioning of UL/EN listed (latest version) intelligent addressable multi criteria detector {Smoke + heat } with inbuilt fault isolator / isolator base / Isolator Module and with unique optical sensing chamber, visible LED, fully coated circuit board, complete with plug into common separate base & housing constructed of LEXAN (or polycarbonate) complete with connections etc. as required and to be installed below / above false ceiling, roof and concealed space and as per enclosed specifications. (Cost of plug in common base/box shall deemed to be included in cost of detectors) | 50.00 | Each |  | 2305.50 | 115275.00 | 4550.00 | 227500.00 | 3000.00 | 150000.00 | 3150.00 | 157500.00 | 115275.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
128.00 | Supply, Installation, Testing & commissioning of UL/EN listed (latest version) intelligent addressable Intrinsically Safe Smoke Detector with Protocol converter, barrier and all other accessories for hazardous storage area with visible LED, fully coated circuit board, complete with plug into common separate base & housing constructed of LEXAN (or polycarbonate) complete with connections etc. as required and to be installed below / above false ceiling, roof and concealed space and as per enclosed specifications. (Cost of plug in common base/box shall deemed to be included in cost of detectors) | 5.00 | Each |  | 27825.00 | 139125.00 | 4025.00 | 20125.00 | 30000.00 | 150000.00 | 2990.00 | 14950.00 | 14950.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
129.00 | Supply, installation, testing and commissioning of UL/EN listed (Latest Version) intelligent Addressable type Heat Detector (Fixed cum-rate of rise type) with inbuilt fault isolator / isolator base / Isolator Module w ith range upto 57° C complete with all fixing accessories like base, base box, self adhesive sticker indicating loop number and address etc. to be installed below / above false ceiling, roof and concealed space, etc. interconnecting to loop cable complete as required. | 10.00 | Each |  | 2146.50 | 21465.00 | 8165.00 | 81650.00 | 2500.00 | 25000.00 | 2680.00 | 26800.00 | 21465.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
130.00 | Supply, installation, testing and commissioning of UL/EN listed (latest version) Intelligent addressable Control Module/ Relay Module (output module) with inbuilt fault isolator or isolator module for tripping of AHU & Ventilation / pressurisation fans / hooter complete with termination etc. as required and as per enclosed specifications. | 2.00 | Each |  | 2782.50 | 5565.00 | 4427.00 | 8854.00 | 3500.00 | 7000.00 | 3400.00 | 6800.00 | 5565.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
131.00 | Supply, installation, testing and commissioning of Response Indicator for getting fire indications of detectors installed above false ceiling area interconnecting to loop cable complete as required. | 5.00 | Each |  | 556.50 | 2782.50 | 250.00 | 1250.00 | 700.00 | 3500.00 | 145.00 | 725.00 | 725.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
132.00 | Supply, Installation, Testing & commissioning of UL/EN listed (latest version) intelligent addressable Manual call station (pull/Push type) suitable for semi flush mounting with inbuilt fault isolator / isolator module with double gang outlet box, equipment for key operated test-reset lock, electronic or rotary switches for address setting. Manual pull station shall be connected with two wire to SLC loop of Fire Control Panel. Cover shall be made out of LEXAN (or poly carbonate) with clear operating instruction and the word "FIRE" appearing on the front complete with connections etc. as required and as per enclosed specifications. | 10.00 | Each |  | 2464.50 | 24645.00 | 9660.00 | 96600.00 | 3000.00 | 30000.00 | 3601.00 | 36010.00 | 24645.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
133.00 | Supply, installation, testing and commissioning of UL/EN listed (latest version) loop powered addressable Hooter- cum- strobe with inbuilt fault isolator / isolator module with minimum 90 dB output at a distance of 1 mtr. complete with termination etc. as required and as per enclosed specification. | 5.00 | Each |  | 4134.00 | 20670.00 | 10753.00 | 53765.00 | 5000.00 | 25000.00 | 5600.00 | 28000.00 | 20670.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
134.00 | Providing, installation, testing & commissioning of UL/EN listed (Latest Version) Monitor Module with inbuilt fault isolator / isolator module (for monitoring different electrical/mechanical device etc) as per specifications. | 5.00 | Each |  | 2782.50 | 13912.50 | 4887.50 | 24437.50 | 3000.00 | 15000.00 | 2879.00 | 14395.00 | 13912.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
135.00 | Supply and laying of 2C x 1.5 sq. mm, PVC insulated FRLS Armoured copper cable for SLC Loop & Power Supply, confirming to standards and specifications including terminations, connections & all labour and material etc. complete as required (For fire detection signal). | 820.00 | Mtr |  | 119.25 | 97785.00 | 135.00 | 110700.00 | 150.00 | 123000.00 | 339.00 | 277980.00 | 97785.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
136.00 | Supply, installation testing and commissioning of UL Listed/ EN54 listed, Vds approved beam detectors refelection type with soft addressable intelligent monitor module including powe supply unit & other accessorie complete as required as per specification. | 2.00 | Each |  | 49290.00 | 98580.00 | 42953.00 | 85906.00 | 5000.00 | 10000.00 | 8500.00 | 17000.00 | 10000.00 | JCC ENGINEERS PRIVATE LIMITED
137.00 | SH-V: VRF SYSTEM & High Wall Split Acs
138.00 | Supply Installation, Testing & Commissioning of 22 Hp (Heating & Cooling) modular type Variable Refrigerant Flow/Variable Refrigerant Volume air cooled Outdoor units suitable for cooling and heating, having all hermetically sealed inverter type Scroll Compressor(s), microprocessor based Controller, top discharge type condensing unit(s), with R 410 A Refrigerant, vibration isolators, with suitable foundation etc. complete as required. The unit shall deliver the rated capacity at AHRI Conditions and work even at 50°C ambient temperature without tripping. The unit shall be suitable to work on 400V +/- 10%, 3 Phase, 50Hz AC power supply. The unit shall be filled with first charge of the refrigerant and ready for use as required. The COP at AHRI conditions shall not be less than 3.1 and IEER not less than 6.5. (Make: Toshiba/ Daikin/ Trane) Ambient Temp. (+) 35 Deg. Cent. Minimum Tem. (-) 10 Deg. Cent. | 1.00 | Job |  | 325000.00 | 325000.00 | 397440.00 | 397440.00 | 425000.00 | 425000.00 | 610144.00 | 610144.00 | 325000.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
139.00 | Supply, installation, testing and commissioning of following minimum capacity VRV/VRF High wall type Indoor unit equipped with washable synthetic media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve, outer cabinet, cord less remote control, drain pan, necessary accessories etc., suitable for operation on 230 V ± 10%, 50 Hz, single phase AC supply, complete as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature.
139.10 | Hiwall Type with Cordless Remotes for 2.0 HP | 12.00 | Job |  | 19500.00 | 234000.00 | 15295.00 | 183540.00 | 22000.00 | 264000.00 | 34200.00 | 410400.00 | 183540.00 | HLK Infrastructure Pvt Ltd
140.00 | Supply, Installation, Testing and Commissioning of copper Y-Joints suitable for gas and liquid line of VRF System complete as required for the above system. | 11.00 | Job |  | 2186.25 | 24048.75 | 3450.00 | 37950.00 | 3000.00 | 33000.00 | 4500.00 | 49500.00 | 24048.75 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
141.00 | Supply, Installation, testing and commissioning including vaccumiazation and Nitrogen testing of following nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with XPLE Class-O tubular insulation/with Class-O closed cell elastometric nitrile rubber tubular sleeves sections of specified thickness as given below for Suction and Liquid lines, all accessories as per specifications etc. as required :
141.10 | 28.6 mm O.D. (insulation : 19 mm) | 10.00 | Mtr |  | 969.00 | 9690.00 | 1325.00 | 13250.00 | 1100.00 | 11000.00 | 1230.00 | 12300.00 | 9690.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
141.20 | 22.2 mm O.D. (insulation : 19 mm) | 15.00 | Mtr |  | 756.00 | 11340.00 | 1150.00 | 17250.00 | 1000.00 | 15000.00 | 1056.00 | 15840.00 | 11340.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
141.30 | 19.1 mm O.D. (insulation : 13 mm) | 15.00 | Mtr |  | 618.00 | 9270.00 | 1127.00 | 16905.00 | 800.00 | 12000.00 | 868.00 | 13020.00 | 9270.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
141.40 | 15.9 mm O.D. (insulation : 13 mm) | 15.00 | Mtr |  | 513.75 | 7706.25 | 977.50 | 14662.50 | 600.00 | 9000.00 | 716.00 | 10740.00 | 7706.25 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
141.50 | 12.7 mm O.D. (insulation : 13 mm) | 15.00 | Mtr |  | 407.25 | 6108.75 | 747.50 | 11212.50 | 500.00 | 7500.00 | 618.00 | 9270.00 | 6108.75 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
141.60 | 9.5 mm O.D. (insulation : 13 mm) | 55.00 | Mtr |  | 289.50 | 15922.50 | 529.00 | 29095.00 | 400.00 | 22000.00 | 530.00 | 29150.00 | 15922.50 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
141.70 | 6.4 mm O.D. (insulation : 13 mm) | 10.00 | Mtr |  | 214.50 | 2145.00 | 368.00 | 3680.00 | 300.00 | 3000.00 | 448.00 | 4480.00 | 2145.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
142.00 | Supply, installation, testing and commissioning of following Drain piping made of rigid uPVC pipe Class - 3 (6 kg/cm2) confirming to IS 4985-2000 complete with fittings, supports etc. as per specifications and duly insulated with 6 mm thick closed cell nitrile rubber insulation.
142.10 | 40 mm dia | 50.00 | Mtr |  | 159.00 | 7950.00 | 368.00 | 18400.00 | 200.00 | 10000.00 | 379.00 | 18950.00 | 7950.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
142.20 | 25 mm dia | 25.00 | Mtr |  | 119.25 | 2981.25 | 294.40 | 7360.00 | 150.00 | 3750.00 | 278.00 | 6950.00 | 2981.25 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
143.00 | Supply, Installation, Testing & Commissioning of Control cum Transmission shielded wiring of 2 core x 1.5 sqmm copper in suitable PVC conduits (Medium Duty) between indoor and out door unit. | 125.00 | Mtr |  | 95.25 | 11906.25 | 138.00 | 17250.00 | 100.00 | 12500.00 | 109.00 | 13625.00 | 11906.25 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
144.00 | Supply and laying power cable for outdoor & indoor units of following sizes
144.10 | 2 Core 1.5 Sqmm Cu Cable | 40.00 | Mtr |  | 119.25 | 4770.00 | 120.00 | 4800.00 | 150.00 | 6000.00 | 89.00 | 3560.00 | 3560.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
144.20 | 4 Core 16 Sqmm Cu Cable | 15.00 | Mtr |  | 258.75 | 3881.25 | 1095.00 | 16425.00 | 300.00 | 4500.00 | 856.00 | 12840.00 | 3881.25 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
145.00 | Supplying and installating 300mm width x 50 mm depth x 1.6 mm thickness size of perforated Hot Dipped Galvanised Iron Cable Tray(Galvanisation thickness not less than 50 microns) with perforation not more than 17.5% in convenient sections,joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts&nuts etc as required | 25.00 | Mtr |  | 537.00 | 13425.00 | 875.00 | 21875.00 | 600.00 | 15000.00 | 897.00 | 22425.00 | 13425.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
146.00 | Supply, Filling, Testing & Commissioning of Refrigerant Gas R-410 | 25.00 | KG |  | 637.50 | 15937.50 | 860.00 | 21500.00 | 700.00 | 17500.00 | 485.00 | 12125.00 | 12125.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
147.00 | Supply, Fabrication & fixing of MS Stand suitable for installation of VRF Outdoor Units | 1.00 | Each |  | 3975.00 | 3975.00 | 5000.00 | 5000.00 | 5000.00 | 5000.00 | 6000.00 | 6000.00 | 3975.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
148.00 | Providing & fixing 63 Amp, 4 pole MCCB complete with MS Enclouser and having following protections i.e under voltage, over voltage, single phase preventor, phase sequence preventor, etc. as required at site. | 1.00 | Each |  | 3720.00 | 3720.00 | 1550.00 | 1550.00 | 4500.00 | 4500.00 | 4850.00 | 4850.00 | 1550.00 | HLK Infrastructure Pvt Ltd
149.00 | SITC of PUSH BUTTON / TOUCH TYPE Centralized Remote Controller for controlling minimum 20 number of Indoor Units. | 1.00 | Each |  | 41340.00 | 41340.00 | 32000.00 | 32000.00 | 50000.00 | 50000.00 | 82670.00 | 82670.00 | 32000.00 | HLK Infrastructure Pvt Ltd
150.00 | Supply, installation, testing & commissioning of following rating, Inverter type, minimum 3 Star rated, Hi-wall, Split air-conditioner with hermetically sealed rotary/ twin rotary/ swing type compressor operating on refrigerant R-404a/ R-410a/ R-32.The body of indoor unit shall be made of ABS/HIPS/GS & having all safety, air filters, evaporator, condenser, cordless remote, electronic operation control & all accessories supplied with the unit by OEM etc as per manufacturer standards suitable for operation on 230 volts , 50 Hz, Single phase, AC supply, complete with refrigerent piping, control & power cable from outdoor to Indoor etc. up to 3 meter complete as required at site.
150.10 | 1.4/1.5 TR (Hot & Cold) | 13.00 | Each |  | 40500.00 | 526500.00 | 50197.00 | 652561.00 | 42000.00 | 546000.00 | 45500.00 | 591500.00 | 526500.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
151.00 | Supply and fixing of M S Stand for Out door unit duly painted of approved color & suaitable for wall mounting i/c fastners etc, as per requirement of outdoor A.C. units of different capacity & as per approval of EIC, complete as reqd. | 13.00 | Each |  | 954.75 | 12411.75 | 1173.00 | 15249.00 | 1000.00 | 13000.00 | 750.00 | 9750.00 | 9750.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
152.00 | Supply and fixing of Voltage Stabilizer suitable for operation of 1.5 TYR Hot & Cold type Inver Split AC and the Voltage range should be 170-280 volts (model: VS 500, make: V Gaurd or similar). | 13.00 | Each |  | 4570.50 | 59416.50 | 5175.00 | 67275.00 | 5000.00 | 65000.00 | 2450.00 | 31850.00 | 31850.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
153.00 | Supply & installation of automatic stainless steel hand dryers with powder coated metal body with touch free infra red activation suitable for co-operation on 230 volt, 50 Hz, single phase AC supply with automatic operation along with sensor, timer control, over load protection etc. complete as required. Similar to Make:- Euronics, Model :EH21NW
154.00 | Supply,Installation Testing Commissioning of water filter cum RO and UV purifier of 50 LPH capcity with TDS controller suitable for open well water and connection with existing water cooler i/c level controller having function of filter change alarm of audiable / visual type, auto start and auto off operation, protection from over voltage and over current etc. as required provided with pre filters etc as required. Make: ION Exchange,Kent , Hitech, Eureka Fobes or equivalent approved | 4.00 | Each |  | 38000.00 | 152000.00 | 33982.50 | 135930.00 | 12000.00 | 48000.00 | 22000.00 | 88000.00 | 48000.00 | JCC ENGINEERS PRIVATE LIMITED
155.00 | Supply, Installation, Testing and Commissioning of storage type self contained drinking water coolers of 60 ltrs cooling capacity per hours with 80 ltr storage capacity (60/80 ltrs.) confirming to IS:1475-2001 with upto date amendments suitable for operation on 230 volts +/- 10%, 50 Hz, single phase AC supply. The tank and body casing shall be made out from stainless steel SS 304 grade with minimum thickenss 0.8 mm.Full width single sheet moulded drain tray to prevent water splash.Top cover insulated fitted with hinges,double gasket all side for avoid dust particles,insects contaminated in the tank. Led bottom sheet should be fitted in between tank and top cover. Compressor and condensing standing base made with heavy guage not less than 1.25 mm and food grade stainless steel to avoid rusting or demage the water coolers. The water cooler shall have 02 numbers faucets and shall confirm as per specification including incomer cable of suitable rating with 3 pin 15 Amp. plug top etc. complete as required. | 2.00 | Each |  | 58299.00 | 116598.00 | 51750.00 | 103500.00 | 60000.00 | 120000.00 | 36000.00 | 72000.00 | 72000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
156.00 | Supply, Installation, Testing and Commissioning of storage type self contained drinking water coolers of 60 ltrs cooling capacity per hours with 80 ltr storage capacity (60/80 ltrs.) confirming to IS:1475-2001 with upto date amendments suitable for operation on 230 volts +/- 10%, 50 Hz, single phase AC supply. The tank and body casing shall be made out from stainless steel SS 304 grade with minimum thickenss 0.8 mm.Full width single sheet moulded drain tray to prevent water splash.Top cover insulated fitted with hinges,double gasket all side for avoid dust particles,insects contaminated in the tank. Led bottom sheet should be fitted in between tank and top cover. Compressor and condensing standing base made with heavy guage not less than 1.25 mm and food grade stainless steel to avoid rusting or demage the water coolers. The water cooler shall have 02 numbers faucets and shall confirm as per specification including incomer cable of suitable rating with 3 pin 15 Amp. plug top etc. complete as required. | 2.00 | Each |  | 29736.00 | 59472.00 | 48000.00 | 96000.00 | 45000.00 | 90000.00 | 36000.00 | 72000.00 | 59472.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
157.00 | SH- XI- Cold Storage facility
158.00 | Outer Dimension of Cold Storage Room will be approximately 3.2M x 3.4M x 4.5M Products to be stored will be Plum, Cherries, Apple & Frozen like Meat. Desire Temperature to be achieved : The Cold Room temperature is to be maintained between -4°C to 0°C while the ambient temperature is 35°C. The Pull down time shall be 24 Hours. Digital Temperature Indicator Cum Controller will be provided by Tenderer. Insulation: The Wall & Ceiling Gasket PUF (Polyurethane Foam) Panel Shall be 120 mm thickness Cyclopentane PUF insulated Panels with PPGI (Pre-Painted Galvanized Iron Sheet) finish and thichkness should be 0.5 mm. The Anti-Skid floor will be of 60 mm thick floor panel with marine ply 12 mm with 1.2 mm Al. Chequer Sheet. . Flush Type Door 34” (W) x 78” (H) with 50% overlap PVC Strip Curtain & View Port (300 x 300 mm). Door safety facility from outside like Al. Kick Plate, light switch, Lock & Key, Door Closure, Safety knob & Safety Alarm etc. reputed make for door accessories Refrigeration Units: Refrigeration System for maintaining temperature in Cold Room, Capacity: 20,000 BTU/H x 2 Nos (1 Working 1 standby). As per specifications i/c copper piping, cabling and starter Installation, testing and commissioning refrigeration units as required for one of door opening approximately 10-20 times in day. The refrigerant will be CFC Free (R 404 a/ R 134a). Refrigeration System will be air-cooled type with power supply 430v, 3 Ph, 50 Hz operations along with all necessary associated accessories. Refrigeration System will be included Copper Piping, PVC wire, refrigerant etc between Indoor & Outdoor unit. PVC drain pipes to drain out the condensate from evaporator outlet to the nearest drain pit. Refrigerant piping, control cabling & drain piping up to 5 meters length is encluded in the scope of this item. | 1.00 | Set |  | 530898.00 | 530898.00 | 718000.00 | 718000.00 | 500000.00 | 500000.00 | 225000.00 | 225000.00 | 225000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
159.00 | Outer Dimension of Cold Storage Room will be approximately 3.2M x 2.2M x 4.5M Products to be stored will be Raw Fish, Prawns Pharma, Cut Flowers, Pre-cut Vegetable. Desire Temperature to be achieved : The Cold Room temperature is to be maintained between 0°C to 10°C while the ambient temperature is 35°C. The Pull down time shall be 24 Hours. Digital Temperature Indicator Cum Controller will be provided by Tenderer. Insulation: The Wall & Ceiling Gasket PUF (Polyurethane Foam) Panel Shall be 60 mm thickness Cyclopentane PUF insulated Panels with PPGI (Pre-Painted Galvanized Iron Sheet) finish and thichkness should be 0.5 mm.. The Anti-Skid floor will be of 60 mm thick floor panel with marine ply 12 mm with 1.2 mm Al. Chequer Sheet. Flush Type Door 34” (W) x 78” (H) with 50% overlap PVC Strip Curtain & View Port (300 x 300 mm). Door safety facility from outside like Al. Kick Plate, light switch, Lock & Key, Door Closure, Safety knob & Safety Alarm etc. reputed make for door accessories. Refrigeration Units: Refrigeration System for maintaining temperature in Cold Room, Capacity: 15,000 BTU/H x 2 Nos (1 Working 1 standby). As per specifications i/c copper piping, cabling and starter Installation, testing and commissioning refrigeration units as required for one of door opening approximately 10-20 times in day. The refrigerant will be CFC Free (R 404 a/ R 134a). Refrigeration System will be air-cooled type with power supply 430v, 3 Ph, 50 Hz operations along with all necessary associated accessories. Refrigeration System will be included Copper Piping, PVC wire, refrigerant etc between Indoor & Outdoor unit. PVC drain pipes to drain out the condensate from evaporator outlet to the nearest drain pit. Refrigerant piping, control cabling & drain piping up to 5 meters length is encluded in the scope of this item. | 1.00 | Set |  | 384025.50 | 384025.50 | 459000.00 | 459000.00 | 500000.00 | 500000.00 | 225078.00 | 225078.00 | 225078.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
160.00 | Outer Dimension of Cold Storage Room will be approximately 3.2M x 2.8M x 4.5M Products to be stored will be Pre-cut Vegetable Desire Temperature to be achieved : The Cold Room temperature is to be maintained between 0°C to 10°C while the ambient temperature is 35°C. The Pull down time shall be 24 Hours. Digital Temperature Indicator Cum Controller will be provided by Tenderer. Insulation: The Wall & Ceiling Gasket PUF (Polyurethane Foam) Panel Shall be 60 mm thickness Cyclopentane PUF insulated Panels with PPGI (Pre-Painted Galvanized Iron Sheet) finish and thichkness should be 0.5 mm.. The Anti-Skid floor will be of 60 mm thick floor panel with marine ply 12 mm with 1.2 mm Al. Chequer Sheet. Flush Type Door 34” (W) x 78” (H) with 50% overlap PVC Strip Curtain & View Port (300 x 300 mm). Door safety facility from outside like Al. Kick Plate, light switch, Lock & Key, Door Closure, Safety knob & Safety Alarm etc. reputed make for door accessories. Refrigeration Units: Refrigeration System for maintaining temperature in Cold Room, Capacity: 15,000 BTU/H x 2 Nos (1 Working 1 standby). As per specifications i/c copper piping, cabling and starter Installation, testing and commissioning refrigeration units as required for one of door opening approximately 10-20 times in day. The refrigerant will be CFC Free (R 404 a/ R 134a). Refrigeration System will be air-cooled type with power supply 430v, 3 Ph, 50 Hz operations along with all necessary associated accessories. Refrigeration System will be included Copper Piping, PVC wire, refrigerant etc between Indoor & Outdoor unit. PVC drain pipes to drain out the condensate from evaporator outlet to the nearest drain pit. Refrigerant piping, control cabling & drain piping up to 5 meters length is encluded in the scope of this item. | 1.00 | Set |  | 428870.00 | 428870.00 | 499000.00 | 499000.00 | 494000.00 | 494000.00 | 225500.00 | 225500.00 | 225500.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
161.00 | Outer Dimension of Cold Storage Room will be approximately 3.2M x 2.8M x 4.5M Products to be stored will be Raw Fish, Prawns Pharma Desire Temperature to be achieved : The Cold Room temperature is to be maintained between 0°C to 10°C while the ambient temperature is 35°C. The Pull down time shall be 24 Hours. Digital Temperature Indicator Cum Controller will be provided by Tenderer. Insulation: The Wall & Ceiling Gasket PUF (Polyurethane Foam) Panel Shall be 60 mm thickness Cyclopentane PUF insulated Panels with PPGI (Pre-Painted Galvanized Iron Sheet) finish and thichkness should be 0.5 mm.. The Anti-Skid floor will be of 60 mm thick floor panel with marine ply 12 mm with 1.2 mm Al. Chequer Sheet. Flush Type Door 34” (W) x 78” (H) with 50% overlap PVC Strip Curtain & View Port (300 x 300 mm). Door safety facility from outside like Al. Kick Plate, light switch, Lock & Key, Door Closure, Safety knob & Safety Alarm etc. reputed make for door accessories. Refrigeration Units: Refrigeration System for maintaining temperature in Cold Room, Capacity: 15,000 BTU/H x 2 Nos (1 Working 1 standby). As per specifications i/c copper piping, cabling and starter Installation, testing and commissioning refrigeration units as required for one of door opening approximately 10-20 times in day. The refrigerant will be CFC Free (R 404 a/ R 134a). Refrigeration System will be air-cooled type with power supply 430v, 3 Ph, 50 Hz operations along with all necessary associated accessories. Refrigeration System will be included Copper Piping, PVC wire, refrigerant etc between Indoor & Outdoor unit. PVC drain pipes to drain out the condensate from evaporator outlet to the nearest drain pit. Refrigerant piping, control cabling & drain piping up to 5 meters length is encluded in the scope of this item. | 1.00 | Set |  | 428870.00 | 428870.00 | 464818.00 | 464818.00 | 497415.00 | 497415.00 | 225000.00 | 225000.00 | 225000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
162.00 | Supplying and Fixing of extra refrigerant piping along with control cable beyond 5 meters against above mentioned items (1 to 4) complete with refrigerant pipe insulation etc.as required | 15.00 | RMT |  | 954.00 | 14310.00 | 950.00 | 14250.00 | 1200.00 | 18000.00 | 830.00 | 12450.00 | 12450.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
| Total in Figures |  |  |  |  | 17261665.75 |  | 20785328.00 |  | 18855555.00 |  | 25449005.00
Lowest Amount Quoted BY: S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED(17261665.75)

## BOQ Summary
BOQ Summary Details Tender Title: Construction Of Cargo Complex At Srinagar Intl Airport, Srinagar (SH Electrical Works) Tender ID: 2021_AAI_69146_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED | 17261665.75 | L1
| 2 | JCC ENGINEERS PRIVATE LIMITED | 18855555.00 | L2
| 3 | HLK Infrastructure Pvt Ltd | 20785328.00 | L3
| 4 | CIS GLOBAL INFRATECH PRIVATE LIMITED | 25449005.00 | L4