## BoQ1
Government eProcurement System Created By: ARUN KUMAR K Created Date/Time: 08-Mar-2021 03:04 PM Tender Title: Provision of Four Pole Structure along with AB switches for terminating 33KV HT cables at LGBI Airport, Guwahati Tender ID: 2021_AAI_69211_1
Tender Inviting Authority: Senior Manager (Engg – Elect), AAI, LGBI Airport, Guwahati, Assam – 781 015
Name of Work: Provision of Four Pole Structure along with AB switches for terminating 33KV HT cables at LGBI Airport, Guwahati.
Contract No: AAI/ENGG/SM(E-E)/GHY/NIT-15/2020-21
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | EVERLITE ENGINEERING INDUSTRIES(GSTN-18AABFE6096R1ZN) |  | Singhi InfraPower Projects Pvt. Ltd.(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply and Erection of Steel tubular circular cross section swaged type G.I poles (Type designation : 410-SP66) conforming to IS: 2713 (Part-I and III): 1980 amended upto date having overall length of 12.0 meters, duly welded with MS/GI base plate of size 500 mm X 500 mm X 10mm thick at the bottom, painting with two coats of bituminous black paint upto planting height (i.e., below ground level) complete as required as per approved drawings and specifications. | 4.00 | Each |  | 32500.00 | 130000.00 | 38000.00 | 152000.00 | 130000.00 | EVERLITE ENGINEERING INDUSTRIES
2.00 | Providing RCC foundation for erection of swaged Poles including excavation (all kinds of soil including concrete/bitumenous surfaces), making base foundation with cement concrete 1:4:8 (1 cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size ), providing centering and shuttering including strutting, steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete, providing reinforced cement concrete 1:1.5:3 (1 cement : 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size) and filling available excavated earth (excluding rock) & disposal of excess excavated soil at a distance of 50 mtrs. etc., complete as required as per attached drawings and as per the directions of E.I.C. | 4.00 | Job |  | 5000.00 | 20000.00 | 4000.00 | 16000.00 | 16000.00 | Singhi InfraPower Projects Pvt. Ltd.
3.00 | Providing and making round Tubular pole collar of 0.40 mtrs dia. X 0.50 mtrs above ground level all around the pole with cement concrete of 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size ) including form work, plastering, painting with two coats of water proofing cement paint etc., complete as required. | 4.00 | Each |  | 2000.00 | 8000.00 | 500.00 | 2000.00 | 2000.00 | Singhi InfraPower Projects Pvt. Ltd.
4.00 | Supplying and erection of Galvanised stay set complete with 20 mm dia X 1.8 metres long stay rod, anchor plate of size 45 cm X 45 cm X 7.5 mm, thimble, stay clamps, turn buckle, 7/ 4.00 mm dia G.I. stay wire and strain insulator etc in cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size ) foundation including excavation and refilling etc. complete as per specifications and as required. | 4.00 | Each |  | 3000.00 | 12000.00 | 2000.00 | 8000.00 | 8000.00 | Singhi InfraPower Projects Pvt. Ltd.
5.00 | Supply, fabrication and erection of Galvanized Channel/Angles for mounting switchgears/ Insulators/ Lightning Arrestor/ D.O Fuse on the four pole structure including cutting, hoisting, welding, drilling holes, fixing in position along with necessary accessories such as clamps, nuts, bolts, washers etc. complete as required as per approved drawing and specifications.(Note: For payment purpose only weight of structural steel members shall be considered excluding fixing accessories such as clamps, nuts, bolts, fasteners etc.) | 1210.00 | Kg |  | 87.00 | 105270.00 | 80.00 | 96800.00 | 96800.00 | Singhi InfraPower Projects Pvt. Ltd.
6.00 | Supplying and Erection of explusion type Drop Out Fuse with polymer insulator having nominal system voltage of 33kV, rated current of 200 Amps, mounting arrangements for fixing on cross arms/channels including drilling holes for insulator fittings, tightening with G.I bolts, nuts, washers etc., complete as per specifications and as required. (1Set of three numbers for 3 phase system). | 3.00 | Set |  | 18500.00 | 55500.00 | 20000.00 | 60000.00 | 55500.00 | EVERLITE ENGINEERING INDUSTRIES
7.00 | Supplying and Erection of 33 KV, 600 Amps double break, centre rotating type, OFF load Isolator with gang operated earth switch, complete with heavy duty and self aligning type, spring loaded fixed contacts and tubular blades forming the moving contacts made from high conductivity hard drawn electrolytic copper, GI phase coupling shaft, GI operating rods of suitable length with handle, polymer insulators, GI base channel, 7/8mm dia GI rod with spring assisted for arching horn etc., complete as per spcifications and as required. (1 set of three number for 3 phase system) | 3.00 | Set |  | 65000.00 | 195000.00 | 50000.00 | 150000.00 | 150000.00 | Singhi InfraPower Projects Pvt. Ltd.
8.00 | Supplying and Erection of Metal oxide Non-Linear resistor, station class gapless type heavy duty lightning arrestor having polymer housing for the insulator suitable for 3 wire, 33 KV overhead lines with continuous operating voltage of 30 KV with a nominal discharge current rating of 10 KA (station class), complete with mounting arrangement, G.I. bolts, nuts, washers etc. complete as per specifications and as required. (Set of three numbers for 3 phase system). | 2.00 | Set |  | 30000.00 | 60000.00 | 45000.00 | 90000.00 | 60000.00 | EVERLITE ENGINEERING INDUSTRIES
9.00 | Supplying and Erection of 33 kV (10 KN) Polymer pin insulator complete with long steel head G.I. pin, nuts, washers etc. complete as per specifications and as required. | 9.00 | Each |  | 800.00 | 7200.00 | 1000.00 | 9000.00 | 7200.00 | EVERLITE ENGINEERING INDUSTRIES
10.00 | Supplying and Erection of AAAC Dog Conductor (100 sq mm) complete with binding at existing insulator, jointing, jumpering, teeing off connecting and clearing of obstacles etc. complete as per specifications and as required. | 72.00 | Meter |  | 105.00 | 7560.00 | 60.00 | 4320.00 | 4320.00 | Singhi InfraPower Projects Pvt. Ltd.
11.00 | Supply and erection of 1.5 inch (Nominal size) Aluminium Tubular Busbar made out of Schedule-40 grade Aluminium Pipe along with post insulators, necessary mounting arrangements, necessary connectors for making connections between pipe bus and conductors (AAAC Dog), painting for identication of phases etc complete as per specifications and as per direction of E-I-C. | 30.00 | Meter |  | 3500.00 | 105000.00 | 200.00 | 6000.00 | 6000.00 | Singhi InfraPower Projects Pvt. Ltd.
12.00 | Providing and fixing of 33 KV H.T. danger notice plate of 250 mm X 200 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 4.00 | set |  | 250.00 | 1000.00 | 100.00 | 400.00 | 400.00 | Singhi InfraPower Projects Pvt. Ltd.
13.00 | Dismantling of existing Cement / M.S Poles of H.T Double pole structure embedded in cement concrete foundation including dismantling the switchgears, fuses, over head conductor, G.I. wire, cross arms/ mounting supports, insulators etc. & shifting the same to the dismantle store/yard upto a distance of 100 mtrs etc., complete as required as per the directions of EIC. | 2.00 | Job |  | 5000.00 | 10000.00 | 5000.00 | 10000.00 | 10000.00 | EVERLITE ENGINEERING INDUSTRIES, Singhi InfraPower Projects Pvt. Ltd.
14.00 | Supply & Installation of 630A, 33KV Vacuum Circuit Breaker(Trolley mounted) of Kirloskar Make (Type VRK36-3) suitable for operation on 33KV, 3 Phase, 50 Hz A.C. supply in the existing 33 KV HT VCB Panel (Type : S36 VCB), testing and commissioning by OEM or their Authorised Indian associate/ system integrator, transportation, loading, unloading etc., complete with the following parameters and as per specifications: (a) Rated Voltage : 33 KV (b) Rated Current : 630 Amps (c) Breaking Capacity : 25 KA (d) Form : GM (e) Spec : IEC 56 (f) Pole : 3 (g) Rated Frequency : 50 Hz (h) Closing/ Tripping coils operating voltage : 110 V DC (i) Operating gear type : Motor & Manual (j) Motor Voltage : 230 V AC | 1.00 | Each |  | 660000.00 | 660000.00 | 600000.00 | 600000.00 | 600000.00 | Singhi InfraPower Projects Pvt. Ltd.
15.00 | Supply & Installation of 1250A, 11KV Vacuum Circuit Breaker (Trolley mounted) of Kirloskar Make (Type C-500) suitable for operation on 11 KV, 3 Phase, 50Hz A.C. supply in the existing 11KV HT VCB Panel (Type : A12 650 VCB) testing and commissioning by OEM or their Authorised Indian associate/ system integrator, transportation, loading, unloading etc., complete with the following parameters and as per specifications: (a) Rated Voltage : 11 KV (b) Rated Current : 1250 Amps (c) Breaking Capacity : 25 KA (d) Form : GM (e) Spec : IEC 56 (f) Pole : 3 (g) Rated Frequency : 50 Hz (h) Closing/ Tripping coils operating voltage : 110 V DC (i) Operating gear type : Motor & Manual (j) Motor Voltage : 230 V AC | 1.00 | Each |  | 615000.00 | 615000.00 | 600000.00 | 600000.00 | 600000.00 | Singhi InfraPower Projects Pvt. Ltd.
16.00 | Supplying, Installation, Testing & Commissioning of Outdoor Type Floor mounted 11KV Load Break Switch (LBS) single panel board with enclosure protection class IP 54 or higher of cubical construction with double door and top canopy having capacities as mentioned below for use on 3 phase, 11KV, 50 Hz AC supply, fabricated out of CRCA sheet steel of 2mm thick for enclosures and covers, 3mm thick for base frame and gland plates including cleaning & finishing complete with 7 tank process and powder coating in approved shade, high conductivity copper bus bars of 630 Amps capacity, space heaters, thermostat, control MCBs, control wiring, common copper earth bar of size 50mm X 5 mm and equipped with the following switchgear and accessories, suitable bus bar arrangement for connections of 3 runs of 1 Core X 185 Sq.mm XLPE cables (Incoming) and 3Core X 120 Sq.mm XLPE cable (outgoing) of grade 11KV (cable entries from bottom) including testing and commissioning by OEM or their Authorised Indian associate/ system integrator, providing civil platform consisting of cement concrete pedestal/foundation, plastering the outer surfaces, excavation & disposal of surplus soil/ hardrock etc., complete as required as per specifications. (1) 11KV, 630A, 21kA for 3sec, Load Break Switch having manual Operated Spring Charge & Closing Mechanism with Earth Switch fitted, HT HRC Fuses of suitable rating, 2 NO+2NC Auxillary Switch, Mechanical ON/OFF Indicators, Mechanical Trip with Push button, Electrical Trip with 230V AC Shunt Trip coil & hand trip device, Mechanical Interlock between Earth and Main Switch - 01 Set (ii) 9KV 10 KA Station class polymer type Surge arrestors - 01 Set (Set of 03 Nos.) (iii) LED indication lamps for LBS ON & OFF - 01 Set | 1.00 | Each |  | 415000.00 | 415000.00 | 300000.00 | 300000.00 | 300000.00 | Singhi InfraPower Projects Pvt. Ltd.
17.00 | Supplying of 250 mm (OD) HDPE pipe of PE-80 grade, PN-6 rating, ISI marked etc conforming to IS:4984 with upto date amendments complete as required as per specifications. | 100.00 | Meter |  | 1750.00 | 175000.00 | 1100.00 | 110000.00 | 110000.00 | Singhi InfraPower Projects Pvt. Ltd.
18.00 | Laying of DWC/HDPE (High Density Polyethylene) of 250mm dia HDPE pipe along with accessories like bends, couplers, sockets including fitting and cutting, jointing with adhesive/solvent etc, direct in ground for the following type of surfaces
18.01 | under soft soil (1.2 mtr below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 75.00 | Meter |  | 250.00 | 18750.00 | 500.00 | 37500.00 | 18750.00 | EVERLITE ENGINEERING INDUSTRIES
18.02 | under hard/concrete/bituminous surface (1.2 mtr below ground level), dismantling/breaking all types of surfaces, excavation and refilling the trench, finishing the top layer with 6" cement concrete etc., complete as required. | 25.00 | Meter |  | 800.00 | 20000.00 | 1000.00 | 25000.00 | 20000.00 | EVERLITE ENGINEERING INDUSTRIES
19.00 | Laying of one number XLPE power cable of 33 kV grade of 3 Core X 185 sq.mm size in the existing RCC/ HUME/ METAL/HDPE pipe as required. | 100.00 | Meter |  | 300.00 | 30000.00 | 500.00 | 50000.00 | 30000.00 | EVERLITE ENGINEERING INDUSTRIES
20.00 | Laying of one number XLPE power cable of 33 kV grade of 3 Core X 185 sq.mm size in the existing masonry open duct as required. | 65.00 | Meter |  | 200.00 | 13000.00 | 200.00 | 13000.00 | 13000.00 | EVERLITE ENGINEERING INDUSTRIES, Singhi InfraPower Projects Pvt. Ltd.
21.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of 3 Core X 120 sq.mm / 3 runs of 1 Core X 185 sq.mm size in the existing masonry open duct as required. | 35.00 | Meter |  | 100.00 | 3500.00 | 100.00 | 3500.00 | 3500.00 | EVERLITE ENGINEERING INDUSTRIES, Singhi InfraPower Projects Pvt. Ltd.
22.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 11 KV grade of 3 Core X 120 sq.mm / 3 runs of 1 Core X 185 sq.mm size in the existing RCC/ HUME/ METAL/HDPE pipe as required. | 15.00 | Meter |  | 150.00 | 2250.00 | 100.00 | 1500.00 | 1500.00 | Singhi InfraPower Projects Pvt. Ltd.
23.00 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for 3 Core X 185 Sq. mm, XLPE aluminium conductor cable of 33 kV grade as required. | 2.00 | Set |  | 26000.00 | 52000.00 | 4000.00 | 8000.00 | 8000.00 | Singhi InfraPower Projects Pvt. Ltd.
24.00 | Supplying and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for 3 Core X 185 Sq. mm, XLPE aluminium conductor cable of 33 kV grade as required. | 5.00 | Set |  | 10000.00 | 50000.00 | 5000.00 | 25000.00 | 25000.00 | Singhi InfraPower Projects Pvt. Ltd.
25.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for the following grades of XLPE aluminium conductor cables as required
25.01 | 1 Core X 185 sq. mm (11 KV grade) | 3.00 | Set |  | 3500.00 | 10500.00 | 5000.00 | 15000.00 | 10500.00 | EVERLITE ENGINEERING INDUSTRIES
25.02 | 3 Core X 120 sq. mm (11 KV grade) | 2.00 | Set |  | 4500.00 | 9000.00 | 5000.00 | 10000.00 | 9000.00 | EVERLITE ENGINEERING INDUSTRIES
25.03 | 3 Core X 185 sq. mm (33 KV grade) | 1.00 | Set |  | 9000.00 | 9000.00 | 10000.00 | 10000.00 | 9000.00 | EVERLITE ENGINEERING INDUSTRIES
26.00 | Retreiving of one number PVC/XLPE insulated and PVC sheathed aluminium conductor cable of 33 KV grade of 3core X 300 Sq. mm size cable from the existing closed duct/RCC/ HUME/ METAL pipe/HDPE pipe/ GI pipe including checking the physical damage of cable etc. as reqd. | 25.00 | Meter |  | 500.00 | 12500.00 | 100.00 | 2500.00 | 2500.00 | Singhi InfraPower Projects Pvt. Ltd.
27.00 | Earthing with GI earth plate 600mm x 600mm x 6.0mm thick including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/coke and salt as required. | 4.00 | Set |  | 7500.00 | 30000.00 | 8000.00 | 32000.00 | 30000.00 | EVERLITE ENGINEERING INDUSTRIES
28.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | Meter |  | 600.00 | 18000.00 | 200.00 | 6000.00 | 6000.00 | Singhi InfraPower Projects Pvt. Ltd.
29.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections including welding/clamping on pole/channels etc. as required. | 88.00 | Meter |  | 250.00 | 22000.00 | 100.00 | 8800.00 | 8800.00 | Singhi InfraPower Projects Pvt. Ltd.
| Total in Figures |  |  |  |  | 2882030.00 |  | 2462320.00
Lowest Amount Quoted BY: Singhi InfraPower Projects Pvt. Ltd.(2462320.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Four Pole Structure along with AB switches for terminating 33KV HT cables at LGBI Airport, Guwahati Tender ID: 2021_AAI_69211_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Singhi InfraPower Projects Pvt. Ltd. | 2462320.00 | L1
| 2 | EVERLITE ENGINEERING INDUSTRIES | 2882030.00 | L2