## BoQ1
Government eProcurement System Created By: Pawan Singh Created Date/Time: 15-Mar-2021 04:26 PM Tender Title: Development of Deoghar Airport. SH SITC of Apron Flood Light High Mast and 100ft Height National Flag Mast at AAI Deoghar Airport. Tender ID: 2021_AAI_69645_1
Tender Inviting Authority: AGM (Engg-Elect), AAI, Deoghar Airport, Deoghar.
Name of Work: Development of Deoghar Airport, Deoghar. SH:- SITC of Apron Flood Light High Mast & 100ft Height National Flag Mast at AAI Deoghar Airport
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ENERGYGREEN TECHNOPOWER PVT LTD(GSTN-23AAECE7344J1ZM) |  | RVD INFRA SOLUTION PVT.LTD.(GSTN-24AAGCR7767L1ZQ) |  | jaydeep agency corporation(GSTN-24ACIPP6157B1ZQ) |  | BR Power Control and Automation Services(GSTN-06AREPS4024K1ZP) |  | M/S AMAR ENTERPRISES(GSTN-20AAMFA2722R1ZE) |  | GIRI ENTERPRISES(GSTN-20ACEPG3920H1ZA) |  | RANJIT SALES CORPORATION(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.10 | Apron High Mast Supply, Fabrication, Installation, Testing and Commissioning of following height High Mast tower, including foundation, two sectioned/three sectioned, hot dip galvanised, suitable for wind velocity as per IS 875 along with its all accessories : viz head frame, Stainless steel wire rope, double drum winch, Galvanised lantern carriage in asymmetrical arrangement (suitable for LED luminaire up to 400 W - 10 Nos ), lightning finial, integral power tool installed inside the base compartment for its operation, trailing cable, supply of foundation bolts, design, construction of shallow foundation with required grade concrete for the High Mast as per the soil bearing capacity at site at suitable depth with all materials & labour etc. including termination, wiring, connection, fitting, fixing, Installation testing and commissioning of luminairs. etc. complete as reqiured lux level as per special condition of contract . The mast shall have an integral powertool with necessary acessories installed inside the base compartment for its operation. The necessary arrangement for motor (Control switch gear and starter) is to be housed inside the base compartment of mast. etc complete as required. 22 (Twenty-Two) metre height | 3.00 | Sets | 400000.00 | 285500.00 | 856500.00 | 402500.00 | 1207500.00 | 330125.00 | 990375.00 | 338570.00 | 1015710.00 | 274500.00 | 823500.00 | 300000.00 | 900000.00 | 400000.00 | 1200000.00 | 823500.00 | M/S AMAR ENTERPRISES
1.20 | Apron High Mast Supply, Fabrication, Installation, Testing and Commissioning of following height High Mast tower, including foundation, two sectioned/three sectioned, hot dip galvanised, suitable for wind velocity as per IS 875 along with its all accessories : viz head frame, Stainless steel wire rope, double drum winch, Galvanised lantern carriage in asymmetrical arrangement (suitable for LED luminaire up to 400 W - 10 Nos ), lightning finial, integral power tool installed inside the base compartment for its operation, trailing cable, supply of foundation bolts, design, construction of shallow foundation with required grade concrete for the High Mast as per the soil bearing capacity at site at suitable depth with all materials & labour etc. including termination, wiring, connection, fitting, fixing, Installation testing and commissioning of luminairs. etc. complete as reqiured lux level as per special condition of contract . The mast shall have an integral powertool with necessary acessories installed inside the base compartment for its operation. The necessary arrangement for motor (Control switch gear and starter) is to be housed inside the base compartment of mast. etc complete as required. 17(Seventeen) metre height | 4.00 | Sets | 390000.00 | 185250.00 | 741000.00 | 345000.00 | 1380000.00 | 225625.00 | 902500.00 | 204079.00 | 816316.00 | 202500.00 | 810000.00 | 290000.00 | 1160000.00 | 250000.00 | 1000000.00 | 741000.00 | ENERGYGREEN TECHNOPOWER PVT LTD
2.00 | Supply of LED Type low intensity aviation obstruction light suitable for 220 V , 50 HZ AC supply and as per ICAO standard etc. complete as required. As per list of approved make or equivalent. | 9.00 | Each | 2783.20 | 12500.00 | 112500.00 | 5750.00 | 51750.00 | 2900.00 | 26100.00 | 2489.00 | 22401.00 | 2100.00 | 18900.00 | 2500.00 | 22500.00 | 5000.00 | 45000.00 | 18900.00 | M/S AMAR ENTERPRISES
3.00 | Supply of LED type Flood light Luminaries having minimum system lumen output of 38500 lumens, maximum 350 watt input power with sufficient nos. of high power LEDS with suitable lens to ensure uniform distribution of light, integral electronics power driver suitable for 140 V to 270 V + 10% ,50HZ AC supply, Outdoor , IP65 Protection, thermal management with heat sinks, average life of LED > 50000 hrs, power factor > 0.95, mounting arrangement with all accessories,CRI > 70,Pressure Die Cast Aluminium housing etc as per TS. (Complete luminiare including Driver/ Control gear, LED, all accessories etc shall have minimum 5 year warrantee) | 80.00 | Each | 16000.00 | 10625.00 | 850000.00 | 14950.00 | 1196000.00 | 14375.00 | 1150000.00 | 13630.00 | 1090400.00 | 10500.00 | 840000.00 | 11000.00 | 880000.00 | 11000.00 | 880000.00 | 840000.00 | M/S AMAR ENTERPRISES
4.00 | FEEDER PILLARS for APRON FLOOD LIGHT : PTTA TYPE PANEL Design, Manufacture, Supplying, Transport to the site, Receiving, Unloading, Shifting to various locations, handling, assembling, installation in correct aligned position, grouting with dash fasteners,GI nuts-bolts,testing and commissioning of the following fabricated in compartmentalize conformto IS: 8623/1993, Suitable for 415V, 3Phase,4Wire 50Hz Ac supply, are housedin CRCA sheet steel of 2mm thick for frame workand covers, 3mm thick for gland plate, bottom base l of Size 50 x 50 x 6 mm MS angle for base with front & back side hinged door with locking arrangement for MDB/MCC and SDBs etc., including cleaning & finishing complete, SMC bus bar supports, with short circuit with stand capacity of 36kA for 1 Sec., fabrication shall be done in transportable sections and all front and backdoors shall be hinged type and earth with frame, Entire panel shall have a Aluminium contineous earth bar of size 50mm x 6mm or as specified below at the rear with 2 Nos. earth stud at each side, inter connections bus bar to switch gears upto cable alley, bus bars and control wiring with suitable size of FRLS PVC insulated copper conductor cable, able alleys, cable gland plate in two half, including providing following switch gears:- The Bus bars will be Copper purity 99.9%/ electrolyticgrade E91 Alumunium duly sleeved with Helogen Free heat shrink coloured Insulated tube confirming to IEC 6068-3-247 Standard. Provide electrical insulating shrouds, reusable type covers for bus bars Bootson corners. Panels will be powder coating (60-80 microns per Is:13871 for indoor and 90-100 micronfor outdoor), include one size higher terminal block in cable alley and interconnecting wires between bus bars and terminals via MCB/MCCB rating 100A. All Bus-Bar alley and relay compartments shall be provided with fully automatic control thermotate with strip heater. Design, manufacturing, supply, installation, testing and commissioning of weather and vermin proof, powder coated, outdoor ( double door , back side door openable) type feeder pillar, Duly fabricated with 2mm thick CRCA Sheet Steel, 3mm thick sheet steel for gland plate Degree of Protection of Enclossure shall be IP~65.suitable for operation on 3 phase and neutral, 415 V,50 HZ AC system.entire panel shall have a common AL earth bar of size 50mmx6mm at the rear with two number earth stud. Cable entry will be from bottom. Control Wiring should be done by 1100V grade PVC insulated 2.5 Sq.mm solid copper conductor cable. The feeder pillar shall consist of following swich gears, BUS Bars and other acessories complete as required and as per technical specification attached with tender document. a) Incomers :- i) 100Amps. 4 poleThermal magnetic release ( adjustable) MCCB, Breaking capecity ICU = 35 KA CT operated digital multi function metre – 2 nos.(Incomers) ii) Extended operating mechanism for MCCB- 02 Nos. iii) ON / OFF / Trip (R,G,A) 230 V AC Supply LED indication lamps : 06 Nos. iv) Phase indication lamp LED type (R,Y,B) 230 V AC Supply : 06 Nos. b) Bus coupler : 100Amps. 4 pole Thermal magnetic release ( adjustable) MCCB, Breaking capecity ICU = 35 KA – 1 no. c) 100 Amps. TPN Aluminium Busbar d) Outgoings. i) 40Amps. 4 pole MCCB with CT operated digital ammeter along with CTs & selector switch – 2 nos. ii) Extended operating mechanism for MCCB- 02 Nos. iii) 10Amp C-Curve TPN MCB : 8 Nos. iv) 12 amp AC3 rating with 1 NO& 1NC ( equivalent to MNX 12, L&T Make) Contactor : 8 Nos. v) L/R SWITCH : 8Nos. vi) ON OFF LED Indication lamp : 16 Nos. vii) CTs,15 VA,40/5 A,CL-1 : 06 Nos. | 2.00 | Jobs | 211000.00 | 262500.00 | 525000.00 | 138000.00 | 276000.00 | 232673.00 | 465346.00 | 221600.00 | 443200.00 | 228000.00 | 456000.00 | 200000.00 | 400000.00 | 25000.00 | 50000.00 | 50000.00 | RANJIT SALES CORPORATION
5.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonary enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 20.00 | Sets | 5102.00 | 10000.00 | 200000.00 | 9200.00 | 184000.00 | 5093.00 | 101860.00 | 14535.00 | 290700.00 | 14000.00 | 280000.00 | 7000.00 | 140000.00 | 10000.00 | 200000.00 | 101860.00 | jaydeep agency corporation
6.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 60.00 | Mtr | 413.00 | 313.00 | 18780.00 | 690.00 | 41400.00 | 480.00 | 28800.00 | 173.00 | 10380.00 | 300.00 | 18000.00 | 500.00 | 30000.00 | 350.00 | 21000.00 | 10380.00 | BR Power Control and Automation Services
7.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 200.00 | Mtr | 114.00 | 438.00 | 87600.00 | 287.50 | 57500.00 | 200.00 | 40000.00 | 208.00 | 41600.00 | 100.00 | 20000.00 | 150.00 | 30000.00 | 200.00 | 40000.00 | 20000.00 | M/S AMAR ENTERPRISES
8.10 | Supply of following sizes XLPE insulated & PVC sheathed,1.1 KV grade, aluminium conductor, armoured power cable confirming to IS: 7098, Part-1/1988 with upto date amendments. 3.5Core x 70 Sq mm | 826.00 | Mtr | 223.20 | 338.00 | 279188.00 | 287.50 | 237475.00 | 362.00 | 299012.00 | 259.00 | 213934.00 | 320.00 | 264320.00 | 220.00 | 181720.00 | 200.00 | 165200.00 | 165200.00 | RANJIT SALES CORPORATION
8.20 | Supply of following sizes XLPE insulated & PVC sheathed,1.1 KV grade, aluminium conductor, armoured power cable confirming to IS: 7098, Part-1/1988 with upto date amendments. 4 X 25 sq. mm | 1113.00 | Mtr | 114.60 | 170.00 | 189210.00 | 218.50 | 243190.50 | 180.00 | 200340.00 | 130.00 | 144690.00 | 163.00 | 181419.00 | 110.00 | 122430.00 | 100.00 | 111300.00 | 111300.00 | RANJIT SALES CORPORATION
8.30 | Supply of following sizes XLPE insulated & PVC sheathed,1.1 KV grade, aluminium conductor, armoured power cable confirming to IS: 7098, Part-1/1988 with upto date amendments. 2 core x 10 Sq mm | 875.00 | Mtr | 57.00 | 88.00 | 77000.00 | 103.50 | 90562.50 | 89.00 | 77875.00 | 65.00 | 56875.00 | 81.00 | 70875.00 | 70.00 | 61250.00 | 80.00 | 70000.00 | 56875.00 | BR Power Control and Automation Services
9.10 | Supply of following sizes XLPE insulated& extruded PVC inner sheath and PVC outer sheath solid Copper conductor armoured Control cable of 1.1 KV grade conforming to IS-1554 (part-I) with upto date amendments etc complete as required. 10 Core x 2.5 Sqmm | 861.00 | Mtr | 210.00 | 331.00 | 284991.00 | 391.00 | 336651.00 | 328.00 | 282408.00 | 254.00 | 218694.00 | 306.00 | 263466.00 | 300.00 | 258300.00 | 20.00 | 17220.00 | 17220.00 | RANJIT SALES CORPORATION
9.20 | Supply of following sizes XLPE insulated& extruded PVC inner sheath and PVC outer sheath solid Copper conductor armoured Control cable of 1.1 KV grade conforming to IS-1554 (part-I) with upto date amendments etc complete as required. 19 Core x 2.5 Sqmm | 236.00 | Mtr | 387.20 | 594.00 | 140184.00 | 897.00 | 211692.00 | 594.00 | 140184.00 | 461.00 | 108796.00 | 560.00 | 132160.00 | 550.00 | 129800.00 | 25.00 | 5900.00 | 5900.00 | RANJIT SALES CORPORATION
10.10 | Laying of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL/ HDPE pipe as required. upto 35 sq. mm | 2423.00 | Mtr | 22.00 | 31.00 | 75113.00 | 69.00 | 167187.00 | 25.00 | 60575.00 | 24.00 | 58152.00 | 50.00 | 121150.00 | 20.00 | 48460.00 | 50.00 | 121150.00 | 48460.00 | GIRI ENTERPRISES
10.20 | Laying of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL/ HDPE pipe as required. Above 35 sq. mm and upto 95 sq. mm | 460.00 | Mtr | 34.00 | 44.00 | 20240.00 | 115.00 | 52900.00 | 30.00 | 13800.00 | 41.00 | 18860.00 | 50.00 | 23000.00 | 30.00 | 13800.00 | 50.00 | 23000.00 | 13800.00 | jaydeep agency corporation, GIRI ENTERPRISES
11.10 | Laying of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1 KV grade of following size in the existing masonary open duct as required. upto 35 sq. mm | 865.00 | Mtr | 17.00 | 31.00 | 26815.00 | 92.00 | 79580.00 | 25.00 | 21625.00 | 24.00 | 20760.00 | 50.00 | 43250.00 | 20.00 | 17300.00 | 50.00 | 43250.00 | 17300.00 | GIRI ENTERPRISES
11.20 | Laying of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1 KV grade of following size in the existing masonary open duct as required. Above 35 sq. mm and upto 95 sq. mm | 350.00 | Mtr | 27.00 | 44.00 | 15400.00 | 126.50 | 44275.00 | 30.00 | 10500.00 | 35.00 | 12250.00 | 50.00 | 17500.00 | 30.00 | 10500.00 | 100.00 | 35000.00 | 10500.00 | jaydeep agency corporation, GIRI ENTERPRISES
12.10 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/ XLPE aluminium conductor cable of 1.1 grade as required. 3.5Core x 70 Sq mm | 8.00 | Sets | 298.00 | 688.00 | 5504.00 | 460.00 | 3680.00 | 350.00 | 2800.00 | 1428.00 | 11424.00 | 1500.00 | 12000.00 | 300.00 | 2400.00 | 100.00 | 800.00 | 800.00 | RANJIT SALES CORPORATION
12.20 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/ XLPE aluminium conductor cable of 1.1 grade as required. 4 X 25 sq. mm | 14.00 | Sets | 198.00 | 438.00 | 6132.00 | 345.00 | 4830.00 | 200.00 | 2800.00 | 935.00 | 13090.00 | 500.00 | 7000.00 | 200.00 | 2800.00 | 100.00 | 1400.00 | 1400.00 | RANJIT SALES CORPORATION
12.30 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/ XLPE aluminium conductor cable of 1.1 grade as required. 2 core x 10 Sq mm | 14.00 | Sets | 155.00 | 313.00 | 4382.00 | 230.00 | 3220.00 | 120.00 | 1680.00 | 1339.00 | 18746.00 | 500.00 | 7000.00 | 150.00 | 2100.00 | 100.00 | 1400.00 | 1400.00 | RANJIT SALES CORPORATION
13.00 | National Flag Mast (100Ft.) Supply ,installation ,Testing and Commissioning of 100 ft. Flag mast. Mast shaft shall be in three sections, hot dip galvanised and suitable for wind velocity as per IS 875. The shaft shall be PU painted with a coating of etch primer, primer and PU paint.The flag pole should have system for Raising Lowering of Flag. It shall have double drum winch, 6 mm dia galvanised wire rope and integral power tool for the raising and lowering of Flag. Suitable control panel shall be provided for reversing operation of Power tool motor. Also includes construction of shallow foundation with required grade concrete for the High Mast as per the soil bearing capacity at site at suitable depth with all materials & labour, LED aviation system with 3C x 2.5 Sqmm Cu armoured cable. | 1.00 | Job | 850000.00 | 385000.00 | 385000.00 | 494500.00 | 494500.00 | 737000.00 | 737000.00 | 511024.00 | 511024.00 | 575000.00 | 575000.00 | 700000.00 | 700000.00 | 400000.00 | 400000.00 | 385000.00 | ENERGYGREEN TECHNOPOWER PVT LTD
14.00 | Supply of National flag of size 20’ x 30’ in 100% Knitted Polyester(140gsm), with reinforced super-strong nylon webbing on all 3 sides & rope/toggle sleeve and UV protected colours etc as required. | 6.00 | Each | 12500.00 | 25000.00 | 150000.00 | 16100.00 | 96600.00 | 14000.00 | 84000.00 | 18049.00 | 108294.00 | 20000.00 | 120000.00 | 13000.00 | 78000.00 | 35000.00 | 210000.00 | 78000.00 | GIRI ENTERPRISES
15.00 | WDI Supply installation testing and commissiong of frangiable & illuminated wind direction indicator(WDI) confiriming to ICAO Annex 14, Volume I and suitable for operation on 230V, 50Hz, single phase,AC Supply and consist of following complete as required. (a) Minimum 4.5 mtr height Fibre-reinforced plastic(FRP) frangible lattice mast(minimum size 500mmx500mm).The frangibility shall confirm to ICAO Annex 14 & Aerodrome design manual part-6 / FAA. The color of mast shall be preferably aviation Red & White. (b) Wind sock assembly complete with slip rings, Pole, Aluminium drum, bracket for drum, bearing with rain shade, carbon brush with holder bracket and wind sock cloth of color Red & White etc. (c )Mounting arrangement & provision of sufficient LED lights fixtures to meet minimum lux level requirement as per technical specification and ICAO Standard. (d) One no. LED Aviation obstruction light having aluminium cast body and red polycarbonate dome. (e ) CI/MS outdoor Junction box with 6A DP MCB, interconnection internal wiring for lights using PVC insulated copper cond cable in suitable PVC rigid/DWC/HDPE Pipe. (f)Hinged arrangement for tilting down of mast for maintenance. (g)Providing and laying suitable cement concrete foundation with supply of grouting accessories i.e anchor bolts,frame etc for installation of WDI as per OEM recommendations. (Type test certificate complying aerodrome design manual part 6 including for maximum deflection and maximum force & maximum energy imparted with upto date amendment to be provided before despatch of materials) | 1.00 | Job | 202500.00 | 562500.00 | 562500.00 | 575000.00 | 575000.00 | 195500.00 | 195500.00 | 173185.00 | 173185.00 | 200000.00 | 200000.00 | 200000.00 | 200000.00 | 50000.00 | 50000.00 | 50000.00 | RANJIT SALES CORPORATION
16.00 | Frangible Mast SITC of tubular pole type frangible Mast of Fibre glass material (As per latest ICAO requirement and specification) of 1.2 Mtr. Length designed to with stand wind speeds as per IS 875, suitable for mounting single LED light fitting with cross arm supports (if necessary), base plate, foundation bolts, suitable cement concrete foundation and other accessories etc complete as required as per site conditions.(Type test certificate complying aerodrome design manual part 6 including clause no. 4.9.18 and 4.9.20 for maximum deflection and maximum force & maximum energy imparted with upto date amendment to be provided before despatch of materials) Note: 1) The required length (approx) & quantity of Poles shall be as below: 1.2 mtr long - 08 Nos. | 10.00 | Mtr | 13000.00 | 6875.00 | 68750.00 | 10235.00 | 102350.00 | 16000.00 | 160000.00 | 14034.00 | 140340.00 | 4400.00 | 44000.00 | 12500.00 | 125000.00 | 50000.00 | 500000.00 | 44000.00 | M/S AMAR ENTERPRISES
| Total in Figures |  |  |  |  | 5681789.00 |  | 7137843.00 |  | 5995080.00 |  | 5559821.00 |  | 5348540.00 |  | 5516360.00 |  | 5191620.00
Lowest Amount Quoted BY: RANJIT SALES CORPORATION(5191620.00)

## BOQ Summary
BOQ Summary Details Tender Title: Development of Deoghar Airport. SH SITC of Apron Flood Light High Mast and 100ft Height National Flag Mast at AAI Deoghar Airport. Tender ID: 2021_AAI_69645_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | RANJIT SALES CORPORATION | 5191620.00 | L1
| 2 | M/S AMAR ENTERPRISES | 5348540.00 | L2
| 3 | GIRI ENTERPRISES | 5516360.00 | L3
| 4 | BR Power Control and Automation Services | 5559821.00 | L4
| 5 | ENERGYGREEN TECHNOPOWER PVT LTD | 5681789.00 | L5
| 6 | jaydeep agency corporation | 5995080.00 | L6
| 7 | RVD INFRA SOLUTION PVT.LTD. | 7137843.00 | L7