## BoQ1
Government eProcurement System Created By: VIVEKANAND PRASAD MORIL Created Date/Time: 16-Mar-2021 12:13 PM Tender Title: Replacement of LT panel Feeder Pillar and associated works in Operational Area at SGRDJ International Airport Amritsar Tender ID: 2021_AAI_69677_1
Tender Inviting Authority: <Asstt. General Manager Engg (Elect)-II, Project, Airports Authority of India, Sri Guru Ram Dass Jee, International Airport, Amritsar - 143101>
Name of Work: <Replacement of LT Panel/Feeder Pillar and associated works in Operational Area at SGRDJ International Airport Amritsar.>
Contract No: <AAI/ASR/ENGG-ELECT/eNIT- 20 /2020-21>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DEEPAKELECTRICALS(GSTN-33ALUPD3531C1ZI) |  | Incotech Engineers Pvt Ltd(GSTN-19AAACI5242B1ZZ) |  | BBN ENERGY SYSTEMS PVT LTD(GSTN-06AAECB3449D1Z0) |  | Industrial Traders(GSTN-09ACJPC1773F1ZQ) |  | BR Power Control and Automation Services(GSTN-06AREPS4024K1ZP) |  | VIJAYPOWER GENERATORS LIMITED(GSTN-07AAACV0191N1Z4) |  | Brilltech Engineers Pvt. Ltd.(GSTN-NA) |  | S chowdhury and Company(GSTN-NA) |  | GLOBAL ELECTRICALS & CONTROLS PVT LTD(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying, installation, testing and commissioning of cubical type, dust & vermin proof, out door type, floor mounted electrical LT panel with IP 54 protection, suitable for 415 V,3 phase, 50 Hz AC supply system fabricated in compartmentalised design from CRCA sheet steel of 2mm thick for frame work and covers, 3mm thick detachable gland plate and front hinged door locking arrangment, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having extendable TPN Aluminum Alloy bus bars of high conductivity, DMC/ SMC bus bar supports, bottom base channel of MS section not less than 100 mm x 50 mm x 5mm thick, fabrication shall be done in transportable sections, entire panel shall have a common GI earth bar of size 25mm x 5mm at the rear with 2 Nos. earth stud, soild connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with 2.5 sq.mm. PVC insulated copper conductor cable, cable alleys, cable gland plates, arrangement for incommers, floor mounted with MS angle leg, making PCC work etc, i/c providing following switch gears:-
1.10 | INCOMER :- MCCB FP 125A, 25KA, breaking capacities shall be ICS=ICU with built in thermal magnetic release- 2 Nos
1.20 | INSTRUMENTS :- 2 Nos. digital multifunction meter including suitable rating CTs for 3 phase, 4 wire operation as per specification. 2 Sets of RYB phase LED indicating lamps controlled by 2 amp MCB.
1.30 | Bus Bars :- 150 Amps Aluminium busbar for phase and neutral - 1 Set
1.40 | OUTGOINGS :- MCCB FP 40 A, 25KA, breaking capacities shall be ICS=ICU with built in thermal magnetic release- 4 Nos 40 A TP Contactor operated with digital/analog 24 hrs Timer - 3 Nos | 9.00 | Job |  | 110000.00 | 990000.00 | 140497.00 | 1264473.00 | 125200.00 | 1126800.00 | 142000.00 | 1278000.00 | 128847.00 | 1159623.00 | 158656.00 | 1427904.00 | 126800.00 | 1141200.00 | 155000.00 | 1395000.00 | 120922.00 | 1088298.00 | 990000.00 | DEEPAKELECTRICALS
2.00 | Supplying, installation, testing and commissioning of cubical type, dust & vermin proof, out door type, floor mounted electrical LT panel with IP 54 protection, suitable for 415 V,3 phase, 50 Hz AC supply system fabricated in compartmentalised design from CRCA sheet steel of 2mm thick for frame work and covers, 3mm thick detachable gland plate and front hinged door locking arrangment, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having extendable TPN Aluminum Alloy bus bars of high conductivity, DMC/ SMC bus bar supports, bottom base channel of MS section not less than 100 mm x 50 mm x 5mm thick, fabrication shall be done in transportable sections, entire panel shall have a common GI earth bar of size 25mm x 5mm at the rear with 2 Nos. earth stud, soild connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with 2.5 sq.mm. PVC insulated copper conductor cable, cable alleys, cable gland plates, arrangement for incommers, floor mounted with MS angle leg, making PCC work etc, i/c providing following switch gears:-
2.10 | INCOMER :- MCCB FP 200A, 35KA, breaking capacities shall be ICS=ICU with built in thermal magnetic release- 2 Nos On load changeover 4P, 200 Amp- 01 No
2.20 | INSTRUMENTS :- 2 Nos. digital multifunction meter including suitable rating CTs for 3 phase, 4 wire operation as per specification. 2 Sets of RYB phase LED indicating lamps controlled by 2 amp MCB.
2.30 | Bus Bars :- 250 Amps of high conductivity electrolytic quality Aluminium busbar for phase and neutral - 1 Set
2.40 | OUTGOINGS :- MCCB FP 32 A, 35KA, breaking capacities shall be ICS=ICU with built in thermal magnetic release- 2 Nos 32 A TP Contactor operated with digital/analog 24 hrs Timer - 2 Nos MCCB FP 63 A, 35KA, breaking capacities shall be ICS=ICU with built in thermal magnetic release- 2 Nos MCCB FP 100 A, 35KA, breaking capacities shall be ICS=ICU with built in thermal magnetic release- 1 Nos | 2.00 | Job |  | 125000.00 | 250000.00 | 175074.00 | 350148.00 | 152698.00 | 305396.00 | 177000.00 | 354000.00 | 152906.00 | 305812.00 | 170000.00 | 340000.00 | 165300.00 | 330600.00 | 185000.00 | 370000.00 | 149453.00 | 298906.00 | 250000.00 | DEEPAKELECTRICALS
3.00 | Supplying, installation, testing and commissioning of cubical type, dust & vermin proof, out door type, floor mounted electrical LT panel with IP 54 protection, suitable for 415 V,3 phase, 50 Hz AC supply system fabricated in compartmentalised design from CRCA sheet steel of 2mm thick for frame work and covers, 3mm thick detachable gland plate and front hinged door locking arrangment, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having extendable TPN Aluminum Alloy bus bars of high conductivity, DMC/ SMC bus bar supports, bottom base channel of MS section not less than 100 mm x 50 mm x 5mm thick, fabrication shall be done in transportable sections, entire panel shall have a common GI earth bar of size 25mm x 5mm at the rear with 2 Nos. earth stud, soild connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with 2.5 sq.mm. PVC insulated copper conductor cable, cable alleys, cable gland plates, arrangement for incommers, floor mounted with MS angle leg, making PCC work etc, i/c providing following switch gears:-
3.10 | INCOMER :- MCCB FP 250A, 35KA, breaking capacities shall be ICS=ICU with built in thermal magnetic release- 2 Nos On load changeover 4P, 250 Amp- 01 No
3.20 | INSTRUMENTS :- 2 Nos. digital multifunction meter including suitable rating CTs for 3 phase, 4 wire operation as per specification. 2 Sets of RYB phase LED indicating lamps controlled by 2 amp MCB.
3.30 | Bus Bars :- 220 Amps of high conductivity electrolytic quality Aluminium busbar for phase and neutral - 1 Set
3.40 | OUTGOINGS :- MCCB FP 40 A, 35KA, breaking capacities shall be ICS=ICU with built in thermal magnetic release- 6 Nos MCCB FP 63 A, 35KA, breaking capacities shall be ICS=ICU with built in thermal magnetic release- 2 Nos | 4.00 | Job |  | 200000.00 | 800000.00 | 223871.00 | 895484.00 | 180461.00 | 721844.00 | 177000.00 | 708000.00 | 186833.00 | 747332.00 | 190000.00 | 760000.00 | 184300.00 | 737200.00 | 150000.00 | 600000.00 | 180456.00 | 721824.00 | 600000.00 | S chowdhury and Company
4.00 | Supplying, installation, testing and commissioning of cubical type, Suitable size not less than 1000mm X 500mm X 300mm, dust & vermin proof, out door type, floor mounted with 40x40x4mm MS angle leg of height 800mm, Feeder Pillar Panel with IP 54 protection on MS channel foundation, fabricated with 2mm thick CRCA Sheet and suitable size MS angle complete with detachable gland plate and front hinged door locking arrangment duly powder coated of approved shade as per approved drawings/SLD, requied MCB/Contracters/auto manual switch/MCB LED indicater lamp/Suitable capacity Busbar as require rating, accessories including connection, inter connection, wiring with minimum 2.5 sqmm flexible copper wire & provision for earth connection etc complete as required: i) 40A, 10 KA FP MCB incomer-01 No., ii) Control system for Raising/ Lowering of Mast light with available 3 phase moter upto 2 hp capacity in existing High Mast-01 No. ii) 32A TP contactors operated through 24 hrs timer switch for automatic switching of luminaries along with Auto/Manual selector switch -01 iii) 32 A, 10 KA, TPN MCB- 02 nos, 16A, 10KA, SP-2 Nos, to feed the luminaries & aviation light. iv) LED type indicating lamps with toggle switches. v) Suitable capacity overload relay & single phase preventer for moter protection | 18.00 | Job |  | 75000.00 | 1350000.00 | 26916.00 | 484488.00 | 26555.00 | 477990.00 | 29500.00 | 531000.00 | 42527.00 | 765486.00 | 50000.00 | 900000.00 | 93900.00 | 1690200.00 | 23000.00 | 414000.00 | 27707.00 | 498726.00 | 414000.00 | S chowdhury and Company
5.00 | Supplying, installation, testing and commissioning of cubical type, dust & vermin proof, out door type, floor mounted electrical Feeder Pillar with IP 54 protection, suitable for 415 V,3 phase, 50 Hz AC supply system fabricated in compartmentalised design from CRCA sheet steel of 2mm thick for frame work and covers, 3mm thick detachable gland plate and front hinged door locking arrangment, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having extendable TPN Aluminum Alloy bus bars of high conductivity, DMC/ SMC bus bar supports, bottom base channel of MS section not less than 40 mm x 40 mm x 4 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common GI earth bar of size 25mm x 5mm at the rear with 2 Nos. earth stud, cable gland plates of 3mm, floor mounted with MS angle leg, making PCC work etc. Bus Bar:- 200 Amps of high conductivity electrolytic quality Aluminium busbar for three phase and neutral - 1 Set | 4.00 | Job |  | 25000.00 | 100000.00 | 10886.00 | 43544.00 | 4972.00 | 19888.00 | 14400.00 | 57600.00 | 9067.00 | 36268.00 | 20000.00 | 80000.00 | 44800.00 | 179200.00 | 25000.00 | 100000.00 | 4635.00 | 18540.00 | 18540.00 | GLOBAL ELECTRICALS & CONTROLS PVT LTD
6.00 | Dismentaling & shifting of existing old LT Panel inside operational area including disconnection of all connected cable, digging out the existing surviceable connected cable by taking necessary care, power supply, including shifting to the AAI store or at desire location ouside operational area etc complete as required. | 17.00 | Job |  | 3500.00 | 59500.00 | 3450.00 | 58650.00 | 4000.00 | 68000.00 | 2400.00 | 40800.00 | 1250.00 | 21250.00 | 5000.00 | 85000.00 | 8400.00 | 142800.00 | 5000.00 | 85000.00 | 3090.00 | 52530.00 | 21250.00 | BR Power Control and Automation Services
7.00 | Dismentaling & shifting of existing old High Mast control Panel inside operational area including disconnection of all connected cable, digging out the existing surviceable connected cable by taking necessary care, power supply, including shifting to the AAI store or at desire location outside operational etc complete as required. | 18.00 | Job |  | 3500.00 | 63000.00 | 2300.00 | 41400.00 | 3900.00 | 70200.00 | 2360.00 | 42480.00 | 625.00 | 11250.00 | 3000.00 | 54000.00 | 5600.00 | 100800.00 | 5000.00 | 90000.00 | 824.00 | 14832.00 | 11250.00 | BR Power Control and Automation Services
8.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
8.10 | 4 X 10 sq. mm (25mm) | 12.00 | Job |  | 200.00 | 2400.00 | 306.00 | 3672.00 | 722.00 | 8664.00 | 600.00 | 7200.00 | 242.00 | 2904.00 | 200.00 | 2400.00 | 400.00 | 4800.00 | 1500.00 | 18000.00 | 220.00 | 2640.00 | 2400.00 | DEEPAKELECTRICALS, VIJAYPOWER GENERATORS LIMITED
8.20 | 4 X 16 sq. mm (28mm) | 23.00 | Job |  | 250.00 | 5750.00 | 364.00 | 8372.00 | 1014.00 | 23322.00 | 720.00 | 16560.00 | 348.00 | 8004.00 | 250.00 | 5750.00 | 500.00 | 11500.00 | 1000.00 | 23000.00 | 247.00 | 5681.00 | 5681.00 | GLOBAL ELECTRICALS & CONTROLS PVT LTD
8.30 | 3½ X 35 sq. mm (32mm) | 37.00 | Job |  | 350.00 | 12950.00 | 462.00 | 17094.00 | 1270.00 | 46990.00 | 720.00 | 26640.00 | 790.00 | 29230.00 | 300.00 | 11100.00 | 600.00 | 22200.00 | 1000.00 | 37000.00 | 495.00 | 18315.00 | 11100.00 | VIJAYPOWER GENERATORS LIMITED
8.40 | 3½ X 50 sq. mm (35mm) | 5.00 | Job |  | 450.00 | 2250.00 | 528.00 | 2640.00 | 1539.00 | 7695.00 | 720.00 | 3600.00 | 1085.00 | 5425.00 | 350.00 | 1750.00 | 900.00 | 4500.00 | 1200.00 | 6000.00 | 550.00 | 2750.00 | 1750.00 | VIJAYPOWER GENERATORS LIMITED
8.50 | 3½ X 95 sq. mm (45mm) | 2.00 | Job |  | 550.00 | 1100.00 | 731.00 | 1462.00 | 2192.00 | 4384.00 | 720.00 | 1440.00 | 640.00 | 1280.00 | 500.00 | 1000.00 | 1300.00 | 2600.00 | 1200.00 | 2400.00 | 660.00 | 1320.00 | 1000.00 | VIJAYPOWER GENERATORS LIMITED
8.60 | 3½ X 150 sq. mm (50mm) | 10.00 | Job |  | 650.00 | 6500.00 | 900.00 | 9000.00 | 2550.00 | 25500.00 | 840.00 | 8400.00 | 1060.00 | 10600.00 | 600.00 | 6000.00 | 1500.00 | 15000.00 | 1200.00 | 12000.00 | 825.00 | 8250.00 | 6000.00 | VIJAYPOWER GENERATORS LIMITED
8.70 | 3½ X 185 sq. mm (57mm) | 4.00 | Job |  | 750.00 | 3000.00 | 1067.00 | 4268.00 | 3500.00 | 14000.00 | 960.00 | 3840.00 | 1024.00 | 4096.00 | 750.00 | 3000.00 | 1700.00 | 6800.00 | 1200.00 | 4800.00 | 907.00 | 3628.00 | 3000.00 | DEEPAKELECTRICALS, VIJAYPOWER GENERATORS LIMITED
8.80 | 3½ X 240 sq. mm (62mm) | 1.00 | Job |  | 900.00 | 900.00 | 1293.00 | 1293.00 | 4332.00 | 4332.00 | 1080.00 | 1080.00 | 1474.00 | 1474.00 | 900.00 | 900.00 | 2500.00 | 2500.00 | 1200.00 | 1200.00 | 990.00 | 990.00 | 900.00 | DEEPAKELECTRICALS, VIJAYPOWER GENERATORS LIMITED
8.90 | 3½ X 400 sq. mm (82mm) | 1.00 | Job |  | 1100.00 | 1100.00 | 1690.00 | 1690.00 | 7424.00 | 7424.00 | 1200.00 | 1200.00 | 2524.00 | 2524.00 | 1000.00 | 1000.00 | 3800.00 | 3800.00 | 1200.00 | 1200.00 | 1375.00 | 1375.00 | 1000.00 | VIJAYPOWER GENERATORS LIMITED
9.00 | Supply of 45-48 W LED street light fittings including required driver, heat resistence toughened glass, IP65, pressure die cast alumunium alloy etc complete as required. (Make/Model- Wipro / LR13-611-XXX-57-XX or equivalant) | 10.00 | Nos. |  | 4500.00 | 45000.00 | 4452.00 | 44520.00 | 2700.00 | 27000.00 | 9400.00 | 94000.00 | 2559.00 | 25590.00 | 3500.00 | 35000.00 | 5900.00 | 59000.00 | 3500.00 | 35000.00 | 3850.00 | 38500.00 | 25590.00 | BR Power Control and Automation Services
10.00 | Installation, testing and commissioning of prewired LED fitting of all types complete with all mounting accessories as required for desired direction at site etc. on pole height upto 2 Mtr including wiring with 3C x 2.5 sq.mm flexible FR PVC insulated copper conductor cable from the light fixture to control box through the pole copper conductor, single core cable upto juction box fixed at pole etc.complete as required. | 10.00 | Nos. |  | 300.00 | 3000.00 | 575.00 | 5750.00 | 300.00 | 3000.00 | 360.00 | 3600.00 | 258.00 | 2580.00 | 500.00 | 5000.00 | 1800.00 | 18000.00 | 1500.00 | 15000.00 | 495.00 | 4950.00 | 2580.00 | BR Power Control and Automation Services
11.00 | Supply of tubular FRP pole of 76 mm nominal diameter of 1 Mtr length / height including 32mm dia bracket of length minimum 30 cm for fixing light fixtures, with 200 x 200 x 5mm base plate and required holes for installation with base in existing concreate foundation and bolt etc including painting with synthetic enamel paint etc complete as required as per approved drawing. | 12.00 | Nos. |  | 1800.00 | 21600.00 | 1675.00 | 20100.00 | 14125.00 | 169500.00 | 3600.00 | 43200.00 | 4443.00 | 53316.00 | 2000.00 | 24000.00 | 3900.00 | 46800.00 | 3500.00 | 42000.00 | 2200.00 | 26400.00 | 20100.00 | Incotech Engineers Pvt Ltd
12.00 | Erection of FRP pole of item no. 11 on existing cement concrete foundation with available nut & bolt including fixing etc complete as required. | 12.00 | Job |  | 250.00 | 3000.00 | 690.00 | 8280.00 | 1500.00 | 18000.00 | 600.00 | 7200.00 | 1876.00 | 22512.00 | 500.00 | 6000.00 | 4500.00 | 54000.00 | 2000.00 | 24000.00 | 165.00 | 1980.00 | 1980.00 | GLOBAL ELECTRICALS & CONTROLS PVT LTD
13.00 | Supply and fixing of Cable junction Box of size approx. 205 x 255 x 112mm, IP 66 with metric knockouts for cable entry, din channel/ connecter etc including MS clamp for fixing on pole as required assosries etc complete. (Make HENSEL, Product Code-DK2500 or similar) | 10.00 | Job |  | 850.00 | 8500.00 | 1847.00 | 18470.00 | 2084.00 | 20840.00 | 2360.00 | 23600.00 | 3662.00 | 36620.00 | 3000.00 | 30000.00 | 3100.00 | 31000.00 | 1500.00 | 15000.00 | 2200.00 | 22000.00 | 8500.00 | DEEPAKELECTRICALS
14.00 | Supply and fixing of Cable junction Box of size approx. 225 x 295 x 122mm, IP 66 with metric knockouts for cable entry, din channel/ connecter etc including MS clamp for fixing on pole as required assosries etc complete. (Make HENSEL, Product Code-DK3500G or similar) | 2.00 | Job |  | 950.00 | 1900.00 | 2386.00 | 4772.00 | 2696.00 | 5392.00 | 3000.00 | 6000.00 | 4388.00 | 8776.00 | 5000.00 | 10000.00 | 4300.00 | 8600.00 | 2500.00 | 5000.00 | 2860.00 | 5720.00 | 1900.00 | DEEPAKELECTRICALS
15.00 | Note: 1. Rate quoted shall be inclusive of any taxes, duties, Cess, fee, royalty charges etc. levied under any statute but exclusive of GST. Goods & Services Tax (GST) shall be paid to the contractor for any taxable supply/ services/works against a valid tax invoice as per terms and conditions of the contract. 2.Being execution of work in operational area , nos. of working hours might be restricted , accordingly contractor has to quote considering all these factors as per SCC .On this account, any claim for extra payment shall not be entertained.
| Total in Figures |  |  |  |  | 3731450.00 |  | 3289570.00 |  | 3176161.00 |  | 3259440.00 |  | 3261952.00 |  | 3789804.00 |  | 4613100.00 |  | 3295600.00 |  | 2838155.00
Lowest Amount Quoted BY: GLOBAL ELECTRICALS & CONTROLS PVT LTD(2838155.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of LT panel Feeder Pillar and associated works in Operational Area at SGRDJ International Airport Amritsar Tender ID: 2021_AAI_69677_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | GLOBAL ELECTRICALS & CONTROLS PVT LTD | 2838155.00 | L1
| 2 | BBN ENERGY SYSTEMS PVT LTD | 3176161.00 | L2
| 3 | Industrial Traders | 3259440.00 | L3
| 4 | BR Power Control and Automation Services | 3261952.00 | L4
| 5 | Incotech Engineers Pvt Ltd | 3289570.00 | L5
| 6 | S chowdhury and Company | 3295600.00 | L6
| 7 | DEEPAKELECTRICALS | 3731450.00 | L7
| 8 | VIJAYPOWER GENERATORS LIMITED | 3789804.00 | L8
| 9 | Brilltech Engineers Pvt. Ltd. | 4613100.00 | L9