## BoQ1
Government eProcurement System Created By: Mayank Gaur Created Date/Time: 18-Mar-2021 11:41 AM Tender Title: Replacement of 11KV 400 Amp Oil Circuit Breaker with similar capacity Vacuum Circuit Breaker at ARSR Bijwasan Tender ID: 2021_AAI_69846_1
Tender Inviting Authority: Senior Manager (Engg.-E), AAI, DATS Complex, IGI Airport, New Delhi.
Name of Work: Replacement of 11KV 400 Amp Oil Circuit Breaker with similar capacity Vacuum Circuit Breaker at ARSR Bijwasan.
Contract No: AAI/DATS/E-E/Repl.-HT-Panel/2020-21/E-NIT-08
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ECS ENGINEERING PVT LTD(GSTN-09AABCE5944P1Z1) |  | jaydeep agency corporation(GSTN-24ACIPP6157B1ZQ) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5) |  | CIS GLOBAL INFRATECH PRIVATE LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply Installation testing and commissioning of extendable type HT panel board suitable for indoor installation for use on 3 phase, 11 KV 50 Hz AC supplyearthed system having a short circuit capacity of 20KA for 3 Sec. at 11 KV comprising triple pole VCB. Panel shall be equipped with power pack back up of suitable capacity along with suitable accessories as per specifications and schematic drawing etc. Note: Plan of existing HT Panel in HT room is attached in the Tender Documents for reference. | 1.00 | Set | 1419050.00 | 1478000.00 | 1478000.00 | 1474000.00 | 1474000.00 | 1179000.00 | 1179000.00 | 1310000.00 | 1310000.00 | 1179000.00 | Awasthi Electric Works
1.01 | (Vacuum Circuit Breaker Metal Clad housing with track having 800A TP integral VCB with Electrically operated draw out type mechanism (spring charged motor - 230 VAC). Air insulated copper bus bar & chamber. Isolating plug and receptacle. Automatic safety shutter. Breaker control switch (TNC) 24 V DC closing coil 24 V DC Shunt Trip Coil Operating Counter Mechanical ON/OFF Push Buttons Manual Spring Charged Device) Incomer-1, Outgoing-2 (Current Transformer [ Indoor Single Phase Resin Cast] Incomer : 300-150/ 5-5 A Outgoing: 100-50/ 5-5 A Class 0.5 and 5p20 burden 15 VA) Incomer-3, Outgoing-6 (Potential Transformer [Single Phase Resin Cast] PT's - 11KV /√3 /110V/√ 3 of class 0.5 (100 VA) Incomer-3, Outgoing-0 11 kv, 3.15 A P.T. fuse links Incomer-3, Outgoing-0 1 - H.T. Cable box for 3C x 240 sq.mm aluminium conductor XLPE cable (11 KV earthed system). Incomer-1, Outgoing-2 Digital Multi function Meter (V, A, F, KW, KVA, KVAH, KWH, PF) Incomer-1, Outgoing-2
1.02 | (Protction relay and Accessories 3 O/c & 1 E/F Numerical Relay with inbult TCS, Incomer-1, Outgoing-2 Master Trip Relay, Incomer-1, Outgoing-2 Aux. relay for transformer Incomer-0, Outgoing-4 Antipumping Relay Incomer-1, Outgoing-2 Aux. Contactor - 2 NO + 2 NC - 24 V DC Incomer-1, Outgoing-2 Restricted Earth Fault Relay Incomer-1, Outgoing-2
1.03 | (Indication Lamp & Accessories for complete panel Indicating Lamps (22.5mm DIA), 24VDC - set of 3 Breaker ON : RED Breaker OFF : GREEN Spring Charged : BLUE VCB Trip : AMBER Trip Circuit : WHITE Indicating Lamps (22.5mm DIA), 63.5 V AC - set of 3 R' Phase Healthy - RED Y' Phase Healthy - YELLOW B' Phase Healthy - BLUE MCB Double Pole ,10kA 6A Single Pole 10kA,6A Breaker Control Swtich (TNC) 25A, Double Pole Power Pack 230V AC / 24V DC Hooter 24V DC Strip Heater 100W, 240V AC Thermostate, 0-60ºC , 240V AC Emergency Stop Button 22.5mm OD 15A 240 V AC 3 pin power socket with ON-OFF switch, 18W LED, 240V AC, bulb, 2A, Door limit switch for cubical lamp, 10A, 240V AC, Toggle switch, 32A Neutral Link, C.T. Terminal 6mm end plate for above, P.T. Terminal 6mm end plate for above) Incomer-Outgoing- 1 LOT)
2.00 | Dismantling of existing 3-phase, 11 KV 50 HZ AC supply HT panel consisting of 3 nos., 3- poles, 400 Amps Oil Circuit Breaker along with all the eletrical accessories, battery bank consisting of 12 nos., 2 V , 40 AH battaries. Including shifting of dismantled material from HT panel room to AAI store complete as required. | 1.00 | Job | 75000.00 | 8000.00 | 8000.00 | 7800.00 | 7800.00 | 25000.00 | 25000.00 | 22000.00 | 22000.00 | 7800.00 | jaydeep agency corporation
3.00 | supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable(400 sq. mm) of 11 KV grade as required : | 3.00 | Set | 13513.00 | 4110.00 | 12330.00 | 4200.00 | 12600.00 | 11000.00 | 33000.00 | 14000.00 | 42000.00 | 12330.00 | ECS ENGINEERING PVT LTD
4.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 3.00 | Set | 13256.00 | 14000.00 | 42000.00 | 9800.00 | 29400.00 | 14500.00 | 43500.00 | 20000.00 | 60000.00 | 29400.00 | jaydeep agency corporation
5.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | 10.00 | Meter | 1038.00 | 1290.00 | 12900.00 | 1290.00 | 12900.00 | 1050.00 | 10500.00 | 1200.00 | 12000.00 | 10500.00 | Awasthi Electric Works
6.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut,bolt, spring, washer excavation and re-filling etc. as required. | 15.00 | Meter | 1356.00 | 1658.00 | 24870.00 | 1580.00 | 23700.00 | 1400.00 | 21000.00 | 1200.00 | 18000.00 | 18000.00 | CIS GLOBAL INFRATECH PRIVATE LIMITED
7.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required | 30.00 | Meter | 1188.00 | 1240.00 | 37200.00 | 1250.00 | 37500.00 | 1050.00 | 31500.00 | 1200.00 | 36000.00 | 31500.00 | Awasthi Electric Works
| Total in Figures |  |  |  |  | 1615300.00 |  | 1597900.00 |  | 1343500.00 |  | 1500000.00
Lowest Amount Quoted BY: Awasthi Electric Works(1343500.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of 11KV 400 Amp Oil Circuit Breaker with similar capacity Vacuum Circuit Breaker at ARSR Bijwasan Tender ID: 2021_AAI_69846_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Awasthi Electric Works | 1343500.00 | L1
| 2 | CIS GLOBAL INFRATECH PRIVATE LIMITED | 1500000.00 | L2
| 3 | jaydeep agency corporation | 1597900.00 | L3
| 4 | ECS ENGINEERING PVT LTD | 1615300.00 | L4