## BoQ1
Government eProcurement System Created By: Keishing Honpam Created Date/Time: 05-Mar-2021 05:43 PM Tender Title: Providing Reserve Lounge and Improvement Works at Old RED Bldg., Guwahati Airport SH Electrical Works for Provision of Intelligent Addressable Fire Alarm System and Detection System and Fire Hydrant system. Tender ID: 2021_AAI_70100_1
Tender Inviting Authority: Airports Authority of India
Name of Work: Providing Reserve Lounge and Improvement Works at Old RED Bldg., Guwahati Airport (SH: Electrical Works for Provision of Intelligent Addressable Fire Alarm & Detection System and Fire Hydrant System)
Tender ID: 2021_AAI_70100_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | GLYPTIC(GSTN-19AAMFG0478J1ZY) |  | DOGRA AND DOGRA ENTERPRISES(GSTN-07AIFPD1861P2Z1) |  | COOLTEK INDIA(GSTN-19ADXPB3581D1ZC) |  | PRUDENT EPC PRIVATE LIMITED(GSTN-27AAKCP4656L1ZS) |  | Globe Detective Agency Pvt. Ltd.(GSTN-19AAACG1108N1ZN) |  | SHIMMER ENTERPRISE(GSTN-18ACKPB9483G1ZA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH: I FIRE ALARM & DETECTION SYSTEM
1.10 | Supply, Installation, Testing &Commissioning of UL /EN listed (latest version) Modular Microprocessor based expandable intellegent Addressable Type Fire Alarm Control Panel of 3 (three) loop, with minimum 320 character graphics / LCD display with touch screen or other keypad and minimum 4000 events history log in the nonvolatile memory (EPROM), The panel should be equipped with loop capacity to take minimum 240 intelligent addressable detectors/ devices (In any combination) in one loop. Four access levels, capable of taking Protocol Devices, Graphical Display, sufficient numbers of programmable relay controls for controlling ventilation fan, fire pump room, monitoring of fire sprinkler and fire hydrant pump, 230 volts, 50 Hz AC power supply, automatic battery charger, 24 volts sealed maintenance free lead acid batteries sufficient for 2 hours normal working and then be capable of operating the system for 30 minutes during an emergency / fault conditions along with battery stand as required. The panel shall have facility for seamless integration with PA system (For Giving trigger Signal to start pre-recorded Digital Voice Evacuation from PA system in case of fire). The panel shall be compatible for Building Management System with open protocol BACNET / MODBUS etc. as per specification, complete as required. | 1.00 | Each | 0.00 | 297830.00 | 297830.00 | 144000.00 | 144000.00 | 196547.00 | 196547.00 | 249375.00 | 249375.00 | 286500.00 | 286500.00 | 272700.00 | 272700.00 | 144000.00 | DOGRA AND DOGRA ENTERPRISES
1.20 | Supply, Installation, Testing & commissioning of UL / EN listed (latest version) intelligent addressable multi criteria detector {Smoke + heat } with inbuilt fault isolator / isolator base and with unique optical sensing chamber, visible LED, fully coated circuit board, superior RF / Transient protection suitable for 2 wires loop connection, complete with plug into common separate base & housing constructed of LEXAN (or polycarbonate) complete with connections etc. as required and to be installed below / above false ceiling roof and concealed space and as per enclosed specifications ,complete as required. (Cost of plug in common base shall deemed to be included in cost of detectors) | 386.00 | Each | 0.00 | 2703.00 | 1043358.00 | 2800.00 | 1080800.00 | 2492.00 | 961912.00 | 3206.00 | 1237516.00 | 1858.00 | 717188.00 | 2659.00 | 1026374.00 | 717188.00 | Globe Detective Agency Pvt. Ltd.
1.30 | Supply, installation, testing and commissioning of UL / EN listed (Latest Version) intelligent Addressable type Heat Detector (Fixed cum-rate of rise type) with inbuilt fault isolator / isolator base with max. triggering temperature programable from 58 degree C to 69 degree C complete with all fixing accessories like base, base box, self adhesive sticker indicating loop number and address etc. to be installed below / above false ceiling, roof and concealed space, etc. interconnecting to loop cable, etc. as per specification complete as required. | 18.00 | Each | 0.00 | 1963.00 | 35334.00 | 2400.00 | 43200.00 | 2260.00 | 40680.00 | 3206.00 | 57708.00 | 1850.00 | 33300.00 | 2659.00 | 47862.00 | 33300.00 | Globe Detective Agency Pvt. Ltd.
1.40 | Supply, installation, testing and commissioning of UL / EN listed (latest version) Intelligent addressable Control Module/ Relay Module (output module) with inbuilt fault isolator / isolator module for tripping of AHU & Ventilation / pressurization fans / hooter complete with termination etc. complete as required and as per enclosed specifications | 6.00 | Each | 0.00 | 3958.00 | 23748.00 | 3700.00 | 22200.00 | 4365.00 | 26190.00 | 3206.00 | 19236.00 | 3080.00 | 18480.00 | 3977.00 | 23862.00 | 18480.00 | Globe Detective Agency Pvt. Ltd.
1.50 | Supply, installation, testing and commissioning of UL /EN listed (Latest Version) Response Indicators for getting fire indications of detectors i/c mounting boxes installed above false ceiling area interconnecting to loop cable etc. as per specification complete as required. | 22.00 | Each | 0.00 | 239.00 | 5258.00 | 650.00 | 14300.00 | 155.00 | 3410.00 | 285.00 | 6270.00 | 115.00 | 2530.00 | 1042.00 | 22924.00 | 2530.00 | Globe Detective Agency Pvt. Ltd.
1.60 | Supply, Installation, Testing & commissioning of UL / EN listed (latest version) intelligent addressable Manual call station (Resettable pull / push type) suitable for semi flus mounting, IP 54 for indoor use & IP 65 for outdoor use with inbuilt fault isolator / isolator module with double gang outlet box, equipment for key operated test reset lock, electronic or rotary switches for address setting. Manual pull station shall be connected with two wire to SLC loop of Fire Control Panel. Cover shall be made out of LEXAN (or polycarbonate equivalent) with clear operating instruction and the word Fire appearing on the front complete with connections etc. as required and as per enclosed specifications. | 12.00 | Each | 0.00 | 4028.00 | 48336.00 | 3300.00 | 39600.00 | 4200.00 | 50400.00 | 4132.50 | 49590.00 | 3110.00 | 37320.00 | 4528.00 | 54336.00 | 37320.00 | Globe Detective Agency Pvt. Ltd.
1.70 | Supply, installation, testing and commissioning of UL / EN listed (latest version) loop powered addressable Hooter-cum- strobe with inbuilt fault isolator / isolator module with adjustable sound level in the range of min. 90 db to Max. 120 db at 1M distance complete with termination etc. as required and as per enclosed specification. | 9.00 | Each | 0.00 | 8856.00 | 79704.00 | 6300.00 | 56700.00 | 4626.00 | 41634.00 | 3277.50 | 29497.50 | 2150.00 | 19350.00 | 5648.00 | 50832.00 | 19350.00 | Globe Detective Agency Pvt. Ltd.
1.80 | Providing, installation, testing & commissioning of UL / EN listed (Latest Version) Monitor Module / input module with inbuilt fault isolator / isolator module (for monitoring different electrical / mechanical device etc.) as per specifications. | 3.00 | Each | 0.00 | 2584.00 | 7752.00 | 3500.00 | 10500.00 | 2850.00 | 8550.00 | 3206.00 | 9618.00 | 2790.00 | 8370.00 | 3750.00 | 11250.00 | 7752.00 | GLYPTIC
1.90 | Supplying & drawing of 2 x 1.5 sqmm FRLS unarmored cable, 600 / 1000V rated with annealed copper conductor as per applicable IS standared complete in existing surface / recessed steel / PVC conduit as required. | 1690.00 | Meter | 0.00 | 106.00 | 179140.00 | 141.00 | 238290.00 | 105.00 | 177450.00 | 127.00 | 214630.00 | 109.00 | 184210.00 | 118.00 | 199420.00 | 177450.00 | COOLTEK INDIA
2.00 | SH:II FIRE HYDRANT SYSTEM
2.10 | Providing laying, testing & commissioning of 'C' class heavy duty MS Pipe conforming to IS 1239/3589 i/c fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. in ground including welding, excavation & providing cement concrete blocks as supports, anticorrosive treatment with coaltar/asphalt tape as per IS 10221, refilling the trench etc. of following sizes complete as required. (a). 150 mm. Dia | 150.00 | Meter | 0.00 | 2238.00 | 335700.00 | 2400.00 | 360000.00 | 2850.00 | 427500.00 | 3411.00 | 511650.00 | 3700.00 | 555000.00 | 2944.00 | 441600.00 | 335700.00 | GLYPTIC
2.20 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : (a). 50 mm dia | 164.00 | Meter | 0.00 | 696.00 | 114144.00 | 1050.00 | 172200.00 | 743.00 | 121852.00 | 1151.00 | 188764.00 | 1300.00 | 213200.00 | 902.00 | 147928.00 | 114144.00 | GLYPTIC
2.30 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : (a). 80 mm dia | 78.00 | Meter | 0.00 | 1104.00 | 86112.00 | 1400.00 | 109200.00 | 1188.00 | 92664.00 | 1766.00 | 137748.00 | 2050.00 | 159900.00 | 1535.00 | 119730.00 | 86112.00 | GLYPTIC
2.40 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : (a). 100 mm dia | 38.00 | Meter | 0.00 | 1540.00 | 58520.00 | 1600.00 | 60800.00 | 1740.00 | 66120.00 | 2320.00 | 88160.00 | 2700.00 | 102600.00 | 1780.00 | 67640.00 | 58520.00 | GLYPTIC
2.50 | Supplying and fixing single headed internal hydrant valve with instantaneous Gunmetal/Stainless Steel coupling of 63 mm dia with cast iron wheel ISI marked conforming to IS 5290 (Type -A) with blank Gunmetal/Stainless Steel cap and chain as required : (a) Single headed Gunmetal | 3.00 | Set | 0.00 | 5170.00 | 15510.00 | 7500.00 | 22500.00 | 5250.00 | 15750.00 | 8978.00 | 26934.00 | 12500.00 | 37500.00 | 5975.00 | 17925.00 | 15510.00 | GLYPTIC
2.60 | Supplying and fixing Single headed external yard hydrant valve with 1 No. 63 mm dia instantaneous FM Gunmetal/Stainless Steel coupling and cast iron wheel, ISI marked, conforming to IS 5290 (type A) with blank Gunmetal/Stainless Steel cap and chain as required : (a) Single headed Gunmetal | 2.00 | Set | 0.00 | 5170.00 | 10340.00 | 7500.00 | 15000.00 | 5250.00 | 10500.00 | 8978.00 | 17956.00 | 12500.00 | 25000.00 | 5975.00 | 11950.00 | 10340.00 | GLYPTIC
2.70 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with bronze / gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required : (a). 50 mm dia | 3.00 | Set | 0.00 | 2670.00 | 8010.00 | 1300.00 | 3900.00 | 1682.00 | 5046.00 | 2431.00 | 7293.00 | 7500.00 | 22500.00 | 2970.00 | 8910.00 | 3900.00 | DOGRA AND DOGRA ENTERPRISES
2.80 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with bronze / gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required : (a) 100 mm dia | 3.00 | Set | 0.00 | 4050.00 | 12150.00 | 3100.00 | 9300.00 | 2989.00 | 8967.00 | 3636.00 | 10908.00 | 12900.00 | 38700.00 | 5482.00 | 16446.00 | 8967.00 | COOLTEK INDIA
2.90 | Supplying, fixing, testing & commissioning of double flanged sluice valve of rating PN 1.6 with non rising spindle, bronze/gun metal seat, ISI marked complete with nuts, bolts, washers, gaskets and conforming to IS 780 of following sizes as required: (a) 150mm dia | 1.00 | Set | 0.00 | 13233.00 | 13233.00 | 4500.00 | 4500.00 | 15075.00 | 15075.00 | 20061.00 | 20061.00 | 32600.00 | 32600.00 | 17580.00 | 17580.00 | 4500.00 | DOGRA AND DOGRA ENTERPRISES
3.00 | Providing, installation, testing and commissioning of non-return valve of following sizes confirming to IS: 5312 complete with rubber gasket, GI bolts, nuts, washers etc.as required : (a) 100mm dia | 2.00 | Set | 0.00 | 15348.00 | 30696.00 | 3500.00 | 7000.00 | 10190.00 | 20380.00 | 9915.00 | 19830.00 | 13750.00 | 27500.00 | 10772.00 | 21544.00 | 7000.00 | DOGRA AND DOGRA ENTERPRISES
3.10 | Supplying and fixing 63 mm dia, 15 m long RRL hose pipe with 63 mm dia male and female couplings duly bound with GI wire, rivets etc. conforming to IS 636 (type-A) as required : (a) Gun Metal | 10.00 | Set | 0.00 | 5150.00 | 51500.00 | 4900.00 | 49000.00 | 4525.00 | 45250.00 | 4631.00 | 46310.00 | 8900.00 | 89000.00 | 5435.00 | 54350.00 | 45250.00 | COOLTEK INDIA
3.20 | Supplying and fixing first-aid Hose Reel with MS construction spray painted in post office red, conforming to IS 884 complete with the following as required.20 mm nominal internal dia water hose thermoplastic (Textile reinforced) type -2 as per IS .:20 mm nominal internal dia water hose thermoplastic (Textile reinforced) type -2 as per IS:12585 20 mm nominal internal dia gun metal globe valve & nozzle. Drum and brackets for fixing the equipmets on wall. Connections from riser with 25 mm dia stop gun metal valve & M.S. Pipe and socket: (a) 30 m | 3.00 | Set | 0.00 | 6725.00 | 20175.00 | 10500.00 | 31500.00 | 6500.00 | 19500.00 | 8977.00 | 26931.00 | 12500.00 | 37500.00 | 9850.00 | 29550.00 | 19500.00 | COOLTEK INDIA
3.30 | Supplying & fixing 63 mm dia gun metal short branch pipe with 20 mm nominal internal diameter size nozzle conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling as required : (a) Gun metal | 5.00 | Each | 0.00 | 2235.00 | 11175.00 | 2100.00 | 10500.00 | 1875.00 | 9375.00 | 2710.00 | 13550.00 | 3500.00 | 17500.00 | 2075.00 | 10375.00 | 9375.00 | COOLTEK INDIA
3.40 | Supplying and fixing of fire brigade connection of cast iron body with gun metal male instantaneous inlet couplings complete with cap and chain as reqd. for suitable dia MS pipe connection conforming to IS 904 as required : (a) 2 way-100 mm dia M.S. Pipe | 1.00 | Set | 0.00 | 4575.00 | 4575.00 | 3200.00 | 3200.00 | 3500.00 | 3500.00 | 7980.00 | 7980.00 | 15000.00 | 15000.00 | 7800.00 | 7800.00 | 3200.00 | DOGRA AND DOGRA ENTERPRISES
3.50 | Supplying and fixing air vessel made of 250 mm dia, 8 mm thick MS sheet, 1200 mm in height with air release valve on top and flanged connection to riser, drain arrangement with25 mm dia gun metal wheel valve with required accessories, pressure gauge and painting with synthetic enamel paint of approved shade as required. | 1.00 | Set | 0.00 | 5870.00 | 5870.00 | 15000.00 | 15000.00 | 18500.00 | 18500.00 | 23512.00 | 23512.00 | 34800.00 | 34800.00 | 25365.00 | 25365.00 | 5870.00 | GLYPTIC
3.60 | Supply and fixing of weather proof cabinet to enclose 2 nos of RRL hose pipes and 1 no of short branch pipe for both indoor and outdoor use. Size: 1000mm X 1200mm X 300mmD | 5.00 | Each | 0.00 | 8392.00 | 41960.00 | 7500.00 | 37500.00 | 4800.00 | 24000.00 | 5273.00 | 26365.00 | 7980.00 | 39900.00 | 15600.00 | 78000.00 | 24000.00 | COOLTEK INDIA
4.00 | SH:III FIRE EXTINGUISHER
4.10 | Supply, installation, testing and commissioning ISI marked (IS:15683) Fire Extinguisher, Carbon-di-oxide type capacity 4.5 Kg. Flat base including valve, discharge hose of not less than 10 mm dia, 1M long and complete in all respects including initial fill with CO2 gas conforming to IS:307-1966 and walll suspension braket complete as required & as per specifications. | 9.00 | Each | 0.00 | 5425.00 | 48825.00 | 6500.00 | 58500.00 | 5500.00 | 49500.00 | 5900.00 | 53100.00 | 5900.00 | 53100.00 | 6068.00 | 54612.00 | 48825.00 | GLYPTIC
4.20 | Supply, installation, testing and commissioning ISI marked (IS:15683) portable fire extinguisher, water (gas pressure) type capacity 9 kg with gun metal cap and nozzle and complete in all respects including initial fill and wall suspension brackets complete as required & as per specifications. | 9.00 | Each | 0.00 | 2000.00 | 18000.00 | 2700.00 | 24300.00 | 2329.00 | 20961.00 | 4845.00 | 43605.00 | 4150.00 | 37350.00 | 3348.00 | 30132.00 | 18000.00 | GLYPTIC
4.30 | Supply, installation, testing and commissioning of 6kg ABC (Powder Type) Fire Extinguisher, Mild Steel Cylinders ISI marked fitted with pressure indicating gauge, internal tube, squeeze lever type valve fully charged with ABC 90 powder (Mono Ammonium Phosphate) pressured by Nitrogen complete in all respects including wall suspensionbracket complete and conforming to IS:15683 as required and as per specifications. | 18.00 | Each | 0.00 | 2268.00 | 40824.00 | 2900.00 | 52200.00 | 2523.00 | 45414.00 | 3063.00 | 55134.00 | 2850.00 | 51300.00 | 3274.00 | 58932.00 | 40824.00 | GLYPTIC
| Total in Figures |  |  |  |  | 2647779.00 |  | 2695690.00 |  | 2526627.00 |  | 3199231.50 |  | 2897198.00 |  | 2929929.00
Lowest Amount Quoted BY: COOLTEK INDIA(2526627.00)

## BOQ Summary
BOQ Summary Details Tender Title: Providing Reserve Lounge and Improvement Works at Old RED Bldg., Guwahati Airport SH Electrical Works for Provision of Intelligent Addressable Fire Alarm System and Detection System and Fire Hydrant system. Tender ID: 2021_AAI_70100_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | COOLTEK INDIA | 2526627.00 | L1
| 2 | GLYPTIC | 2647779.00 | L2
| 3 | DOGRA AND DOGRA ENTERPRISES | 2695690.00 | L3
| 4 | Globe Detective Agency Pvt. Ltd. | 2897198.00 | L4
| 5 | SHIMMER ENTERPRISE | 2929929.00 | L5
| 6 | PRUDENT EPC PRIVATE LIMITED | 3199231.50 | L6