## BoQ1
Government eProcurement System Created By: Nirad Patra Created Date/Time: 03-Jun-2021 12:51 PM Tender Title: Provision of 11 KV Substation and allied works at CCR building Tender ID: 2021_AAI_70108_1
Tender Inviting Authority: Asst. General Manager Engg (E)-II, Airports Authority of India, B.P.I.Airport, Bhubaneswar.
Name of Work: Construction of ATC Tower cum Technical Block, Fire Station and E&M Workshop at B. P. I. Airport, Bhubaneswar. S.H. :-Provision of 11 KV Substation and allied works at CCR building.
Contract No: 2021_AAI_70108_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Power And Instrumentation Guj Ltd(GSTN-24AACCP4292Q1ZW) |  | TECHNISYS ENGINEERING PRIVATE LIMITED(GSTN-06AACCT8886E1ZZ) |  | SYSTEM HOUSE CORPORATION(GSTN-21AAOFS9357C1Z2) |  | SHIVRAM ELECTRICALS(GSTN-24AGPPP8489B2ZV) |  | JITENDRA ELECTRICALS(GSTN-24AACFJ9752E1ZE) |  | Incotech Engineers Pvt Ltd(GSTN-19AAACI5242B1ZZ) |  | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION(GSTN-09AOTPS2578C1ZC) |  | HITECH ERECTORS PVT. LTD.(GSTN-07AAACH0859B1Z0) |  | GIRI ENTERPRISES(GSTN-20ACEPG3920H1ZA) |  | EVERCREST PROJECTS PVT LTD(GSTN-24AADCE7826L1ZE) |  | Shekhawati Electrical Engineers(GSTN-08AGWPS9218G2ZK) |  | Mars Developments(GSTN-19ACTPJ8300R1ZQ) |  | K B CONTRACT (P) LTD(GSTN-07AADCK6091P1ZX) |  | CREATIVE ENTREPRENEURS LLP(GSTN-07AAGFC0083M1ZE) |  | shiv electric(GSTN-07AACFS2722H1ZF) |  | MAHADEV ENTERPRISE(GSTN-NA) |  | Brilltech Engineers Pvt. Ltd.(GSTN-NA) |  | RN Electro Power Pvt. Ltd.(GSTN-NA) |  | GAYATRI AGENCY(GSTN-NA) |  | AT AND T ENGINEERS PVT LTD(GSTN-NA) |  | Bhanwariya Infra Projects Pvt Ltd(GSTN-NA) |  | JAI ENTERPRISES(GSTN-NA) |  | STERLINGELECTRO(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | H.T. PANEL BOARD 11KV H.T. (04) BREAKER SWITCH BOARD PANEL Supplying, installation, testing & commissioning of indoor type floor mounted metal clad, 11 KV VCB panel with 04 nos. VCBs(single panel), totally enclosed with electrical and mechanical interlocking system for both the incomers, trolley mounted(additional VCB handling trolley will not be acceptable), horizontal draw out type breaker as per IS:13118 & IEC 62271-200/100, as amended up to date and additional specifications, having capacities as mentioned below, single break, trip free mechanism, electrical as well as manually charged and electrical closing breaker system suitable for use on 11 KV, 3 Phase, 50Hz A.C. supply with short circuit fault level of 25KA for 3 sec with rated voltage 12KV & rated current 630Amp, complete with self contained, fully interlocked, rack in and rack out mechanism, air insulated but encapsulated copper bus bars of 800 Amps capacity, breaker featured with mechanical ON/OFF indicator with hand trip device, spring release coil, shunt trip coil and auxiliary switch of 6 NO + 6 NC and equipped with following switchgears and accessories i/c connections suitable for 3 X 185/300 sqmm. XLPE 11KV cable (cable entry from bottom), end termination with heat shrinkable jointing material etc. as required. (Note-Cost of end termination not included in this item) as per technical specification and site condition etc as required as per direction of E-I-C.(Note:-Closing Coil -24V/110V DC, Tripping coil - 24V/110V DC , spring charging motor with 230V AC contactor 06 NO + 06 NC with test & service limit switch Actuator.) along with RS-485 or equivalent communication protocol in numeric relay as per tender spcification, as per site requirement and as per direction of Engineering In-Charge(Five years warranty certificate should be given from OEM for complete HT Panel).
1.01 | A) INCOMER - 2 nos. Min 800 Amp. VCB Each incomer will have the following:- i 1 no. 11 KV, PT Class 0.5 accuracy and 100 VA burden with 1 no. digital Voltmeter (0-15KV), selector switch for voltmeter and protection MCB for HT metering . ii 1 no. (0-400A) dual scale ~ammeter, digital type, selector switches for ammeters. iii Potential Transformer, Single Phase(03 Nos.) Cast Rasin, Draw Out type mounted below VCB, PTR:11KV/V3/110V/V3, 100VA, OVF 1.2 Const & 1.9 for 8 hours. iv 1 no. microprocessor based numerical relay with OIL, EIF , SIC protection, UVOV Protection, Flush Mounted with RS-485 Connector. v 1 no. set of dual core dual ratio 3 CT's 400/200/5/5A of 15 VA burden and accuracy Class-0.5 for Metering and class 5 P10 for protection. vi Multifunction digital meter to read A,V,KVA,KW,KVAR,KVAH,KAVARH,HZ,PF, CTR-5A, PTR-24VAC with RS 485 Port vii LED type phase indications lamps for R,Y,B, Breaker ON,OFF,TRIP, Trip circuit healthy, spring charge DC ON(110V AC) etc. viii Electrical & Mechanical interlocking arrangement among 2 nos. Incomers B OUTGOING - 02 (TWO) nos. 800 Amp. VCB Each outgoing will have the following:- i (1 no. (0-400 A) Ammeters, dual scale digital type & selector switches for Ammeters. ii 1 no. microprocessor based numerical relay with OIL, E/F and S/C protection. iii 1 no. of dual core dual ratio 3 CTs 100/50/5/5 A of 7.5VA burden and accuracy Class-0.5 for metering and class 5P10 for protection. iv Multifunction digital meter to read A,V,KVA,KW,KVAR,KVAH,KAVARH,HZ,PF etc. v LED type indications lamps for Breaker ON,OFF,TRIP, Trip circuit healthy, spring charge etc. vi All metering and protection devices, interconnections, necessary control wiring and all other accessories shall be provided as per Technical specifications & technical particulars. vii Trip circuit supervision Relay, Aux. Supply-24VDC-Flush mounted. viii Master Trip Relay, Aux Supply-24VDC-Flush Mounted. ix 10A, 2P DC supply ON/OFF Switch. x 10A, 2P AC supply ON/OFF Switch xi 10A, 2P Local/ Remote Selector Switch xii 25A, 220V DC, 1P, Trip Neutral Close(TNC) switch, Spring return xiii Space Heater (02 Nos.) with thermostat, 230V AC xiv Panel Illumination Lamp, LED type, 230V AC xv Buzzer, 230V AC xvi 4A MCB for PT Secondary-03 Nos, 2A MCB for Lamp circuit 24V DC-02 Nos.,6A MCB for Spring charging meter 230V AC-02 Nos., 16A MCB for plug point, space heater etc.-01 No, Neutral Link-02 Nos. xvii Announciator for each incoming and out going feeder VCB | 1.00 | Job |  | 2183625.00 | 2183625.00 | 1681099.00 | 1681099.00 | 2300000.00 | 2300000.00 | 2457000.00 | 2457000.00 | 1290000.00 | 1290000.00 | 1566750.00 | 1566750.00 | 2850000.00 | 2850000.00 | 2991937.50 | 2991937.50 | 2591971.00 | 2591971.00 | 1794480.00 | 1794480.00 | 1825000.00 | 1825000.00 | 1982400.00 | 1982400.00 | 2052000.00 | 2052000.00 | 1800000.00 | 1800000.00 | 1500000.00 | 1500000.00 | 1400000.00 | 1400000.00 | 1944000.00 | 1944000.00 | 1788963.00 | 1788963.00 | 2550000.00 | 2550000.00 | 1840320.00 | 1840320.00 | 3224571.75 | 3224571.75 | 1787500.00 | 1787500.00 | 2312588.00 | 2312588.00 | 1290000.00 | JITENDRA ELECTRICALS
2.00 | BATTERIES & BATTERY CHARGER Supply, installation, testing and commissioning of 36 V Battery Charger & 18 (Eighteen) numbers of 2V 100 AH Valve Regulated Lead Acid (VRLA) batteries, Battery Charger shall be solid state, full wave fully controlled bridge, input suitable for single phase 230V +I- 10% AC supply, conforming to degree of protection IP-42, Sheet steel enclosure 1.6mm thick, with automatic voltage regulation, current limiting circuit, auto cut facility, smooth filter circuit switches, digital Ammeter & voltmeter on DC side, phase indicating lamps (LED type) on AC side complete in all respect with switchgear, earthing, powder coated painting etc as required. The battery charger shall have electronic health module which will monitor and indicate the health of connected batteries regularly. Suitable Iron angle stand for 18nos. 2V, battery bank shall be provided as per tender specification. | 1.00 | Job |  | 431622.00 | 431622.00 | 491509.00 | 491509.00 | 350000.00 | 350000.00 | 325000.00 | 325000.00 | 310000.00 | 310000.00 | 177368.00 | 177368.00 | 220000.00 | 220000.00 | 529200.00 | 529200.00 | 280000.00 | 280000.00 | 328320.00 | 328320.00 | 50000.00 | 50000.00 | 129600.00 | 129600.00 | 315000.00 | 315000.00 | 250000.00 | 250000.00 | 150000.00 | 150000.00 | 400000.00 | 400000.00 | 246620.00 | 246620.00 | 312870.00 | 312870.00 | 280000.00 | 280000.00 | 236780.00 | 236780.00 | 578974.50 | 578974.50 | 682500.00 | 682500.00 | 701793.00 | 701793.00 | 50000.00 | Shekhawati Electrical Engineers
3.00 | TRANSFORMER 11KV/0.433KV INDOOR TYPE TRANSFORMER Supply, installation, testing and commissioning of indoor type, 11/0.433 KV, min 1000KVA, 3Ph, 50 Hz, vector group Dyn-11,OIL COOL type, copper wound Transformer with off load tap changer on HV side to cater to voltage variation range of +7.5% to -7.5% in steps of 2.5%, suitable HV cable termination boxes on both sides (suitable for 11KV, 3 core x 400Sq.mm. XLPE cable on HT side and 3200 Amp TPN Busduct connection arrangement on LT side), complete with standard fittings, accessories and first filling of filtered dehydrated oil as per IS:1180 level 2 BIS with up to date ammendments, including required transformer oil, oil temperature. indicator, winding temperature indicator, bucholz relay, marshalling box etc and as per Technical Specifications as per technical specification and site condition etc as required as per direction of E-I-C. | 2.00 | Job |  | 2081362.00 | 4162724.00 | 1755811.00 | 3511622.00 | 1750000.00 | 3500000.00 | 1975000.00 | 3950000.00 | 1540000.00 | 3080000.00 | 1571476.00 | 3142952.00 | 2650000.00 | 5300000.00 | 2025000.00 | 4050000.00 | 1725000.00 | 3450000.00 | 1689900.00 | 3379800.00 | 1525000.00 | 3050000.00 | 2023200.00 | 4046400.00 | 2016000.00 | 4032000.00 | 1700000.00 | 3400000.00 | 1820000.00 | 3640000.00 | 1800000.00 | 3600000.00 | 1811300.00 | 3622600.00 | 1781022.00 | 3562044.00 | 1800000.00 | 3600000.00 | 1759325.00 | 3518650.00 | 1802010.50 | 3604021.00 | 2197000.00 | 4394000.00 | 2080045.00 | 4160090.00 | 3050000.00 | Shekhawati Electrical Engineers
4.00 | HT CABLE SUPPLY OF HT CABLE Supply of following sizes of XLPE insulated PVC sheathed aluminium conductor armoured power cable of following KV grade conforming to IS : 7098 ( Part-11) amended up to date.
4.01 | I) 3 Core, 300 Sq.mm. (11KV UE grade) | 2200.00 | Mtr |  | 1698.00 | 3735600.00 | 1484.00 | 3264800.00 | 1500.00 | 3300000.00 | 1775.00 | 3905000.00 | 1240.00 | 2728000.00 | 1364.00 | 3000800.00 | 1650.00 | 3630000.00 | 1890.00 | 4158000.00 | 1414.00 | 3110800.00 | 1478.00 | 3251600.00 | 1700.00 | 3740000.00 | 1540.00 | 3388000.00 | 1350.00 | 2970000.00 | 2900.00 | 6380000.00 | 1460.00 | 3212000.00 | 2500.00 | 5500000.00 | 1381.00 | 3038200.00 | 1822.00 | 4008400.00 | 1550.00 | 3410000.00 | 1477.00 | 3249400.00 | 1418.04 | 3119688.00 | 1913.60 | 4209920.00 | 1734.00 | 3814800.00 | 2728000.00 | JITENDRA ELECTRICALS
5.00 | HT CABLE END TERMINATION Supplying & making indoor cable end termination with heat shrinkable jointing kit complete with all accessories, including lugs suitable for following size of 3 core XLPE aluminium conductor cable of 11 KV grade complete as required.For 3 Core 300 Sq.mm cable
5.01 | 3 Core, 300 Sq.mm. (11KV UE grade) | 4.00 | Sets |  | 11198.00 | 44792.00 | 19597.00 | 78388.00 | 6840.00 | 27360.00 | 5500.00 | 22000.00 | 6400.00 | 25600.00 | 12555.00 | 50220.00 | 6500.00 | 26000.00 | 14850.00 | 59400.00 | 20000.00 | 80000.00 | 13675.00 | 54700.00 | 5000.00 | 20000.00 | 12500.00 | 50000.00 | 9360.00 | 37440.00 | 14000.00 | 56000.00 | 8000.00 | 32000.00 | 4000.00 | 16000.00 | 7873.00 | 31492.00 | 9642.00 | 38568.00 | 5600.00 | 22400.00 | 9890.00 | 39560.00 | 2508.19 | 10032.76 | 5330.00 | 21320.00 | 11001.00 | 44004.00 | 10032.76 | Bhanwariya Infra Projects Pvt Ltd
6.00 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size.
6.01 | 3 Core, 300 Sq.mm. (11KV UE grade) | 5.00 | Sets |  | 34670.00 | 173350.00 | 39525.00 | 197625.00 | 12000.00 | 60000.00 | 11000.00 | 55000.00 | 12700.00 | 63500.00 | 21796.00 | 108980.00 | 10500.00 | 52500.00 | 34425.00 | 172125.00 | 30000.00 | 150000.00 | 29000.00 | 145000.00 | 10000.00 | 50000.00 | 38800.00 | 194000.00 | 27900.00 | 139500.00 | 50000.00 | 250000.00 | 28000.00 | 140000.00 | 2000.00 | 10000.00 | 24223.00 | 121115.00 | 27793.00 | 138965.00 | 11200.00 | 56000.00 | 20472.00 | 102360.00 | 6374.16 | 31870.80 | 3900.00 | 19500.00 | 26469.00 | 132345.00 | 10000.00 | MAHADEV ENTERPRISE
7.00 | HT CABLE LAYING Laying of HT cable
7.01 | Laying of one number XLPE power cable of 11 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required Size: Above 120 sq. mm and upto 400 sq. Mm | 2050.00 | Mtr |  | 128.00 | 262400.00 | 160.00 | 328000.00 | 210.00 | 430500.00 | 150.00 | 307500.00 | 100.00 | 205000.00 | 162.00 | 332100.00 | 250.00 | 512500.00 | 270.00 | 553500.00 | 100.00 | 205000.00 | 128.00 | 262400.00 | 125.00 | 256250.00 | 180.00 | 369000.00 | 81.00 | 166050.00 | 200.00 | 410000.00 | 100.00 | 205000.00 | 240.00 | 492000.00 | 159.00 | 325950.00 | 193.00 | 395650.00 | 100.00 | 205000.00 | 120.00 | 246000.00 | 152.10 | 311805.00 | 78.00 | 159900.00 | 248.00 | 508400.00 | 159900.00 | JAI ENTERPRISES
7.02 | Laying of one number XLPE power cable of 11 KV grade of following size in the existing masonry open duct as required Size: Above 120 sq. mm and upto 400 sq. Mm | 100.00 | Mtr |  | 121.00 | 12100.00 | 123.00 | 12300.00 | 180.00 | 18000.00 | 120.00 | 12000.00 | 100.00 | 10000.00 | 162.00 | 16200.00 | 150.00 | 15000.00 | 270.00 | 27000.00 | 100.00 | 10000.00 | 120.00 | 12000.00 | 110.00 | 11000.00 | 168.00 | 16800.00 | 81.00 | 8100.00 | 200.00 | 20000.00 | 80.00 | 8000.00 | 230.00 | 23000.00 | 159.00 | 15900.00 | 193.00 | 19300.00 | 300.00 | 30000.00 | 120.00 | 12000.00 | 175.50 | 17550.00 | 78.00 | 7800.00 | 223.00 | 22300.00 | 7800.00 | JAI ENTERPRISES
8.00 | Horizontal Boring
8.01 | Laying of HDPE pipe by HDD method including preparing & setting up plant & machinery including jointing reamring and pulling of HDPE pipe upto 200 mm dia pipe in soft soil as per technical specification and site condition etc as required as per direction of E-I-C. | 60.00 | RMtr |  | 1080.00 | 64800.00 | 1500.00 | 90000.00 | 3000.00 | 180000.00 | 3500.00 | 210000.00 | 600.00 | 36000.00 | 540.00 | 32400.00 | 750.00 | 45000.00 | 2970.00 | 178200.00 | 700.00 | 42000.00 | 525.00 | 31500.00 | 650.00 | 39000.00 | 900.00 | 54000.00 | 1863.00 | 111780.00 | 2500.00 | 150000.00 | 1000.00 | 60000.00 | 2500.00 | 150000.00 | 470.00 | 28200.00 | 2042.00 | 122520.00 | 4000.00 | 240000.00 | 1835.00 | 110100.00 | 409.50 | 24570.00 | 3250.00 | 195000.00 | 3727.00 | 223620.00 | 24570.00 | Bhanwariya Infra Projects Pvt Ltd
8.02 | Laying of HDPE pipe by HDD method including preparing & setting up plant & machinery including jointing reamring and pulling of HDPE pipe upto 200 mm dia pipe in rock area as per technical specification and site condition etc as required as per direction of E-I-C. | 50.00 | RMtr |  | 1485.00 | 74250.00 | 4000.00 | 200000.00 | 3000.00 | 150000.00 | 5500.00 | 275000.00 | 700.00 | 35000.00 | 540.00 | 27000.00 | 650.00 | 32500.00 | 4320.00 | 216000.00 | 700.00 | 35000.00 | 825.00 | 41250.00 | 1500.00 | 75000.00 | 1200.00 | 60000.00 | 4320.00 | 216000.00 | 2500.00 | 125000.00 | 1000.00 | 50000.00 | 1600.00 | 80000.00 | 470.00 | 23500.00 | 2042.00 | 102100.00 | 4000.00 | 200000.00 | 1835.00 | 91750.00 | 468.00 | 23400.00 | 4550.00 | 227500.00 | 6212.00 | 310600.00 | 23400.00 | Bhanwariya Infra Projects Pvt Ltd
9.00 | Supply and laying of HDPE pipe of 200 MM dia PE-100, PN-6 at a depth of 1.2 mtr below the ground as per site condition. | 2050.00 | Mtr |  | 1599.00 | 3277950.00 | 1292.00 | 2648600.00 | 1250.00 | 2562500.00 | 1250.00 | 2562500.00 | 1005.00 | 2060250.00 | 975.00 | 1998750.00 | 900.00 | 1845000.00 | 885.00 | 1814250.00 | 1000.00 | 2050000.00 | 1029.00 | 2109450.00 | 500.00 | 1025000.00 | 1140.00 | 2337000.00 | 1044.00 | 2140200.00 | 2200.00 | 4510000.00 | 1100.00 | 2255000.00 | 2000.00 | 4100000.00 | 1041.00 | 2134050.00 | 2306.00 | 4727300.00 | 1050.00 | 2152500.00 | 692.00 | 1418600.00 | 526.50 | 1079325.00 | 1105.00 | 2265250.00 | 1860.00 | 3813000.00 | 1025000.00 | Shekhawati Electrical Engineers
10.00 | LT CABLE Supply of following sizes of XLPE insulated PVC sheathed, aluminium conductor, armoured, power cable of 1.1 KV grade conforming to IS 7098 (Part I), 1988 amended up to date.
10.01 | 3.5 Core, 240 Sq.mm. | 534.00 | Mtr |  | 989.00 | 528126.00 | 842.00 | 449628.00 | 850.00 | 453900.00 | 1010.00 | 539340.00 | 700.00 | 373800.00 | 780.00 | 416520.00 | 850.00 | 453900.00 | 1147.50 | 612765.00 | 754.00 | 402636.00 | 807.00 | 430938.00 | 850.00 | 453900.00 | 880.00 | 469920.00 | 774.00 | 413316.00 | 1200.00 | 640800.00 | 824.00 | 440016.00 | 1600.00 | 854400.00 | 807.00 | 430938.00 | 1039.00 | 554826.00 | 960.00 | 512640.00 | 825.00 | 440550.00 | 915.82 | 489047.88 | 1092.00 | 583128.00 | 814.00 | 434676.00 | 373800.00 | JITENDRA ELECTRICALS
10.02 | 3.5 Core, 185 Sq.mm. | 1164.00 | Mtr |  | 772.00 | 898608.00 | 658.00 | 765912.00 | 690.00 | 803160.00 | 790.00 | 919560.00 | 550.00 | 640200.00 | 610.00 | 710040.00 | 720.00 | 838080.00 | 945.00 | 1099980.00 | 588.00 | 684432.00 | 631.00 | 734484.00 | 750.00 | 873000.00 | 690.00 | 803160.00 | 603.00 | 701892.00 | 900.00 | 1047600.00 | 647.00 | 753108.00 | 1600.00 | 1862400.00 | 630.00 | 733320.00 | 811.00 | 944004.00 | 765.00 | 890460.00 | 644.00 | 749616.00 | 738.56 | 859683.84 | 851.50 | 991146.00 | 635.00 | 739140.00 | 640200.00 | JITENDRA ELECTRICALS
10.03 | 3.5 Core, 150 Sq.mm. | 1284.00 | Mtr |  | 613.00 | 787092.00 | 522.00 | 670248.00 | 580.00 | 744720.00 | 627.00 | 805068.00 | 445.00 | 571380.00 | 485.00 | 622740.00 | 520.00 | 667680.00 | 776.25 | 996705.00 | 466.00 | 598344.00 | 500.00 | 642000.00 | 600.00 | 770400.00 | 545.00 | 699780.00 | 486.00 | 624024.00 | 800.00 | 1027200.00 | 502.00 | 644568.00 | 1400.00 | 1797600.00 | 500.00 | 642000.00 | 644.00 | 826896.00 | 610.00 | 783240.00 | 512.00 | 657408.00 | 607.39 | 779888.76 | 676.00 | 867984.00 | 504.00 | 647136.00 | 571380.00 | JITENDRA ELECTRICALS
10.04 | 3.5 Core, 70 Sq.mm. | 902.00 | Mtr |  | 337.00 | 303974.00 | 287.00 | 258874.00 | 380.00 | 342760.00 | 345.00 | 311190.00 | 235.00 | 211970.00 | 245.00 | 220990.00 | 350.00 | 315700.00 | 506.25 | 456637.50 | 256.00 | 230912.00 | 275.00 | 248050.00 | 350.00 | 315700.00 | 300.00 | 270600.00 | 270.00 | 243540.00 | 500.00 | 451000.00 | 287.00 | 258874.00 | 1300.00 | 1172600.00 | 275.00 | 248050.00 | 354.00 | 319308.00 | 350.00 | 315700.00 | 281.00 | 253462.00 | 356.87 | 321896.74 | 332.80 | 300185.60 | 304.00 | 274208.00 | 211970.00 | JITENDRA ELECTRICALS
10.05 | 4 Core, 25 Sq.mm. | 83.00 | Mtr |  | 181.00 | 15023.00 | 175.00 | 14525.00 | 260.00 | 21580.00 | 175.00 | 14525.00 | 125.00 | 10375.00 | 133.00 | 11039.00 | 140.00 | 11620.00 | 337.50 | 28012.50 | 126.00 | 10458.00 | 136.00 | 11288.00 | 180.00 | 14940.00 | 150.00 | 12450.00 | 153.00 | 12699.00 | 280.00 | 23240.00 | 142.00 | 11786.00 | 800.00 | 66400.00 | 152.00 | 12616.00 | 176.00 | 14608.00 | 185.00 | 15355.00 | 139.00 | 11537.00 | 174.89 | 14515.87 | 184.60 | 15321.80 | 125.00 | 10375.00 | 10375.00 | JITENDRA ELECTRICALS, STERLINGELECTRO
11.00 | Supplying of following sizes of 1.1 KV grade PVC insulated copper conductor armoured multistranded Control Cable complete as required.
11.01 | 4 core, 2.5 Sq.mm. Copper Conductor cable | 50.00 | Mtr |  | 152.00 | 7600.00 | 152.00 | 7600.00 | 200.00 | 10000.00 | 150.00 | 7500.00 | 125.00 | 6250.00 | 125.00 | 6250.00 | 180.00 | 9000.00 | 290.25 | 14512.50 | 117.00 | 5850.00 | 120.00 | 6000.00 | 200.00 | 10000.00 | 130.00 | 6500.00 | 153.00 | 7650.00 | 190.00 | 9500.00 | 150.00 | 7500.00 | 250.00 | 12500.00 | 133.00 | 6650.00 | 154.00 | 7700.00 | 160.00 | 8000.00 | 122.00 | 6100.00 | 157.37 | 7868.50 | 169.00 | 8450.00 | 125.00 | 6250.00 | 5850.00 | GIRI ENTERPRISES
11.02 | 10 core, 2.5 Sq.mm. Copper Conductor cable | 50.00 | Mtr |  | 318.00 | 15900.00 | 324.00 | 16200.00 | 340.00 | 17000.00 | 315.00 | 15750.00 | 230.00 | 11500.00 | 258.00 | 12900.00 | 310.00 | 15500.00 | 452.25 | 22612.50 | 246.00 | 12300.00 | 249.00 | 12450.00 | 425.00 | 21250.00 | 270.00 | 13500.00 | 306.00 | 15300.00 | 390.00 | 19500.00 | 440.00 | 22000.00 | 600.00 | 30000.00 | 277.00 | 13850.00 | 321.00 | 16050.00 | 310.00 | 15500.00 | 254.00 | 12700.00 | 316.29 | 15814.50 | 349.70 | 17485.00 | 262.00 | 13100.00 | 11500.00 | JITENDRA ELECTRICALS
12.00 | Supply of 1.0 Core x 150 Sqmm size 1.1 kv grade, XLPE insulated and PVC inner sheathed copper conductor armored power cable conforming to IS: 7098(Part 1)1988 with upto date amendments etc. complete as required. | 696.00 | Mtr |  | 1772.00 | 1233312.00 | 1472.00 | 1024512.00 | 1300.00 | 904800.00 | 1875.00 | 1305000.00 | 1040.00 | 723840.00 | 1469.00 | 1022424.00 | 1650.00 | 1148400.00 | 1890.00 | 1315440.00 | 1352.00 | 940992.00 | 1447.00 | 1007112.00 | 1550.00 | 1078800.00 | 1570.00 | 1092720.00 | 1566.00 | 1089936.00 | 2500.00 | 1740000.00 | 1613.00 | 1122648.00 | 4500.00 | 3132000.00 | 1259.00 | 876264.00 | 1862.00 | 1295952.00 | 1630.00 | 1134480.00 | 1478.00 | 1028688.00 | 1589.39 | 1106215.44 | 2003.30 | 1394296.80 | 1519.00 | 1057224.00 | 723840.00 | JITENDRA ELECTRICALS
13.00 | Supplying and making end termination with brass single compression gland and copper lugs for 1.0 Core x 150 Sqmm PVC/XLPE insulated PVC sheathed copper conductor cable of 1.1KV grade as required. | 16.00 | Set |  | 323.00 | 5168.00 | 2155.00 | 34480.00 | 3000.00 | 48000.00 | 1000.00 | 16000.00 | 500.00 | 8000.00 | 254.00 | 4064.00 | 250.00 | 4000.00 | 4252.50 | 68040.00 | 500.00 | 8000.00 | 753.00 | 12048.00 | 400.00 | 6400.00 | 910.00 | 14560.00 | 549.00 | 8784.00 | 1000.00 | 16000.00 | 1000.00 | 16000.00 | 600.00 | 9600.00 | 450.00 | 7200.00 | 398.00 | 6368.00 | 400.00 | 6400.00 | 640.00 | 10240.00 | 1412.13 | 22594.08 | 195.00 | 3120.00 | 544.00 | 8704.00 | 3120.00 | JAI ENTERPRISES
14.00 | LAYING OF LT CABLE Laying and fixing of one number armoured PVC insulated and 1 PVC sheathed 1XLPE power cable 1.1 kV of following size in the I existing cable Trays/ Surface including providing suitable size 1 clamp to secure the cable in tray surface as required.
14.01 | Upto 35 Sq.mm (including control cables) | 80.00 | Mtr |  | 42.00 | 3360.00 | 40.00 | 3200.00 | 40.00 | 3200.00 | 80.00 | 6400.00 | 50.00 | 4000.00 | 43.00 | 3440.00 | 100.00 | 8000.00 | 162.00 | 12960.00 | 30.00 | 2400.00 | 75.00 | 6000.00 | 50.00 | 4000.00 | 240.00 | 19200.00 | 45.00 | 3600.00 | 200.00 | 16000.00 | 80.00 | 6400.00 | 170.00 | 13600.00 | 35.00 | 2800.00 | 57.00 | 4560.00 | 30.00 | 2400.00 | 48.00 | 3840.00 | 35.10 | 2808.00 | 78.00 | 6240.00 | 43.00 | 3440.00 | 2400.00 | GAYATRI AGENCY, GIRI ENTERPRISES
14.02 | Above 35 sq. mm and upto 95 sq. Mm | 5.00 | Mtr |  | 54.00 | 270.00 | 75.00 | 375.00 | 70.00 | 350.00 | 120.00 | 600.00 | 70.00 | 350.00 | 54.00 | 270.00 | 100.00 | 500.00 | 202.50 | 1012.50 | 40.00 | 200.00 | 90.00 | 450.00 | 80.00 | 400.00 | 540.00 | 2700.00 | 63.00 | 315.00 | 200.00 | 1000.00 | 80.00 | 400.00 | 195.00 | 975.00 | 47.00 | 235.00 | 91.00 | 455.00 | 40.00 | 200.00 | 72.00 | 360.00 | 70.20 | 351.00 | 78.00 | 390.00 | 75.00 | 375.00 | 200.00 | GAYATRI AGENCY, GIRI ENTERPRISES
14.03 | Above 95 Sq.mm. but not exceeding 400 Sq.mm. | 25.00 | Mtr |  | 121.00 | 3025.00 | 85.00 | 2125.00 | 100.00 | 2500.00 | 150.00 | 3750.00 | 100.00 | 2500.00 | 108.00 | 2700.00 | 250.00 | 6250.00 | 270.00 | 6750.00 | 100.00 | 2500.00 | 225.00 | 5625.00 | 100.00 | 2500.00 | 600.00 | 15000.00 | 63.00 | 1575.00 | 200.00 | 5000.00 | 80.00 | 2000.00 | 260.00 | 6500.00 | 59.00 | 1475.00 | 125.00 | 3125.00 | 70.00 | 1750.00 | 108.00 | 2700.00 | 146.25 | 3656.25 | 117.00 | 2925.00 | 156.00 | 3900.00 | 1475.00 | Brilltech Engineers Pvt. Ltd.
15.00 | Laying of one number PVC insulated and PVC sheathed/XLPE power cable of 1.1 KV grade of following size in the existing RCCI HUMEI STONEWARE1 METALICORRUGATED PIPE as required.
15.01 | upto 35 sq mm | 10.00 | Mtr |  | 34.00 | 340.00 | 80.00 | 800.00 | 30.00 | 300.00 | 105.00 | 1050.00 | 50.00 | 500.00 | 43.00 | 430.00 | 100.00 | 1000.00 | 162.00 | 1620.00 | 30.00 | 300.00 | 75.00 | 750.00 | 50.00 | 500.00 | 540.00 | 5400.00 | 45.00 | 450.00 | 200.00 | 2000.00 | 80.00 | 800.00 | 110.00 | 1100.00 | 35.00 | 350.00 | 45.00 | 450.00 | 30.00 | 300.00 | 60.00 | 600.00 | 117.00 | 1170.00 | 78.00 | 780.00 | 49.00 | 490.00 | 300.00 | SYSTEM HOUSE CORPORATION, GAYATRI AGENCY, GIRI ENTERPRISES
15.02 | Above 35Sq.mm up to 400Sqmm | 1100.00 | Mtr |  | 108.00 | 118800.00 | 180.00 | 198000.00 | 100.00 | 110000.00 | 150.00 | 165000.00 | 70.00 | 77000.00 | 108.00 | 118800.00 | 100.00 | 110000.00 | 270.00 | 297000.00 | 60.00 | 66000.00 | 135.00 | 148500.00 | 100.00 | 110000.00 | 140.00 | 154000.00 | 90.00 | 99000.00 | 200.00 | 220000.00 | 80.00 | 88000.00 | 150.00 | 165000.00 | 59.00 | 64900.00 | 147.00 | 161700.00 | 70.00 | 77000.00 | 120.00 | 132000.00 | 140.40 | 154440.00 | 97.50 | 107250.00 | 174.00 | 191400.00 | 64900.00 | Brilltech Engineers Pvt. Ltd.
16.00 | Laying of one number PVC insulated and PVC sheathed/XLPE . lower cable of 1.1 KV grade of following size in the existing masonary open duct as required.
16.01 | upto 35 sq mm | 10.00 | Mtr |  | 34.00 | 340.00 | 46.00 | 460.00 | 30.00 | 300.00 | 55.00 | 550.00 | 50.00 | 500.00 | 43.00 | 430.00 | 150.00 | 1500.00 | 162.00 | 1620.00 | 30.00 | 300.00 | 75.00 | 750.00 | 50.00 | 500.00 | 540.00 | 5400.00 | 90.00 | 900.00 | 200.00 | 2000.00 | 80.00 | 800.00 | 85.00 | 850.00 | 35.00 | 350.00 | 45.00 | 450.00 | 30.00 | 300.00 | 60.00 | 600.00 | 29.25 | 292.50 | 78.00 | 780.00 | 43.00 | 430.00 | 292.50 | Bhanwariya Infra Projects Pvt Ltd
16.02 | Above 35Sq.mm up to 400Sqmm | 205.00 | Mtr |  | 108.00 | 22140.00 | 115.00 | 23575.00 | 80.00 | 16400.00 | 80.00 | 16400.00 | 70.00 | 14350.00 | 108.00 | 22140.00 | 200.00 | 41000.00 | 270.00 | 55350.00 | 60.00 | 12300.00 | 135.00 | 27675.00 | 100.00 | 20500.00 | 120.00 | 24600.00 | 90.00 | 18450.00 | 200.00 | 41000.00 | 80.00 | 16400.00 | 325.00 | 66625.00 | 59.00 | 12095.00 | 147.00 | 30135.00 | 70.00 | 14350.00 | 120.00 | 24600.00 | 93.60 | 19188.00 | 91.00 | 18655.00 | 156.00 | 31980.00 | 12095.00 | Brilltech Engineers Pvt. Ltd.
17.00 | Laying of one number armoured PVC/XLPE insulated and PVC sheathed power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective, covering and refilling the trench etc. as required.
17.01 | Upto 35 sq mm | 5.00 | Mtr |  | 216.00 | 1080.00 | 200.00 | 1000.00 | 150.00 | 750.00 | 325.00 | 1625.00 | 350.00 | 1750.00 | 486.00 | 2430.00 | 50.00 | 250.00 | 162.00 | 810.00 | 200.00 | 1000.00 | 788.00 | 3940.00 | 100.00 | 500.00 | 470.00 | 2350.00 | 207.00 | 1035.00 | 1000.00 | 5000.00 | 250.00 | 1250.00 | 1500.00 | 7500.00 | 106.00 | 530.00 | 295.00 | 1475.00 | 30.00 | 150.00 | 36.00 | 180.00 | 93.60 | 468.00 | 390.00 | 1950.00 | 472.00 | 2360.00 | 150.00 | GAYATRI AGENCY
17.02 | Above 35 Sq.mm. but not exceeding 95 sq.mm. | 5.00 | Mtr |  | 236.00 | 1180.00 | 406.00 | 2030.00 | 200.00 | 1000.00 | 360.00 | 1800.00 | 400.00 | 2000.00 | 540.00 | 2700.00 | 50.00 | 250.00 | 202.50 | 1012.50 | 200.00 | 1000.00 | 875.00 | 4375.00 | 125.00 | 625.00 | 525.00 | 2625.00 | 216.00 | 1080.00 | 1000.00 | 5000.00 | 20.00 | 100.00 | 2000.00 | 10000.00 | 130.00 | 650.00 | 329.00 | 1645.00 | 40.00 | 200.00 | 48.00 | 240.00 | 152.10 | 760.50 | 390.00 | 1950.00 | 497.00 | 2485.00 | 100.00 | shiv electric
17.03 | Above 95 Sq.mm. but not exceeding 185 sq.mm. | 5.00 | Mtr |  | 250.00 | 1250.00 | 422.00 | 2110.00 | 220.00 | 1100.00 | 390.00 | 1950.00 | 450.00 | 2250.00 | 648.00 | 3240.00 | 100.00 | 500.00 | 270.00 | 1350.00 | 200.00 | 1000.00 | 963.00 | 4815.00 | 150.00 | 750.00 | 560.00 | 2800.00 | 216.00 | 1080.00 | 1000.00 | 5000.00 | 250.00 | 1250.00 | 3000.00 | 15000.00 | 153.00 | 765.00 | 363.00 | 1815.00 | 70.00 | 350.00 | 72.00 | 360.00 | 163.80 | 819.00 | 390.00 | 1950.00 | 963.00 | 4815.00 | 350.00 | GAYATRI AGENCY
17.04 | Above 185 Sq.mm. but not exceeding 400 sq.mm. | 5.00 | Mtr |  | 290.00 | 1450.00 | 475.00 | 2375.00 | 250.00 | 1250.00 | 425.00 | 2125.00 | 500.00 | 2500.00 | 648.00 | 3240.00 | 100.00 | 500.00 | 270.00 | 1350.00 | 200.00 | 1000.00 | 1050.00 | 5250.00 | 200.00 | 1000.00 | 600.00 | 3000.00 | 270.00 | 1350.00 | 1000.00 | 5000.00 | 250.00 | 1250.00 | 3500.00 | 17500.00 | 165.00 | 825.00 | 397.00 | 1985.00 | 70.00 | 350.00 | 108.00 | 540.00 | 163.80 | 819.00 | 390.00 | 1950.00 | 1012.00 | 5060.00 | 350.00 | GAYATRI AGENCY
18.00 | L.T. CABLE END TERMINATION Supplying and making end termination with brass compression gland and Aluminum lugs for following size of XLPE insulated PVC sheathed aluminium conductor armoured power cable of 1.1 KV grade as required.
18.01 | 3.5 Core, 240 Sq.mm. | 8.00 | Set |  | 873.00 | 6984.00 | 2236.00 | 17888.00 | 460.00 | 3680.00 | 1950.00 | 15600.00 | 1000.00 | 8000.00 | 1265.00 | 10120.00 | 350.00 | 2800.00 | 3240.00 | 25920.00 | 600.00 | 4800.00 | 1996.00 | 15968.00 | 1000.00 | 8000.00 | 2650.00 | 21200.00 | 720.00 | 5760.00 | 1000.00 | 8000.00 | 1000.00 | 8000.00 | 1850.00 | 14800.00 | 1849.00 | 14792.00 | 822.00 | 6576.00 | 1900.00 | 15200.00 | 1612.00 | 12896.00 | 1983.50 | 15868.00 | 1690.00 | 13520.00 | 2638.00 | 21104.00 | 2800.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
18.02 | 3.5 Core, 185 Sq.mm. | 22.00 | Set |  | 678.00 | 14916.00 | 1757.00 | 38654.00 | 380.00 | 8360.00 | 1690.00 | 37180.00 | 800.00 | 17600.00 | 1093.00 | 24046.00 | 300.00 | 6600.00 | 2835.00 | 62370.00 | 500.00 | 11000.00 | 1392.00 | 30624.00 | 700.00 | 15400.00 | 2035.00 | 44770.00 | 630.00 | 13860.00 | 1000.00 | 22000.00 | 800.00 | 17600.00 | 1800.00 | 39600.00 | 1256.00 | 27632.00 | 647.00 | 14234.00 | 1500.00 | 33000.00 | 1281.00 | 28182.00 | 1593.54 | 35057.88 | 1495.00 | 32890.00 | 1923.00 | 42306.00 | 6600.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
18.03 | 3.5 Core, 150 Sq.mm. | 4.00 | Set |  | 601.00 | 2404.00 | 1453.00 | 5812.00 | 285.00 | 1140.00 | 1450.00 | 5800.00 | 700.00 | 2800.00 | 1012.00 | 4048.00 | 250.00 | 1000.00 | 2835.00 | 11340.00 | 400.00 | 1600.00 | 1050.00 | 4200.00 | 500.00 | 2000.00 | 1855.00 | 7420.00 | 540.00 | 2160.00 | 1000.00 | 4000.00 | 700.00 | 2800.00 | 1700.00 | 6800.00 | 1114.00 | 4456.00 | 542.00 | 2168.00 | 1150.00 | 4600.00 | 1210.00 | 4840.00 | 1475.37 | 5901.48 | 1495.00 | 5980.00 | 1693.00 | 6772.00 | 1000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
18.04 | 3.5 Core, 70 Sq.mm. | 22.00 | Set |  | 351.00 | 7722.00 | 1375.00 | 30250.00 | 210.00 | 4620.00 | 1170.00 | 25740.00 | 500.00 | 11000.00 | 702.00 | 15444.00 | 200.00 | 4400.00 | 2430.00 | 53460.00 | 300.00 | 6600.00 | 816.00 | 17952.00 | 350.00 | 7700.00 | 1200.00 | 26400.00 | 450.00 | 9900.00 | 1000.00 | 22000.00 | 400.00 | 8800.00 | 1200.00 | 26400.00 | 767.00 | 16874.00 | 386.00 | 8492.00 | 550.00 | 12100.00 | 727.00 | 15994.00 | 849.42 | 18687.24 | 1170.00 | 25740.00 | 1105.00 | 24310.00 | 4400.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
18.05 | 4 Core, 25 Sq.mm. | 4.00 | Set |  | 175.00 | 700.00 | 1314.00 | 5256.00 | 285.00 | 1140.00 | 920.00 | 3680.00 | 400.00 | 1600.00 | 541.00 | 2164.00 | 100.00 | 400.00 | 2025.00 | 8100.00 | 200.00 | 800.00 | 364.00 | 1456.00 | 200.00 | 800.00 | 770.00 | 3080.00 | 360.00 | 1440.00 | 1000.00 | 4000.00 | 300.00 | 1200.00 | 600.00 | 2400.00 | 375.00 | 1500.00 | 269.00 | 1076.00 | 210.00 | 840.00 | 390.00 | 1560.00 | 472.10 | 1888.40 | 780.00 | 3120.00 | 535.00 | 2140.00 | 400.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
19.00 | Supplying and making end termination with brass compression gland and Copper lugs for following size of PVC sheathed copper conductor armoured control cable of 1.1 KV grade as required.
19.01 | 4 C x 2.5sqmm | 16.00 | Set |  | 117.00 | 1872.00 | 583.00 | 9328.00 | 75.00 | 1200.00 | 920.00 | 14720.00 | 250.00 | 4000.00 | 322.00 | 5152.00 | 68.50 | 1096.00 | 1350.00 | 21600.00 | 200.00 | 3200.00 | 249.00 | 3984.00 | 200.00 | 3200.00 | 500.00 | 8000.00 | 270.00 | 4320.00 | 3000.00 | 48000.00 | 500.00 | 8000.00 | 750.00 | 12000.00 | 375.00 | 6000.00 | 117.00 | 1872.00 | 45.00 | 720.00 | 229.00 | 3664.00 | 790.34 | 12645.44 | 325.00 | 5200.00 | 288.00 | 4608.00 | 720.00 | GAYATRI AGENCY
19.02 | 10 C x 2.5sqmm | 12.00 | Set |  | 281.00 | 3372.00 | 623.00 | 7476.00 | 145.00 | 1740.00 | 1170.00 | 14040.00 | 400.00 | 4800.00 | 515.00 | 6180.00 | 88.52 | 1062.24 | 1620.00 | 19440.00 | 300.00 | 3600.00 | 405.00 | 4860.00 | 250.00 | 3000.00 | 1040.00 | 12480.00 | 360.00 | 4320.00 | 3000.00 | 36000.00 | 700.00 | 8400.00 | 1350.00 | 16200.00 | 490.00 | 5880.00 | 193.00 | 2316.00 | 90.00 | 1080.00 | 237.00 | 2844.00 | 1044.40 | 12532.80 | 325.00 | 3900.00 | 653.00 | 7836.00 | 1062.24 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
20.00 | CABLE TRAY Supplying and installing following size of perforated painted with powder coating G.I. cable trays Tee with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders as per technical specification and site condition etc as required as per direction of E-I-C.
20.01 | 100mm width x 54mm depth x 2.0mm thickness. | 50.00 | Mtr |  | 648.00 | 32400.00 | 801.00 | 40050.00 | 510.00 | 25500.00 | 495.00 | 24750.00 | 400.00 | 20000.00 | 468.00 | 23400.00 | 750.00 | 37500.00 | 540.00 | 27000.00 | 400.00 | 20000.00 | 520.00 | 26000.00 | 400.00 | 20000.00 | 1680.00 | 84000.00 | 1080.00 | 54000.00 | 500.00 | 25000.00 | 700.00 | 35000.00 | 1800.00 | 90000.00 | 846.00 | 42300.00 | 442.00 | 22100.00 | 420.00 | 21000.00 | 458.00 | 22900.00 | 447.64 | 22382.00 | 728.00 | 36400.00 | 754.00 | 37700.00 | 20000.00 | JITENDRA ELECTRICALS, GIRI ENTERPRISES, Shekhawati Electrical Engineers
20.02 | 200/150 mm width x 54mm depth x 2.0mm thickness. | 150.00 | Mtr |  | 764.00 | 114600.00 | 1037.00 | 155550.00 | 585.00 | 87750.00 | 610.00 | 91500.00 | 470.00 | 70500.00 | 700.00 | 105000.00 | 950.00 | 142500.00 | 877.50 | 131625.00 | 450.00 | 67500.00 | 706.00 | 105900.00 | 600.00 | 90000.00 | 1970.00 | 295500.00 | 1350.00 | 202500.00 | 800.00 | 120000.00 | 900.00 | 135000.00 | 1900.00 | 285000.00 | 973.00 | 145950.00 | 488.00 | 73200.00 | 580.00 | 87000.00 | 640.00 | 96000.00 | 506.73 | 76009.50 | 949.00 | 142350.00 | 988.00 | 148200.00 | 67500.00 | GIRI ENTERPRISES
20.03 | 400mm width x 54mm depth x 2.0mm thickness. | 250.00 | Mtr |  | 1262.00 | 315500.00 | 1665.00 | 416250.00 | 660.00 | 165000.00 | 1170.00 | 292500.00 | 890.00 | 222500.00 | 905.00 | 226250.00 | 1050.00 | 262500.00 | 1215.00 | 303750.00 | 800.00 | 200000.00 | 1165.00 | 291250.00 | 800.00 | 200000.00 | 2540.00 | 635000.00 | 1800.00 | 450000.00 | 1330.00 | 332500.00 | 1100.00 | 275000.00 | 3800.00 | 950000.00 | 1728.00 | 432000.00 | 618.00 | 154500.00 | 930.00 | 232500.00 | 1087.00 | 271750.00 | 790.34 | 197585.00 | 1469.00 | 367250.00 | 2352.00 | 588000.00 | 154500.00 | RN Electro Power Pvt. Ltd.
20.04 | 600/500 mm width x 54mm depth x 2.0mm thickness. | 50.00 | Mtr |  | 1555.00 | 77750.00 | 1984.00 | 99200.00 | 975.00 | 48750.00 | 1300.00 | 65000.00 | 1065.00 | 53250.00 | 1306.00 | 65300.00 | 1200.00 | 60000.00 | 1620.00 | 81000.00 | 1000.00 | 50000.00 | 1450.00 | 72500.00 | 1000.00 | 50000.00 | 2940.00 | 147000.00 | 2520.00 | 126000.00 | 1500.00 | 75000.00 | 1300.00 | 65000.00 | 3800.00 | 190000.00 | 2307.00 | 115350.00 | 703.00 | 35150.00 | 1280.00 | 64000.00 | 1345.00 | 67250.00 | 1191.65 | 59582.50 | 1989.00 | 99450.00 | 2731.00 | 136550.00 | 35150.00 | RN Electro Power Pvt. Ltd.
21.00 | LT BUS DUCT (SANDWICH INSULATED BUS DUCT) Supply, Installation, Testing and Commissioning of following rating pre-fabricated sandwiched bustrunking suitable for 3 Phase 4 Wire, 415 V, 50 Hz AC supply system with aluminium busbars complete with bends, expansion joints, fire barriers, copper flexible end connection at both ends, earthing with 2 runs of GI earth of size 50mm x 6mm strips i/c necessary supports etc as per specifications attached. (Made out of 1.6 mm thick CRCA sheet steel / GI enclosure with powder coated painting, IP 54 degree of protection (minimum), complete with proper supporting arrangement with suspenders / brackets etc) Note: The bustrunking shall be measured along with length centreline of enclosure. The aluminium strips which will go inside LT panels and end termination boxes of transformers shall not be taken into measurement of bustrunking quantity including flexible coupling to terminate with panels and busduct end box along with all accessories as per technical specification and site condition etc as required as per direction of E-I-C.
21.01 | 1250 A, Four pole busduct | 100.00 | Mtr |  | 19673.00 | 1967300.00 | 21056.00 | 2105600.00 | 13500.00 | 1350000.00 | 13500.00 | 1350000.00 | 15025.00 | 1502500.00 | 15389.00 | 1538900.00 | 32600.00 | 3260000.00 | 28552.50 | 2855250.00 | 13000.00 | 1300000.00 | 17170.00 | 1717000.00 | 19000.00 | 1900000.00 | 22800.00 | 2280000.00 | 18000.00 | 1800000.00 | 13000.00 | 1300000.00 | 13500.00 | 1350000.00 | 8250.00 | 825000.00 | 11998.00 | 1199800.00 | 16532.00 | 1653200.00 | 20500.00 | 2050000.00 | 16435.00 | 1643500.00 | 16286.40 | 1628640.00 | 16250.00 | 1625000.00 | 25553.00 | 2555300.00 | 825000.00 | MAHADEV ENTERPRISE
22.00 | LT PANEL NON-ESSENTIAL PANEL Design, manufacture supply, installation, testing and commissioning of main LT Panel, cubicle & modular type, made of 2 mm thick sheet steel for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 42, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing complete with 7 tank process, powder coated, painting, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Al.busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common copper earth bar of size 25mm x 5mm at the rear with 2 nos, earth stud, control wiring with 2.5 sq.mm. PVC insulated copper conductor, cable alloys, cable gland plates in two half, interconnections including supply & installation of following items and as per technical specification and site condition etc as required as per direction of E-I-C:(ACB should be mount on single tire only)
22.01 | A) INCOMER i) 2 nos. ACB, ED0 type 1250A, FP, fault braking capacity Ics=lcu up to 433V) 65 kA, (for Transformers) motor wound spring charged closing mechanism, drawout type ACB with microprocessor based release having short circuit, over current, earth fault, zone selective interlocking features with communication module RS 485 . ii) 2 nos. Digital Voltmeter, accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP 1 MCBs. iii) 2 sets Indication Lamps, LED type for R,Y ,B and breaker 'ON', 'OFF', 'TRIP' indications with 2 Amp MCBs for protection. 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-2000A), for 3 phase 4 wire operation with LED iv) display and selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 2 sets. v) 2 nos.(l for each transformer incomer) of current transformer Class 1,15 VA for APFC Relay. B) Bus Bars 1 set of high conductivity Aluminium bus bars of minimum 2000 Amps capacity, TPN with heat shrinkable coloured sleeves and i/c DMCISMC busbars supports at required intervals. C) Bus coupler i) 1 Nos. ACB, 1250A, ED0 type FP, 65 kA, (Ics=Icu=Icw=65KA foe 1 sec).motor wound spring charged closing mechanism, drawout type ACB without release ii) 1 Sets Indication Lamps, LED type for 'ON' , 'OFF', 'TRIP indications with 2 Amp SP/MCBs, auxiliary contact contactors for positive electrical interlocking of breakers etc. as required. D) Accessories for Electrical & Mechanical Interlocking i) Electrical & mechanical interlocking arrangement as per drawing and specifications among 2 nos. Incomers for transformer and 1 no. Bus coupler including interconnections etc. as required. E) Outgoing i) 2 nos. ACB, EDO type 1250A, FP, breaking capacity 65 kA (Ics=Icu up to 433V), drawout type ACB with microprocessor based release having short circuit, over current, earth fault protection. ii) 2 Nos. MCCB, 630A,65 kA, pour Pole , with microprocessor based release having Over current, Short Circuit, Earth Fault Protection (Ics=Icu). iii) 2Nos. MCCB, 400A, 65 kA, Four Pole, with microprocessor based release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). iv) Digital Ammeter (for 3 Phase 4 wire operation with LED display and selector switch) with 3 nos CT of required ratings for all out goings v) Intelligent multi function digital meter to read V,A,KVA, KW, KVAR, PF, Hz etc with communication facility (RS485 module) and LED display with 3 Nos CTs, 15 VA, class 1.0 and control circuit wiring with HRC control fuses 1 MCBs for all out goings vi) (1 Set for all out goings ACB) of Indicating lamps, LED type, for breaker "ON", "OFF", "TRIP" indication with HRC control fuses/MCBs . vii) (1 set for all out goings MCCB) of Extended Rotary operating mechanism, terminal extension spreaders and "ON", indication with HRC control fuses1MCBs. | 1.00 | Job |  | 2066850.00 | 2066850.00 | 1729943.00 | 1729943.00 | 2650000.00 | 2650000.00 | 2550000.00 | 2550000.00 | 1840000.00 | 1840000.00 | 2074571.00 | 2074571.00 | 2044620.00 | 2044620.00 | 2635470.00 | 2635470.00 | 1725000.00 | 1725000.00 | 1727280.00 | 1727280.00 | 2500001.00 | 2500001.00 | 2211600.00 | 2211600.00 | 2016000.00 | 2016000.00 | 1700000.00 | 1700000.00 | 1638000.00 | 1638000.00 | 3300250.00 | 3300250.00 | 2061316.00 | 2061316.00 | 2016979.00 | 2016979.00 | 2400001.69 | 2400001.69 | 1509180.00 | 1509180.00 | 3053700.00 | 3053700.00 | 2054000.00 | 2054000.00 | 2030946.00 | 2030946.00 | 1509180.00 | AT AND T ENGINEERS PVT LTD
23.00 | MAIN Distribution LT PANEL Design, manufacture supply, installation, testing and commissioning of main LT Panel, cubicle & modular type, made of 2 mm thick sheet steel for frame work and covers, 3mm thick for gland plates, totally enclosed, IP 42, free standing, floor mounting, dust and vermin proof, indoor, compartmentalised, including cleaning & finishing complete with 7 tank process, powder coated, painting, suitable for operation on 3 Phase and neutral, 415v, 50 Hz AC system with Al.busbars extensible on both sides, fabrication shall be done in transportation sections, entire panel shall have a common copper earth bar of size 25mm x 5mm at the rear with 2 nos, earth stud, control wiring with 2.5 sq.mm. PVC insulated copper conductor, cable alloys, cable gland plates in two half, interconnections including supply & installation of following items and as per technical specification and site condition etc as required as per direction of E-I-C.. ACB should be mount on single tire only)
23.01 | A) INCOMER i) 4 nos. ACB, ED0 type 1250A, FP, fault braking capacity Ics=lcu up to 433V) 50 kA, (for Transformers) motor wound spring charged closing mechanism, drawout type ACB with microprocessor based release having short circuit, over current, earth fault, zone selective interlocking features with communication module RS 485 ii Digital Voltmeter, accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP 1 MCBs for all incomers. iii) 2 sets Indication Lamps, LED type for R,Y ,B and breaker 'ON', 'OFF', 'TRIP' indications with 2 Amp MCBs for protection. 96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-2000A), for 3 phase 4 wire operation with LED for all incomers. iv) Display and selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- for all incomers.. B) Bus Bars 1 set of high conductivity Aluminium bus bars of minimum 1600 Amps capacity, TPN with heat shrinkable coloured sleeves and i/c DMCISMC busbars supports at required intervals. C) Bus coupler i) 1 Nos. ACB,1250A, ED0 type FP, 50 kA, motor wound spring charged closing mechanism, drawout type ACB without release ii) 1 Sets Indication Lamps, LED type for 'ON' , 'OFF', 'TRIP indications with 2 Amp SP/MCBs, auxiliary contact contactors for positive electrical interlocking of breakers etc. as required. D) Accessories for Electrical & Mechanical Interlocking i) Electrical & mechanical interlocking arrangement as per drawing and specifications among 4 nos. Incomers for transformer and 1 no. Bus coupler including interconnections etc. as required. E) Outgoing i 02 Nos. MCCB, 200A, 50 kA, Four Pole, with microprocessor based release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). ii 16 Nos. MCCB, 160A, 50 kA, Four Pole, with microprocessor based release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). iii) 02 Nos. MCCB,63A, 50 kA, Four Pole, with microprocessor based release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). iv) Digital Ammeter (for 3 Phase 4 wire operation with LED display and selector switch) with 3 nos CT of required ratings for all out goings v) Intelligent multi function digital meter to read V,A,KVA, KW, KVAR, PF, Hz etc with communication facility (RS485 module) and LED display with 3 Nos CTs, 15 VA, class 1.0 and control circuit wiring with HRC control fuses 1 MCBs for all out goings vi) (1 Set for all out goings ACB) of Indicating lamps, LED type, for breaker "ON", "OFF", "TRIP" indication with HRC control fuses/MCBs all out goings. vii) (1 set for all out goings MCCB) of Extended Rotary operating mechanism, terminal extension spreaders and "ON", indication with HRC control fuses1MCBs all out goings. | 2.00 | Job |  | 2810700.00 | 5621400.00 | 2432218.00 | 4864436.00 | 2730000.00 | 5460000.00 | 3175000.00 | 6350000.00 | 2500000.00 | 5000000.00 | 2922960.00 | 5845920.00 | 3055650.00 | 6111300.00 | 4139775.00 | 8279550.00 | 2450000.00 | 4900000.00 | 2438530.00 | 4877060.00 | 3500000.00 | 7000000.00 | 3022800.00 | 6045600.00 | 2790000.00 | 5580000.00 | 2400000.00 | 4800000.00 | 2300000.00 | 4600000.00 | 4000000.00 | 8000000.00 | 3276399.00 | 6552798.00 | 2755480.00 | 5510960.00 | 4000000.00 | 8000000.00 | 2138993.00 | 4277986.00 | 3289794.00 | 6579588.00 | 2379000.00 | 4758000.00 | 3013962.00 | 6027924.00 | 4277986.00 | AT AND T ENGINEERS PVT LTD
24.00 | Design, fabrication, assembly, wiring, supply, erection , testing and commissioning of Hybrid Solution to achieve 1.0 or 0.99 Lag power factor with following rating incomer of MCCB as specified below, 415V, 50Hz, 3 phase, 36KA (ICS=ICU) System. The system shall be of design as per IS 16636. The degree of protection of enclosures system shall be IP42 in accordance with IEC 60529.The switching device of the active compensation system shall be IGBT based. The active compensation system specifications are mentioned below. The active compensation system should filter all type of harmonics from 2nd to 51st individual harmonic order and shall be selectable for the entire range. The active compensation system should have feature to improve PF correction as well. The active compensation system should have a Multi master operation. Response time shall be 100 micro Sec or less.( Panel shall be designed with appropriate heat ventilation and separation of components).
24.10 | The Hybrid should deliver the specified output at 415V The Hybrid Solution should comprise of a minimum of 35% Active filter by capacity. Incomer shall be of 630A MCCB ,415V, 50Hz, 3 phase, 36KA (ICS=ICU) • The Active harmonic filter Incomer shall be of MCCB 200A, 415V, 50Hz, 3 phase, 36KA (ICS=ICU)and contactor shall be 200A TP AC3 duty. • The capacitor shall be of MPP Type of required ratings @525V • Detuned reactor shall be of 7% Aluminium of required ratings • Each capacitor bank shall have Incomer of MCCBs of required rating . Capacitors shall be as per MPP low loss as per standards. . Contactor bsed switching • APFC Relay controling for Bank The system should be with compatible with Grid Power OR D.G. Power Supply. The Hybrid Solution described as above complete in all respect as per specification enclosed, up to the entire satisfaction of engineer In Charge. Busbar and switchgears shall be as per followings and as per specifications. Bus Bar Specifications 630A Electrolytic high conductivity Aluminium extensible three phase and neutral busbars of required ratings & auxiliary Bus Bars of suitable capacity insulated with heat shrinkable coloured PVC sleeves & clip on shrouds for joints having a maximum current density as per indian standards suitable to with stand symmetrical fault level of atleast 36 kA at 415 volts i/c polyamide/smc/dmc bus bars supports at required intervals complete for cross section, size supports & their spacing etc.The neutral busbar is to be of 100 % capacity. Display and indications 7 inch LCD touchscreen for all parameters related to IGBT based system - 01 No The LCD should display all parameters like Currents, Fundamental Current, iTHD, iTDD, Aunb, Voltages, vTHD, kW, kVAr, kVA, PF, dPF, Filter Current, Filter Loading (%), Stack Temperature, Ambient Temperature, Filter Runtime, System Runtime etc and also have the provision of a proper fault log which can be exported to an external storage device LCD should be capable of displaying individual harmonics for currents and voltages upto 51st order, LCD should be capable of simultaneously displaying current and voltage waveforms. User should be able to select the phases to display. HMI Shall have Ethernet port,USB Port and SD card port,Modbus TCP for communication protocol , IGBT based Active technology (No use of low power discrete IGBTs ), IGBT based 3-Level stacks with complete forced cooling arrangement, Single phase, toroidal, powder core, low loss, low noise inductor designed for high frequency application with noise level < 70dB. System should use a single inductor/phase All required hardwares, softwares, protections, cards, inscription plates, Danger notice board etc., as required to be provided to complete the system Long life Aluminium DC capacitors to be used for DC link High speed semi conductor fuses to protect power stack and contactor, Full output without de-rating upto 45degrees ambient. 45 to 55 degrees with derating Under voltage, Over voltage, Over load, Over DC, Over temperature, Fuse failure, Contactor abnormal etc protections to be Provided, Temperature Sensor to be provided in each cubicle for all panels and suitable to map on BMS. corrections in current THD levels/Power factor as per requirement Ratings 300 kVAR (minimum active filter of 150A plus 200 kVAR detuned PFC) | 2.00 | Job |  | 1595700.00 | 3191400.00 | 1234805.00 | 2469610.00 | 1784526.00 | 3569052.00 | 1750000.00 | 3500000.00 | 1040000.00 | 2080000.00 | 790043.00 | 1580086.00 | 750000.00 | 1500000.00 | 1910250.00 | 3820500.00 | 1330000.00 | 2660000.00 | 1302780.00 | 2605560.00 | 1150000.00 | 2300000.00 | 1230000.00 | 2460000.00 | 1440000.00 | 2880000.00 | 1300000.00 | 2600000.00 | 1100000.00 | 2200000.00 | 22000.00 | 44000.00 | 1338000.00 | 2676000.00 | 1089033.00 | 2178066.00 | 2500000.00 | 5000000.00 | 1172805.00 | 2345610.00 | 2035800.00 | 4071600.00 | 474500.00 | 949000.00 | 1186829.00 | 2373658.00 | 44000.00 | MAHADEV ENTERPRISE
25.00 | EARTHING Earthing with copper earth plate 600mm x 600mm x 3.0mm thick including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc. Including charcoal and salt complete as required. | 14.00 | Set |  | 16753.00 | 234542.00 | 25343.00 | 354802.00 | 13644.00 | 191016.00 | 28500.00 | 399000.00 | 15500.00 | 217000.00 | 14800.00 | 207200.00 | 12000.00 | 168000.00 | 24300.00 | 340200.00 | 12000.00 | 168000.00 | 27840.00 | 389760.00 | 11000.00 | 154000.00 | 32290.00 | 452060.00 | 16200.00 | 226800.00 | 13000.00 | 182000.00 | 12000.00 | 168000.00 | 16000.00 | 224000.00 | 17800.00 | 249200.00 | 21554.00 | 301756.00 | 11000.00 | 154000.00 | 17713.00 | 247982.00 | 14642.55 | 204995.70 | 15600.00 | 218400.00 | 37157.00 | 520198.00 | 154000.00 | GAYATRI AGENCY, Shekhawati Electrical Engineers
26.00 | Earthing with G.I. earth plate 600mm x 600mm x 6mm thick including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc. including charcoal and salt complete as required. | 12.00 | Set |  | 8542.00 | 102504.00 | 14896.00 | 178752.00 | 6660.00 | 79920.00 | 10500.00 | 126000.00 | 9300.00 | 111600.00 | 8303.00 | 99636.00 | 9500.00 | 114000.00 | 29700.00 | 356400.00 | 7000.00 | 84000.00 | 13885.00 | 166620.00 | 6000.00 | 72000.00 | 16910.00 | 202920.00 | 9270.00 | 111240.00 | 9000.00 | 108000.00 | 6500.00 | 78000.00 | 10000.00 | 120000.00 | 7800.00 | 93600.00 | 19285.00 | 231420.00 | 9000.00 | 108000.00 | 11675.00 | 140100.00 | 6370.65 | 76447.80 | 9100.00 | 109200.00 | 20448.00 | 245376.00 | 72000.00 | Shekhawati Electrical Engineers
27.00 | Providing & fixing of 50mm x 5mm copper strip on surface or recess for earth connection as required. | 75.00 | Mtr |  | 2200.00 | 165000.00 | 1977.00 | 148275.00 | 2187.00 | 164025.00 | 2100.00 | 157500.00 | 1915.00 | 143625.00 | 2400.00 | 180000.00 | 650.00 | 48750.00 | 3465.45 | 259908.75 | 1400.00 | 105000.00 | 2176.00 | 163200.00 | 1500.00 | 112500.00 | 1880.00 | 141000.00 | 2097.00 | 157275.00 | 2500.00 | 187500.00 | 2500.00 | 187500.00 | 3500.00 | 262500.00 | 1700.00 | 127500.00 | 1942.00 | 145650.00 | 2150.00 | 161250.00 | 1837.00 | 137775.00 | 1506.38 | 112978.50 | 2340.00 | 175500.00 | 1912.00 | 143400.00 | 48750.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
28.00 | Supply & fixing of 50 mm x 5mm copper strip in 80 mm dia GI pipe from earth electrode as required. | 250.00 | Mtr |  | 3172.00 | 793000.00 | 2967.00 | 741750.00 | 2427.00 | 606750.00 | 3000.00 | 750000.00 | 2435.00 | 608750.00 | 3721.00 | 930250.00 | 550.00 | 137500.00 | 3465.45 | 866362.50 | 2100.00 | 525000.00 | 2695.00 | 673750.00 | 2300.00 | 575000.00 | 2810.00 | 702500.00 | 1125.00 | 281250.00 | 2000.00 | 500000.00 | 3000.00 | 750000.00 | 2750.00 | 687500.00 | 2548.00 | 637000.00 | 2723.00 | 680750.00 | 2150.00 | 537500.00 | 2789.00 | 697250.00 | 2173.27 | 543317.50 | 3250.00 | 812500.00 | 2916.00 | 729000.00 | 137500.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
29.00 | Providing & fixing of 50mm x 5mm G.I. strip on surface or recess for earth connection as required. | 250.00 | Mtr |  | 333.00 | 83250.00 | 301.00 | 75250.00 | 276.00 | 69000.00 | 300.00 | 75000.00 | 260.00 | 65000.00 | 400.00 | 100000.00 | 450.00 | 112500.00 | 276.75 | 69187.50 | 300.00 | 75000.00 | 305.00 | 76250.00 | 300.00 | 75000.00 | 260.00 | 65000.00 | 234.00 | 58500.00 | 300.00 | 75000.00 | 600.00 | 150000.00 | 1000.00 | 250000.00 | 220.00 | 55000.00 | 324.00 | 81000.00 | 230.00 | 57500.00 | 263.00 | 65750.00 | 224.71 | 56177.50 | 273.00 | 68250.00 | 237.00 | 59250.00 | 55000.00 | Brilltech Engineers Pvt. Ltd.
30.00 | Supplying and laying 25 mm x 5 mm GI strip at 0.50 m below ground level as strip earth electrode, including soldering etc. as required. | 350.00 | Mtr |  | 243.00 | 85050.00 | 181.00 | 63350.00 | 216.00 | 75600.00 | 225.00 | 78750.00 | 290.00 | 101500.00 | 297.00 | 103950.00 | 350.00 | 122500.00 | 290.25 | 101587.50 | 200.00 | 70000.00 | 182.00 | 63700.00 | 150.00 | 52500.00 | 260.00 | 91000.00 | 135.00 | 47250.00 | 200.00 | 70000.00 | 400.00 | 140000.00 | 1900.00 | 665000.00 | 122.00 | 42700.00 | 221.00 | 77350.00 | 95.00 | 33250.00 | 206.00 | 72100.00 | 68.10 | 23835.00 | 286.00 | 100100.00 | 176.00 | 61600.00 | 23835.00 | Bhanwariya Infra Projects Pvt Ltd
31.00 | Providing & fixing of 25mm x 5mm GI strip on surface or in recess for earth connection as required. | 150.00 | Mtr |  | 186.00 | 27900.00 | 181.00 | 27150.00 | 216.00 | 32400.00 | 195.00 | 29250.00 | 260.00 | 39000.00 | 265.00 | 39750.00 | 350.00 | 52500.00 | 276.75 | 41512.50 | 190.00 | 28500.00 | 145.00 | 21750.00 | 100.00 | 15000.00 | 140.00 | 21000.00 | 153.00 | 22950.00 | 200.00 | 30000.00 | 400.00 | 60000.00 | 1400.00 | 210000.00 | 122.00 | 18300.00 | 163.00 | 24450.00 | 95.00 | 14250.00 | 146.00 | 21900.00 | 68.10 | 10215.00 | 286.00 | 42900.00 | 158.00 | 23700.00 | 10215.00 | Bhanwariya Infra Projects Pvt Ltd
32.00 | Supply of Rubber Hand Globes suitable for 11 KV operation. | 2.00 | Pair |  | 472.00 | 944.00 | 660.00 | 1320.00 | 900.00 | 1800.00 | 2500.00 | 5000.00 | 1000.00 | 2000.00 | 2225.00 | 4450.00 | 950.00 | 1900.00 | 8775.00 | 17550.00 | 1500.00 | 3000.00 | 660.00 | 1320.00 | 500.00 | 1000.00 | 600.00 | 1200.00 | 630.00 | 1260.00 | 1000.00 | 2000.00 | 1000.00 | 2000.00 | 1200.00 | 2400.00 | 100.00 | 200.00 | 1702.00 | 3404.00 | 1500.00 | 3000.00 | 575.00 | 1150.00 | 307.13 | 614.26 | 1430.00 | 2860.00 | 2389.00 | 4778.00 | 200.00 | Brilltech Engineers Pvt. Ltd.
33.00 | Supply and fixing Fire Buckets 12 liter capacity painted in post office red colour and written with white paint 'FIRE' filled with Dry Sand and suitable hanging arrangement & conforming IS 2546 - 1974 for hanging on canopy type MS Structure. | 2.00 | Each |  | 4050.00 | 8100.00 | 1526.00 | 3052.00 | 14400.00 | 28800.00 | 650.00 | 1300.00 | 500.00 | 1000.00 | 2955.00 | 5910.00 | 5400.00 | 10800.00 | 2632.50 | 5265.00 | 1000.00 | 2000.00 | 3125.00 | 6250.00 | 500.00 | 1000.00 | 4200.00 | 8400.00 | 2250.00 | 4500.00 | 5000.00 | 10000.00 | 4000.00 | 8000.00 | 300.00 | 600.00 | 4500.00 | 9000.00 | 681.00 | 1362.00 | 5000.00 | 10000.00 | 3130.00 | 6260.00 | 1062.95 | 2125.90 | 4550.00 | 9100.00 | 1568.00 | 3136.00 | 600.00 | MAHADEV ENTERPRISE
34.00 | Supply of First Aid Box containing material as prescribed by St. John Ambulance brigade OR Indian Red Cross conforming to IS 2217-1963. | 2.00 | Each |  | 1620.00 | 3240.00 | 5905.00 | 11810.00 | 600.00 | 1200.00 | 650.00 | 1300.00 | 2500.00 | 5000.00 | 3337.00 | 6674.00 | 1500.00 | 3000.00 | 4927.50 | 9855.00 | 4000.00 | 8000.00 | 3850.00 | 7700.00 | 1000.00 | 2000.00 | 3000.00 | 6000.00 | 1800.00 | 3600.00 | 1000.00 | 2000.00 | 1000.00 | 2000.00 | 1500.00 | 3000.00 | 1000.00 | 2000.00 | 1134.00 | 2268.00 | 2500.00 | 5000.00 | 5870.00 | 11740.00 | 437.00 | 874.00 | 1950.00 | 3900.00 | 3531.00 | 7062.00 | 874.00 | Bhanwariya Infra Projects Pvt Ltd
35.00 | Supply and fixing of flame retardant electrical insulation mat of 2.0 mm thick to withstand up to 3.3 kV conforming to IS 15652:2006 with up to date amendments and having minimum width 1000mm (±20mm). The sufficient of adhesive/compound shall be supplied to fix the insulation mat on the fronurear side of electrical installation. Mat shall be ISI marked. Its leakage current at 3.3 KV shall not be more than 10 MA. The mat shall be welded by hot gas welding with filler martial method by making V grove cut at joints with suitable welding .cord of insulating material of matching colour to provide a seamless jointed surface as per IS :8002. | 80.00 | RM |  | 817.00 | 65360.00 | 1674.00 | 133920.00 | 2400.00 | 192000.00 | 2275.00 | 182000.00 | 750.00 | 60000.00 | 707.00 | 56560.00 | 3500.00 | 280000.00 | 4738.50 | 379080.00 | 2500.00 | 200000.00 | 724.00 | 57920.00 | 1200.00 | 96000.00 | 660.00 | 52800.00 | 2250.00 | 180000.00 | 2000.00 | 160000.00 | 1800.00 | 144000.00 | 2500.00 | 200000.00 | 826.00 | 66080.00 | 510.00 | 40800.00 | 1350.00 | 108000.00 | 1040.00 | 83200.00 | 3393.00 | 271440.00 | 1040.00 | 83200.00 | 1452.00 | 116160.00 | 40800.00 | RN Electro Power Pvt. Ltd.
36.00 | Supply and fixing of flame retardant electrical insulation mat of minimum 2.5mm thick to withstand up to 11 kV conforming to IS 15652:2006 with up to date amendments and having minimum width 1000mm (±20mm). The sufficient of adhesive / compound shall be supplied to fix the insulation mat on the front/rear side of electrical installation. Mat shall be ISI marked. Its-leakage current at 33 KV shall not be more than 10 MA. The mat shall be welded by hot gas welding with filler martial method by making V grove cut at joints with suitable welding cord of insulating material of matching colour to provide a seamless jointed surface as per IS :8002. | 25.00 | RM |  | 1019.00 | 25475.00 | 1969.00 | 49225.00 | 2400.00 | 60000.00 | 4100.00 | 102500.00 | 1000.00 | 25000.00 | 967.00 | 24175.00 | 3000.00 | 75000.00 | 5143.50 | 128587.50 | 3000.00 | 75000.00 | 926.00 | 23150.00 | 1500.00 | 37500.00 | 790.00 | 19750.00 | 1350.00 | 33750.00 | 5000.00 | 125000.00 | 2000.00 | 50000.00 | 1500.00 | 37500.00 | 944.00 | 23600.00 | 624.00 | 15600.00 | 1550.00 | 38750.00 | 1155.00 | 28875.00 | 3393.00 | 84825.00 | 1040.00 | 26000.00 | 1692.00 | 42300.00 | 15600.00 | RN Electro Power Pvt. Ltd.
37.00 | Supplying and Fixing of the following danger1 Caution notice boards as per the I.E. specifications.
37.01 | Danger board for 11KV size 250mm x 200mm x 2mm thick. | 4.00 | Each |  | 196.00 | 784.00 | 936.00 | 3744.00 | 240.00 | 960.00 | 1300.00 | 5200.00 | 250.00 | 1000.00 | 291.00 | 1164.00 | 1200.00 | 4800.00 | 1987.20 | 7948.80 | 300.00 | 1200.00 | 401.00 | 1604.00 | 200.00 | 800.00 | 240.00 | 960.00 | 270.00 | 1080.00 | 4000.00 | 16000.00 | 500.00 | 2000.00 | 260.00 | 1040.00 | 150.00 | 600.00 | 227.00 | 908.00 | 230.00 | 920.00 | 635.00 | 2540.00 | 248.04 | 992.16 | 260.00 | 1040.00 | 602.00 | 2408.00 | 600.00 | Brilltech Engineers Pvt. Ltd.
37.02 | Danger board for 433V size 250mm x 200mm x 2mm thick. | 4.00 | Each |  | 196.00 | 784.00 | 936.00 | 3744.00 | 240.00 | 960.00 | 1300.00 | 5200.00 | 250.00 | 1000.00 | 291.00 | 1164.00 | 1500.00 | 6000.00 | 1987.20 | 7948.80 | 250.00 | 1000.00 | 401.00 | 1604.00 | 300.00 | 1200.00 | 180.00 | 720.00 | 270.00 | 1080.00 | 4000.00 | 16000.00 | 500.00 | 2000.00 | 250.00 | 1000.00 | 150.00 | 600.00 | 227.00 | 908.00 | 230.00 | 920.00 | 635.00 | 2540.00 | 248.04 | 992.16 | 260.00 | 1040.00 | 602.00 | 2408.00 | 600.00 | Brilltech Engineers Pvt. Ltd.
37.03 | Caution board printed in signal red "Man on Line" size 250mm x 200mm x 2mm thick. . | 4.00 | Each |  | 297.00 | 1188.00 | 936.00 | 3744.00 | 240.00 | 960.00 | 1300.00 | 5200.00 | 250.00 | 1000.00 | 291.00 | 1164.00 | 1800.00 | 7200.00 | 1987.20 | 7948.80 | 1000.00 | 4000.00 | 516.00 | 2064.00 | 500.00 | 2000.00 | 360.00 | 1440.00 | 450.00 | 1800.00 | 4000.00 | 16000.00 | 750.00 | 3000.00 | 250.00 | 1000.00 | 150.00 | 600.00 | 227.00 | 908.00 | 230.00 | 920.00 | 635.00 | 2540.00 | 1193.40 | 4773.60 | 260.00 | 1040.00 | 721.00 | 2884.00 | 600.00 | Brilltech Engineers Pvt. Ltd.
37.04 | Caution board printed in signal red "Don't switch on" size 250mm x 200mm x 2mm thick. | 4.00 | Each |  | 297.00 | 1188.00 | 936.00 | 3744.00 | 240.00 | 960.00 | 1300.00 | 5200.00 | 250.00 | 1000.00 | 291.00 | 1164.00 | 2000.00 | 8000.00 | 1987.20 | 7948.80 | 1000.00 | 4000.00 | 516.00 | 2064.00 | 500.00 | 2000.00 | 360.00 | 1440.00 | 450.00 | 1800.00 | 4000.00 | 16000.00 | 750.00 | 3000.00 | 250.00 | 1000.00 | 150.00 | 600.00 | 227.00 | 908.00 | 230.00 | 920.00 | 635.00 | 2540.00 | 1193.40 | 4773.60 | 260.00 | 1040.00 | 721.00 | 2884.00 | 600.00 | Brilltech Engineers Pvt. Ltd.
38.00 | 750KVA SILENT TYPE DG SET WITH DG SET CONTROL MODULE Supply, installation, testing and commissioning of 750 KVA Silent type D.G Set as per CPCB norms-II with DG set controller module mounted on DG set having AMF control, auto synchronizing, inbuilt metering & protection, communicable port (RS485) etc. facilities and acoustic enclosure conforming to latest environment protection regulations for emission and noise levels complete with Diesel Engine of suitable BHP (considering de-rating factor if any) at 1500 RPM, Radiator, four stroke, electric start, turbo-charged & after cooled conforming to BS: 55 14 with all standard accessories, coupled with Alternator of 750 KVA rating, brushless, self excited, self regulated and suitable for continuous operation, generating 415 V+/-5% Volts at 0.8 PF (lag), 50Hz, 3 phase, 4 wire system generally conforming to BS: 2613 & IS: 4722. Both Engine and Alternator shall be mounted on common channel iron base frame, with fuel pipe line up to 10 meter ( to be concealed under floor), exhaust pipe line with insulation as per OEM (C class MS pipe) as per site condition ( to be erected with sufficient M.S supports and hood on top), required accessories and radiator , Ant vibration mountings, residential type silencer, electric starter, minimum batteries-02 nos of 180AH & battery charger, fuel tank of 990 Itrs. capacity with level indicator, other standard accessories etc complete as required for successful installation and commissioning of the DG sets as per site condition including necessary foundation as per OEM recommendation including Supply, Installation, Testing & Commissioning AMF panel(TTA Panel) with two nos of four pole, 50 KA, EDO type 1250KVA microprocessor based released type ACB(with undervolthage protection,shunt trip,over voltage protection, short circuit, over current, earth fault protection with electrical interlocking with two ACB and other protection as required as per site condition) with all control wiring as per OEM etc. as required as per site condition for automatic operation. Note: Necessary provision should be provided for two sets of incoming & out going BUS DUCT of rating 1250A through flexible copper link etc as per site condition and tender specification as directed by the Engg-In-Charge. | 2.00 | Job |  | 6732716.00 | 13465432.00 | 9666049.00 | 19332098.00 | 7447537.00 | 14895074.00 | 7025000.00 | 14050000.00 | 5583000.00 | 11166000.00 | 5275000.00 | 10550000.00 | 4900000.00 | 9800000.00 | 5670000.00 | 11340000.00 | 7200000.00 | 14400000.00 | 6266988.00 | 12533976.00 | 5125000.00 | 10250000.00 | 6825600.00 | 13651200.00 | 6300000.00 | 12600000.00 | 7000000.00 | 14000000.00 | 5100000.00 | 10200000.00 | 3924250.00 | 7848500.00 | 5505435.00 | 11010870.00 | 5936221.00 | 11872442.00 | 5200000.00 | 10400000.00 | 5990040.00 | 11980080.00 | 6395600.00 | 12791200.00 | 6864000.00 | 13728000.00 | 7349747.00 | 14699494.00 | 7848500.00 | MAHADEV ENTERPRISE
39.00 | Supply, installation, testing, and commissioning of single spike air terminals of 16 mm dia. of 1.5 Meter lengths as required and as per site conditions. the air terminal shall be manufactured with copper. The terminal shall be provided with the integrated / attached threaded base support suitable for mounting the terminals as per site condition. The base support shall be minimum 3 mm thick and shall have inbuilt connector fitting for connection of lightning conductor in such way that conductor contact area shall not be less than 40mm on all side of the conductor. The air terminals shall be supplied with the intermediate guywire supports to make it stable in case of high wind speed. | 2.00 | Each |  | 46879.00 | 93758.00 | 9948.00 | 19896.00 | 15600.00 | 31200.00 | 9000.00 | 18000.00 | 7075.00 | 14150.00 | 26760.00 | 53520.00 | 250000.00 | 500000.00 | 109350.00 | 218700.00 | 100000.00 | 200000.00 | 18837.00 | 37674.00 | 50000.00 | 100000.00 | 16200.00 | 32400.00 | 38700.00 | 77400.00 | 50000.00 | 100000.00 | 10000.00 | 20000.00 | 12000.00 | 24000.00 | 11115.00 | 22230.00 | 14180.00 | 28360.00 | 140000.00 | 280000.00 | 8840.00 | 17680.00 | 6903.20 | 13806.40 | 19500.00 | 39000.00 | 55820.00 | 111640.00 | 13806.40 | Bhanwariya Infra Projects Pvt Ltd
40.00 | Supply, Installation, testing and commissioning of 240 kA 3 phase 4 wire Digital Portable Low Impedance equipment Grounding & bonding system with built in 100% Lightning and Surges suppressor, static charge, Noises, ESD, EPR and abnormal electrical characteristics eliminator which enter from power and other service lines and ensuring clear bonding potential (earth to Neutral voltage) less than 1.0V, a digital 6 digit lightening surge counter, self health visual status indicator and ON-LINE remote monitoring facility of Earth-Neutral voltage in a Pre-wired pulverulent body painted metal enclosure to be connected in parallel to the power supply circuit, Conforming to IEC , CE Marked, CPRI tested as per site condition. | 3.00 | Each |  | 25650.00 | 76950.00 | 233393.00 | 700179.00 | 258000.00 | 774000.00 | 250000.00 | 750000.00 | 225000.00 | 675000.00 | 155196.00 | 465588.00 | 55000.00 | 165000.00 | 139050.00 | 417150.00 | 300000.00 | 900000.00 | 31750.00 | 95250.00 | 485000.00 | 1455000.00 | 264000.00 | 792000.00 | 279000.00 | 837000.00 | 300000.00 | 900000.00 | 200000.00 | 600000.00 | 50000.00 | 150000.00 | 218790.00 | 656370.00 | 182292.00 | 546876.00 | 70000.00 | 210000.00 | 36551.00 | 109653.00 | 442200.00 | 1326600.00 | 260000.00 | 780000.00 | 338954.00 | 1016862.00 | 76950.00 | Power And Instrumentation Guj Ltd
41.00 | Dismantalling,shifting and re installation of Existing 320 KVA DG sets from existing T2 power house to New CCR substation along with exhust piping system,supporting MS structure as per site, 990 Liters fuel tank including necessary MS Piping work, foundation work with 1:2:4 as per the OEM recommendation including necessary testing and commissoning (HSD will be supplied by AAI) as directed by Engg In Charge as per site conditions. | 2.00 | Each |  | 164122.00 | 328244.00 | 646000.00 | 1292000.00 | 90000.00 | 180000.00 | 225000.00 | 450000.00 | 350000.00 | 700000.00 | 162000.00 | 324000.00 | 56000.00 | 112000.00 | 135000.00 | 270000.00 | 200000.00 | 400000.00 | 218750.00 | 437500.00 | 250000.00 | 500000.00 | 240000.00 | 480000.00 | 126000.00 | 252000.00 | 90000.00 | 180000.00 | 180000.00 | 360000.00 | 175000.00 | 350000.00 | 75000.00 | 150000.00 | 283602.00 | 567204.00 | 500000.00 | 1000000.00 | 250000.00 | 500000.00 | 18000.00 | 36000.00 | 390000.00 | 780000.00 | 993840.00 | 1987680.00 | 36000.00 | Bhanwariya Infra Projects Pvt Ltd
42.00 | Providing and fixing ABC powder type fire extinguishers consisting of welded MS cylindrical body automatic modular ABC powder type extinguisher actuated through a sprinkler head mounted on the extinguisher body finished externally with red enamel paint and fixed to wall with brackets complete with internal charge.Minimum 4.0 KG | 4.00 | Each |  | 4860.00 | 19440.00 | 15067.00 | 60268.00 | 3600.00 | 14400.00 | 9500.00 | 38000.00 | 6500.00 | 26000.00 | 2418.00 | 9672.00 | 5500.00 | 22000.00 | 2835.00 | 11340.00 | 10000.00 | 40000.00 | 2775.00 | 11100.00 | 2000.00 | 8000.00 | 6300.00 | 25200.00 | 2070.00 | 8280.00 | 10000.00 | 40000.00 | 7000.00 | 28000.00 | 2500.00 | 10000.00 | 4500.00 | 18000.00 | 1985.00 | 7940.00 | 3122.00 | 12488.00 | 4900.00 | 19600.00 | 3933.60 | 15734.40 | 5200.00 | 20800.00 | 4065.00 | 16260.00 | 7940.00 | RN Electro Power Pvt. Ltd.
43.00 | Providing and fixing Co2 type fire extinguisher as per IS 2878 with discharge time of 10 sec to 18 sec and gas storage pressure of 85 kgf/sq cm fixed to wall with brackets complete with internal charge.6.5KG | 4.00 | Each |  | 5805.00 | 23220.00 | 6749.00 | 26996.00 | 7200.00 | 28800.00 | 11500.00 | 46000.00 | 8800.00 | 35200.00 | 7905.00 | 31620.00 | 5200.00 | 20800.00 | 6345.00 | 25380.00 | 3000.00 | 12000.00 | 9900.00 | 39600.00 | 6011.00 | 24044.00 | 8100.00 | 32400.00 | 9540.00 | 38160.00 | 10000.00 | 40000.00 | 4000.00 | 16000.00 | 8500.00 | 34000.00 | 5500.00 | 22000.00 | 10777.00 | 43108.00 | 15000.00 | 60000.00 | 8925.00 | 35700.00 | 4782.00 | 19128.00 | 3900.00 | 15600.00 | 8365.00 | 33460.00 | 12000.00 | GIRI ENTERPRISES
44.00 | Rate for each one rupee value of work executed from the DSR-2018 (Electrical) Schedule & cost worked out on the basis of DSR-2018 (Electrical) rates. {For example, if the quoted rate for this item is Rs.0.90, then for executing DSR-2018 (Electrical) schedule works of value Rs.1,00,000.00 at DSR-2018 (Electrical) rates, the quoted amount will be Rs.90,000.00. And if quoted rate for this item is Rs.1.25, then quoted amount for the same will be Rs.1,25,000.00}(Note:-Excluding all above items) | 715623.00 | Each |  | 1.20 | 858747.60 | 1.30 | 930309.90 | .90 | 644060.70 | 1.25 | 894528.75 | 1.00 | 715623.00 | 1.10 | 787185.30 | .95 | 679841.85 | 0.00 | 0.00 | 1.00 | 715623.00 | 1.50 | 1073434.50 | .93 | 661951.28 | 1.50 | 1073434.50 | 1.26 | 901684.98 | 1.30 | 930309.90 | .90 | 644060.70 | 1.00 | 715623.00 | 1.22 | 873060.06 | .87 | 622592.01 | .90 | 644060.70 | 1.00 | 715623.00 | 2.67 | 1911429.03 | 1.00 | 715623.00 | 1.31 | 937466.13 | 0.00 | HITECH ERECTORS PVT. LTD.
| Total in Figures |  |  |  |  | 48260521.60 |  | 52142653.90 |  | 47813247.70 |  | 50731621.75 |  | 38062363.00 |  | 39151684.30 |  | 44050000.09 |  | 52971388.95 |  | 43962118.00 |  | 42111834.50 |  | 42125511.28 |  | 48384339.50 |  | 44432965.98 |  | 51435149.90 |  | 38617510.70 |  | 50614263.00 |  | 41969248.06 |  | 46389040.01 |  | 48287795.39 |  | 39408575.00 |  | 49133050.42 |  | 46153020.20 |  | 54257848.13
Lowest Amount Quoted BY: JITENDRA ELECTRICALS(38062363.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of 11 KV Substation and allied works at CCR building Tender ID: 2021_AAI_70108_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | JITENDRA ELECTRICALS | 38062363.00 | L1
| 2 | shiv electric | 38617510.70 | L2
| 3 | Incotech Engineers Pvt Ltd | 39151684.30 | L3
| 4 | AT AND T ENGINEERS PVT LTD | 39408575.00 | L4
| 5 | Brilltech Engineers Pvt. Ltd. | 41969248.06 | L5
| 6 | EVERCREST PROJECTS PVT LTD | 42111834.50 | L6
| 7 | Shekhawati Electrical Engineers | 42125511.28 | L7
| 8 | GIRI ENTERPRISES | 43962118.00 | L8
| 9 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION | 44050000.09 | L9
| 10 | K B CONTRACT (P) LTD | 44432965.98 | L10
| 11 | JAI ENTERPRISES | 46153020.20 | L11
| 12 | RN Electro Power Pvt. Ltd. | 46389040.01 | L12
| 13 | SYSTEM HOUSE CORPORATION | 47813247.70 | L13
| 14 | Power And Instrumentation Guj Ltd | 48260521.60 | L14
| 15 | GAYATRI AGENCY | 48287795.39 | L15
| 16 | Mars Developments | 48384339.50 | L16
| 17 | Bhanwariya Infra Projects Pvt Ltd | 49133050.42 | L17
| 18 | MAHADEV ENTERPRISE | 50614263.00 | L18
| 19 | SHIVRAM ELECTRICALS | 50731621.75 | L19
| 20 | CREATIVE ENTREPRENEURS LLP | 51435149.90 | L20
| 21 | TECHNISYS ENGINEERING PRIVATE LIMITED | 52142653.90 | L21
| 22 | HITECH ERECTORS PVT. LTD. | 52971388.95 | L22
| 23 | STERLINGELECTRO | 54257848.13 | L23