## BoQ1
Government eProcurement System Created By: Sudhir Tripathi Created Date/Time: 17-Mar-2021 12:13 PM Tender Title: Provision of External and Internal fountain in existing water bodies. Tender ID: 2021_AAI_70837_1
Tender Inviting Authority: Airports Authority of India, Agartala Airport.
Name of Work: Provision of External and Internal fountain in existing water bodies i/c provision of pumps, filters, Mushroom nozzles, U stand LED lights etc at NITB Agartala Airport. Agartala.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | COLOR DESIGN INDIA(GSTN-07AJRPM6212C1ZB) |  | FAMILY FOUNTAINS(GSTN-NA) |  | DIVINE WATERCRAFTS & LANDSCAPES(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.10 | Filter SITC of Dia 1200mm(48") Bobbin Wound Fibre Glass anti corrosive sand filter with 2" MPV and necessary accessories such as pressure gauge, manual air vent, manual water drain etc., Filtration Velocity 25 m³/hr/m² Maximum working pressure : 2.5 Bar Flow rate = 25 m³/hr | 2.00 | Nos. | 110050.00 | 202230.00 | 404460.00 | 172800.00 | 345600.00 | 104655.00 | 209310.00 | 209310.00 | DIVINE WATERCRAFTS & LANDSCAPES
1.20 | FILTER MEDIA SITC of Grade 1 Eco Glass Filter Media- Per 25 Kg. | 72.00 | Nos. | 1510.00 | 950.00 | 68400.00 | 900.00 | 64800.00 | 1480.00 | 106560.00 | 64800.00 | FAMILY FOUNTAINS
1.30 | FILTER MEDIA SITC of Grade 3 Eco Glass Filter Media- Per 25 Kg. | 24.00 | Nos. | 1510.00 | 650.00 | 15600.00 | 900.00 | 21600.00 | 1480.00 | 35520.00 | 15600.00 | COLOR DESIGN INDIA
1.40 | Recirculation Pump SITC of centrifugal self priming pump with high hydraulic efficiency, chemical resistant and ultra quiet operation. Each pump integrated along with IP-55 protection- class F continuous rating. Pump shall be of one piece body of durable composite material, with SS Shaft and mechanical seal. Also have large capacity strainer with fast opening translucent lid. Impeller : Plastic impeller Horse power : 3.0 HP Phase : 1 phase 220v 2.25 kw Flow rate = 25 m³/hr @ 13m water head. | 4.00 | Nos. | 60398.00 | 80407.00 | 321628.00 | 44100.00 | 176400.00 | 58675.00 | 234700.00 | 176400.00 | FAMILY FOUNTAINS
1.50 | Submersible Pump for stream nozzle Supply, installation, testing & commissioning of Submersible Openwell Type Pump 5 HP ,3 PH for the sheet fall. (2 Working + 1 stand by ), flowrate of 21.5 LPS @ 10 Mtrs head, including all necessary indigenous accessories as required to complete the installation. (Make:- Crompton / Kirloskar/ Lubi) | 3.00 | Nos. | 37875.00 | 32400.00 | 97200.00 | 44500.00 | 133500.00 | 37200.00 | 111600.00 | 97200.00 | COLOR DESIGN INDIA
1.60 | Submersible Pump for cascade nozzle Supply, installation, testing & commissioning of Submersible Openwell Type Pump 7.5 HP ,3 PH for the Cascade nozzles of suitable flowrate. (2 Working + 1 stand by), flowrate of 27 LPS @ 12 Mtrs head, including all necessary indigenous accessories as required to complete the installation. | 9.00 | Nos. | 48682.00 | 41600.00 | 374400.00 | 62500.00 | 562500.00 | 46900.00 | 422100.00 | 374400.00 | COLOR DESIGN INDIA
1.70 | Submersible Pump for waterfalls Supply, installation, testing & commissioning of Submersible Openwell Type Pump 7.5 HP ,3 PH for the Cascade nozzles of suitable flowrate. (2 Working + 1 stand by), flowrate of 27 LPS @ 12 Mtrs head, including all necessary indigenous accessories as required to complete the installation. | 3.00 | Nos. | 48682.00 | 41600.00 | 124800.00 | 62500.00 | 187500.00 | 46900.00 | 140700.00 | 124800.00 | COLOR DESIGN INDIA
2.10 | Main Drain for cascade nozzle SITC of Main Drain Grille & Frame Only 300x300x1.5 On commercial or shollow pool application stainless steel main drain must be used. Main drain must be arranged so that there is no risk of bathers being drawn towards them or trapped there. It is recommended that a minimum of 2 X Main drains are installed 2 metres apart. All Flow rates listed do not exceed 0.5 m/s velocity.Flow rate : 43 m3/h | 6.00 | Nos. | 43147.00 | 12215.00 | 73290.00 | 6500.00 | 39000.00 | 39960.00 | 239760.00 | 39000.00 | FAMILY FOUNTAINS
2.20 | Vacuum Point SITC of Vacuum Point & Plug - ABS - 2" / 1 1/2" threaded connection The vacuum point are used to connect the pool cleaner. | 21.00 | Nos. | 1288.00 | 4325.00 | 90825.00 | 1550.00 | 32550.00 | 1275.00 | 26775.00 | 26775.00 | DIVINE WATERCRAFTS & LANDSCAPES
2.30 | Return Inlet SITC of Wall/ Floor Inlet - ABS-2" threaded connection The return inlets filtered , threated water to the pool.They include the multiflow system , which allows the diameter ,and therefore the flow rate of the water through the inlets.Flow 12m3/h | 36.00 | Nos. | 1364.00 | 995.00 | 35820.00 | 1540.00 | 55440.00 | 1350.00 | 48600.00 | 35820.00 | COLOR DESIGN INDIA
2.40 | Mushroom/Cascade Nozzle SITC of Mushroom nozzle - AISI316 Stainless Steel . Flow rate: 50 LPM | 75.00 | Nos. | 27502.00 | 9500.00 | 712500.00 | 6400.00 | 480000.00 | 26500.00 | 1987500.00 | 480000.00 | FAMILY FOUNTAINS
2.50 | Wall conduit SITC of Wall Conduit with 2" Push Fitting are used to aid the installation of vacuum point.They are adaptable in length for easier installation of concrate pools | 18.00 | Nos. | 737.00 | 2450.00 | 44100.00 | 9800.00 | 176400.00 | 730.00 | 13140.00 | 13140.00 | DIVINE WATERCRAFTS & LANDSCAPES
2.60 | Stainless steel (316 grade) Waterfalls SITC of 300mm Waterfall. Flow rate: 50 LPM | 23.00 | Nos. | 32805.00 | 32802.00 | 754446.00 | 13500.00 | 310500.00 | 32100.00 | 738300.00 | 310500.00 | FAMILY FOUNTAINS
2.70 | Diffuser Header Assembly for Sheet fall. SITC of pvc diffuser header assembly for water sheet fall effect. | 4.00 | Nos. | 33532.00 | 22500.00 | 90000.00 | 4450.00 | 17800.00 | 33850.00 | 135400.00 | 17800.00 | FAMILY FOUNTAINS
3.10 | Chemical Dosing Pump SITC of 5 lit@7 bar metering dosing pump | 4.00 | Nos. | 23079.00 | 28200.00 | 112800.00 | 14400.00 | 57600.00 | 22000.00 | 88000.00 | 57600.00 | FAMILY FOUNTAINS
3.20 | SITC of 100 litre dosing tank | 4.00 | Nos. | 13332.00 | 9500.00 | 38000.00 | 2200.00 | 8800.00 | 11850.00 | 47400.00 | 8800.00 | FAMILY FOUNTAINS
3.30 | SITC of Manual Agitator Shaft Length 600mm | 4.00 | Nos. | 7323.00 | 30900.00 | 123600.00 | 7450.00 | 29800.00 | 7050.00 | 28200.00 | 28200.00 | DIVINE WATERCRAFTS & LANDSCAPES
4.10 | Underwater Light Supplying, installing, testing and commissioning of U stand LED lights, in stainless steel fixture, 12 / 24 V supply, fixed to wall with plugs & screws, complete with toughened glass cover, 9 w, 2.5 M flexible cable, for waterfall. | 35.00 | Nos. | 11312.00 | 13987.00 | 489545.00 | 9500.00 | 332500.00 | 11020.00 | 385700.00 | 332500.00 | FAMILY FOUNTAINS
4.20 | Transformer SITC of Transformer / power supply 12V / 24 V output. | 10.00 | Nos. | 5454.00 | 6500.00 | 65000.00 | 3850.00 | 38500.00 | 5375.00 | 53750.00 | 38500.00 | FAMILY FOUNTAINS
5.10 | Maintenance equipment: Vacuum Hose 'SITC of 1.5" (38mm) Floating Hose Spiralwound 2 color - 12 Metre | 2.00 | Nos. | 3838.00 | 5500.00 | 11000.00 | 5600.00 | 11200.00 | 3800.00 | 7600.00 | 7600.00 | DIVINE WATERCRAFTS & LANDSCAPES
5.20 | Wall Brush 'SITC of 18" Plastic/Aluminium Brush | 3.00 | Nos. | 1061.00 | 1734.00 | 5202.00 | 2250.00 | 6750.00 | 1050.00 | 3150.00 | 3150.00 | DIVINE WATERCRAFTS & LANDSCAPES
5.30 | Algae brush SITC of 5" Steel Algae Brush | 3.00 | Nos. | 1162.00 | 1450.00 | 4350.00 | 2545.00 | 7635.00 | 1150.00 | 3450.00 | 3450.00 | DIVINE WATERCRAFTS & LANDSCAPES
5.40 | Deep Net 'SITC of Deep Net | 3.00 | Nos. | 1273.00 | 1950.00 | 5850.00 | 2265.00 | 6795.00 | 1260.00 | 3780.00 | 3780.00 | DIVINE WATERCRAFTS & LANDSCAPES
5.50 | Flat Net 'SITC of Flat Net | 3.00 | Nos. | 1111.00 | 1250.00 | 3750.00 | 2140.00 | 6420.00 | 1100.00 | 3300.00 | 3300.00 | DIVINE WATERCRAFTS & LANDSCAPES
5.60 | 'Telescopic Pole SITC of 8 - 16' Aluminium Telescopic Handle - | 3.00 | Nos. | 3283.00 | 4443.00 | 13329.00 | 3000.00 | 9000.00 | 3250.00 | 9750.00 | 9000.00 | FAMILY FOUNTAINS
5.70 | Vacuum Head SITC of Vacuum Head Flexible with Swivel +Spring Clip Handle | 2.00 | Nos. | 1798.00 | 4250.00 | 8500.00 | 6800.00 | 13600.00 | 1800.00 | 3600.00 | 3600.00 | DIVINE WATERCRAFTS & LANDSCAPES
5.80 | Corner Brush SITC of Corner brush | 3.00 | Nos. | 768.00 | 950.00 | 2850.00 | 1250.00 | 3750.00 | 760.00 | 2280.00 | 2280.00 | DIVINE WATERCRAFTS & LANDSCAPES
5.90 | Test Kit Make SITC of Pool ID 5 in 1 pakaged | 3.00 | Nos. | 2045.00 | 1165.00 | 3495.00 | 1500.00 | 4500.00 | 2100.00 | 6300.00 | 3495.00 | COLOR DESIGN INDIA
6.00 | Interconnecting and Piping and valves for the complete system in UPVC schedule 40. the piping, valving shall complete with all required fittings like Tee, elbow, union, NRV, ball valve, butterfly valve (If required) complete in all respect. For Left Hand side External Fountain | 1.00 | Lot | 510050.00 | 245000.00 | 245000.00 | 285000.00 | 285000.00 | 498700.00 | 498700.00 | 245000.00 | COLOR DESIGN INDIA
7.00 | Interconnecting and Piping and valves for the complete system in UPVC schedule 40. the piping, valving shall complete with all required fittings like Tee, elbow, union, NRV, ball valve, butterfly valve (If required) complete in all respect. For Right Hand side External Fountain | 1.00 | Set | 575700.00 | 265000.00 | 265000.00 | 285000.00 | 285000.00 | 561000.00 | 561000.00 | 265000.00 | COLOR DESIGN INDIA
8.00 | Supply, installation. Testing and commissioning of electrical control panel for the auto operation of the system as mentioned above. For Left Hand side External Fountain | 1.00 | Set | 321180.00 | 95000.00 | 95000.00 | 350000.00 | 350000.00 | 310000.00 | 310000.00 | 95000.00 | COLOR DESIGN INDIA
9.00 | Supply, installation. Testing and commissioning of electrical control panel for the auto operation of the system as mentioned above. For Right Hand side External Fountain | 1.00 | Set | 351480.00 | 95000.00 | 95000.00 | 350000.00 | 350000.00 | 332500.00 | 332500.00 | 95000.00 | COLOR DESIGN INDIA
10.00 | Supply, installation, testing & commissioning of cabling, cable tray, earthing complete in all respect. For Left Hand side External Fountain | 1.00 | Lot | 164125.00 | 125000.00 | 125000.00 | 120000.00 | 120000.00 | 154000.00 | 154000.00 | 120000.00 | FAMILY FOUNTAINS
11.00 | Supply, installation, testing & commissioning of cabling, cable tray, earthing complete in all respect. For Right Hand side External Fountain | 1.00 | Set | 155540.00 | 125000.00 | 125000.00 | 120000.00 | 120000.00 | 151500.00 | 151500.00 | 120000.00 | FAMILY FOUNTAINS
12.10 | CORE CUTTING 150MM WALL THICKNESS 65MM | 62.00 | NOS | 788.00 | 350.00 | 21700.00 | 2800.00 | 173600.00 | 780.00 | 48360.00 | 21700.00 | COLOR DESIGN INDIA
12.20 | 100MM | 58.00 | NOS | 1202.00 | 450.00 | 26100.00 | 3600.00 | 208800.00 | 1190.00 | 69020.00 | 26100.00 | COLOR DESIGN INDIA
12.30 | 200MM | 9.00 | NOS | 1495.00 | 1200.00 | 10800.00 | 4600.00 | 41400.00 | 1480.00 | 13320.00 | 10800.00 | COLOR DESIGN INDIA
13.10 | Sealing / Waterproofing of corecuts :- using swelling bar tape ( Technonicol ) alongwith polymer based compound added to the filling concrete . This to be top finished / cured with dual layer of polymer compound make CICO / FOSROC / Dr . FIXIT. 65MM | 62.00 | NOS | 995.00 | 65.00 | 4030.00 | 1800.00 | 111600.00 | 995.00 | 61690.00 | 4030.00 | COLOR DESIGN INDIA
13.20 | 100MM | 58.00 | NOS | 1394.00 | 95.00 | 5510.00 | 2000.00 | 116000.00 | 1440.00 | 83520.00 | 5510.00 | COLOR DESIGN INDIA
13.30 | 200MM | 9.00 | NOS | 1737.00 | 225.00 | 2025.00 | 2800.00 | 25200.00 | 1750.00 | 15750.00 | 2025.00 | COLOR DESIGN INDIA
14.00 | Surface Chasing : to insert the pipes for the fountain nozzles, we shall chase the floor by manual tools and tackles. | 645.00 | SFT | 57.00 | 165.00 | 106425.00 | 180.00 | 116100.00 | 60.00 | 38700.00 | 38700.00 | DIVINE WATERCRAFTS & LANDSCAPES
15.00 | Screed Filling :- To fill the chased surface of the waterbody floor with screed of ratio 1:2:4 upto the desired levels manually or mechanically. | 225.00 | CFT | 250.00 | 699.00 | 157275.00 | 800.00 | 180000.00 | 246.00 | 55350.00 | 55350.00 | DIVINE WATERCRAFTS & LANDSCAPES
16.00 | Waterproofing of chased surface and also on top of screeding: surface to be waterproofed using polymer based compound of make CICO / FOSROC / Dr. FIXIT. Three coats of this compound with cement shall be applied alongwith heavy fiber reinforcement., as per manufacturers specification. | 1290.00 | SFT | 83.00 | 195.00 | 251550.00 | 750.00 | 967500.00 | 81.00 | 104490.00 | 104490.00 | DIVINE WATERCRAFTS & LANDSCAPES
17.00 | CIVIL items for the plumbing / piping :- Complete civil works for the plumbing pipes, etc. including excavation, honching of pipes with pcc (1:4:8), and soil filling. | 2.00 | L.S. | 171195.00 | 320000.00 | 640000.00 | 240000.00 | 480000.00 | 169500.00 | 339000.00 | 339000.00 | DIVINE WATERCRAFTS & LANDSCAPES
18.00 | Valve box :- SITC of PVB / PIMTAS valve box of dia 10 inches to hold the control valves. | 56.00 | Nos | 1909.00 | 2400.00 | 134400.00 | 2250.00 | 126000.00 | 1810.00 | 101360.00 | 101360.00 | DIVINE WATERCRAFTS & LANDSCAPES
19.00 | Auto Sump Pump: To supply and install a suitable automatic sump pump in the plantroom sump to discharge any water out of exigency. This is good for the safety of pumps, etc. Discharge 9 M3 @ 4 Mtrs head with 35 mm solid handling | 2.00 | NO | 25795.00 | 12500.00 | 25000.00 | 54598.00 | 109196.00 | 24900.00 | 49800.00 | 25000.00 | COLOR DESIGN INDIA
20.10 | Filter SITC of 15 micron cartridge filter with 1.5" pipe connection and necessary accessories such as pressure gauge, manual air vent, manual water drain etc., Filtration Velocity 25 m³/hr/m² Maximum working pressure : 2.5 Bar Flow rate = 17 m³/hr | 1.00 | Nos. | 29219.00 | 104927.00 | 104927.00 | 35500.00 | 35500.00 | 26430.00 | 26430.00 | 26430.00 | DIVINE WATERCRAFTS & LANDSCAPES
20.20 | Recirculation Pump Supply, installation, testing & commissioning of Submersible Openwell Type Pump 1 HP ,3 PH for the Filtration, (1 Working + 1 stand by), flowrate of 4.8 LPS @ 8 Mtrs head, including all necessary indigenous accessories as required to complete the installation. | 2.00 | Nos. | 23008.00 | 19000.00 | 38000.00 | 24500.00 | 49000.00 | 19400.00 | 38800.00 | 38000.00 | COLOR DESIGN INDIA
21.10 | Chemical feeder SITC of Chlorine / Bromine In line feeder . | 1.00 | Nos. | 11979.00 | 79000.00 | 79000.00 | 6750.00 | 6750.00 | 11860.00 | 11860.00 | 6750.00 | FAMILY FOUNTAINS
22.10 | Underwater Light Supply , installation , testing & commissioning of Under water round fountain light for Cascade Fountain, 12/24 V 12 W LED lights, nozzle mounted as per approved by Architect. | 19.00 | Nos. | 15004.00 | 15500.00 | 294500.00 | 7800.00 | 148200.00 | 14300.00 | 271700.00 | 148200.00 | FAMILY FOUNTAINS
23.00 | Interconnecting and Piping and valevs for the complete system in UPVC schedule 40. the piping, valving shall complete with all required fittings like Tee, elbow, union, NRV, ball valve, butterfly valve (If required) complete in all respect. Make Supreme / Prince / Finolex for internal fountain | 1.00 | Lot | 265125.00 | 54442.00 | 54442.00 | 310000.00 | 310000.00 | 258000.00 | 258000.00 | 54442.00 | COLOR DESIGN INDIA
24.00 | Supply, installation. Testing and commissioing of electrical control panel for the auto operation of the system as mentioend above. For internal fountain | 1.00 | Set | 212100.00 | 18900.00 | 18900.00 | 360000.00 | 360000.00 | 205000.00 | 205000.00 | 18900.00 | COLOR DESIGN INDIA
25.00 | Supply, installation, testing & commissioning of cabling, cable tray, earthing complete in all respect. For Internal fountain | 1.00 | Lot | 105545.00 | 21500.00 | 21500.00 | 144500.00 | 144500.00 | 102000.00 | 102000.00 | 21500.00 | COLOR DESIGN INDIA
26.00 | Screed Filling :- To fill the waterbody floor by screed ratio 1:2:4 upto the desired levels by manually or mechanically. | 325.00 | CFT | 250.00 | 699.00 | 227175.00 | 800.00 | 260000.00 | 246.00 | 79950.00 | 79950.00 | DIVINE WATERCRAFTS & LANDSCAPES
| Total in Figures |  |  |  |  | 7267999.00 |  | 8619786.00 |  | 9078025.00
Lowest Amount Quoted BY: COLOR DESIGN INDIA(7267999.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of External and Internal fountain in existing water bodies. Tender ID: 2021_AAI_70837_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | COLOR DESIGN INDIA | 7267999.00 | L1
| 2 | FAMILY FOUNTAINS | 8619786.00 | L2
| 3 | DIVINE WATERCRAFTS & LANDSCAPES | 9078025.00 | L3