## BoQ1
Government eProcurement System Created By: NANDKUMAR KUNDALE Created Date/Time: 26-Mar-2021 05:20 PM Tender Title: Annual Maintenance Contract of Fire Hydrant, Sprinkler system and Ventilation system at Integration Operational offices building, Mumbai for 2 Years (2021-23) Tender ID: 2021_AAI_71898_1
Tender Inviting Authority: AGM(E-E)
Name of Work: Annual Maintenance Contract of Fire Hydrant, Sprinkler system & Ventilation System at Integration Operational Offices Building, Mumbai for 2 Years (2021-23).
Contract No: 2021_AAI_71898_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Katyayni Engineering And Services(GSTN-07ADZPV0433A1ZG) |  | CENTRE TAP ENGINEERING(GSTN-24AGPPP8172K1ZP) |  | Manish Electricals(GSTN-22ABLPM9012E1ZY)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Annual Operation & Maintenance of Fire Hydrant, Fire Sprinkler system & Ventilation System including all fire pumps i.e Main Hydrant pump, Sprinkler pump, Jockey pump & Booster pump, Internal and External hydrants, all valves, Hose reel, Hose Boxes, Fire LT Panel, Diesel pump (Except Diesel Engine), sprinklers, fire alarm valve, SS braided flexible, Smoke Exhaust Fans, Jet Fans, In-Line fan for Atrium, Exhaust and Ventilation Panel etc as required. Work includes preventive maintenance of pumps, ventilation fans and other equipments, attending complaints/faults/breakdown and taking rectification action to ensure serviceability & satisfactory working condition of system, maintaining water pressure as required including testing of fire hydrant and fire Sprinkler system and ventilation system and maintaining records by deploying qualified manpower in General shift (shift of eight hours) on all working days including saturdays, holiday except sunday as per special conditions of contract and additional special conditions of contract. | 24.00 | Month | 43437.00 | 37000.00 | 888000.00 | 43000.00 | 1032000.00 | 41000.00 | 984000.00 | 888000.00 | Katyayni Engineering And Services
2.00 | Painting of various MS/GI pipe line of Fire Hydrant system and Fire sprinkler system including Pumps, Hose boxes, by one and more coat of red oxide metal primer and synthetic enamel paint of approved brand and colour including cleaning and scrapping of old paint with metal brush/ emery paper including numbering of hose boxes and writing the names on the pumps and panels with the paint complete etc. as required details as below :
2.01 | Main Hydrant Pump (75 KW) | 1.00 | Each | 750.00 | 500.00 | 500.00 | 350.00 | 350.00 | 2500.00 | 2500.00 | 350.00 | CENTRE TAP ENGINEERING
2.02 | Main Sprinkler Pump (75 KW) | 1.00 | Each | 750.00 | 500.00 | 500.00 | 350.00 | 350.00 | 2500.00 | 2500.00 | 350.00 | CENTRE TAP ENGINEERING
2.03 | Jockey Pump (7.5 KW) | 1.00 | Each | 750.00 | 500.00 | 500.00 | 350.00 | 350.00 | 2500.00 | 2500.00 | 350.00 | CENTRE TAP ENGINEERING
2.04 | Fire Engine Pump (83 HP) | 1.00 | Each | 750.00 | 500.00 | 500.00 | 350.00 | 350.00 | 2500.00 | 2500.00 | 350.00 | CENTRE TAP ENGINEERING
2.05 | Booster Pump (12.5HP) | 1.00 | Each | 360.00 | 500.00 | 500.00 | 150.00 | 150.00 | 1500.00 | 1500.00 | 150.00 | CENTRE TAP ENGINEERING
2.06 | M.S/GI pipe (Size 25 mm to 200 mm) | 200.00 | Sq. Meter | 150.00 | 80.00 | 16000.00 | 80.00 | 16000.00 | 280.00 | 56000.00 | 16000.00 | Katyayni Engineering And Services, CENTRE TAP ENGINEERING
2.07 | Hose Box (900 x 600 x 500 mm) including MS supports. | 13.00 | Job | 500.00 | 400.00 | 5200.00 | 200.00 | 2600.00 | 1000.00 | 13000.00 | 2600.00 | CENTRE TAP ENGINEERING
3.00 | Rewinding of 7.5 KW capacity 3 phase, 415 V AC supply Jockey Pump motor with suitable gauge copper wire including overhauling/servicing, replacement of ball bearings, varnishing, baking, dismantling, re-assembling, including transportation from site to contractor’s workshop & back to site, loading, unloading, testing and commissioning etc. complete as required. (Credit towards dismantled copper wire & damaged parts which shall be replaced may be considered the property of contractor accordingly rate shall be quoted) | 1.00 | Job | 19500.00 | 7500.00 | 7500.00 | 10000.00 | 10000.00 | 7500.00 | 7500.00 | 7500.00 | Katyayni Engineering And Services, Manish Electricals
4.00 | Supply of 15 mm standard response, quartzoid bulb Pendent type sprinkler of rating 68 °C. | 5.00 | Each | 350.00 | 3150.00 | 15750.00 | 180.00 | 900.00 | 4500.00 | 22500.00 | 900.00 | CENTRE TAP ENGINEERING
5.00 | Supply of 15 mm standard response, quartzoid bulb Upright type sprinkler of rating 68 °C. | 5.00 | Each | 350.00 | 3150.00 | 15750.00 | 180.00 | 900.00 | 4500.00 | 22500.00 | 900.00 | CENTRE TAP ENGINEERING
6.00 | Supply of 15 mm standard response, quartzoid bulb side wall type sprinkler of rating 68 °C. | 5.00 | Each | 350.00 | 3150.00 | 15750.00 | 180.00 | 900.00 | 4500.00 | 22500.00 | 900.00 | CENTRE TAP ENGINEERING
7.00 | Supply of UL approved SS Braided flexible drops 25 mm dia capable to withstand maximum working pressure of 175 PSI, minimum length 1.5meter . | 5.00 | Each | 1500.00 | 3500.00 | 17500.00 | 1000.00 | 5000.00 | 5500.00 | 27500.00 | 5000.00 | CENTRE TAP ENGINEERING
8.00 | Supply & Fixing of following size cast Iron foot valve with strainer for negative suction complete etc. as required.
8.01 | 200 mm dia | 2.00 | Each | 12000.00 | 8000.00 | 16000.00 | 6000.00 | 12000.00 | 6000.00 | 12000.00 | 12000.00 | CENTRE TAP ENGINEERING, Manish Electricals
8.02 | 80 mm dia | 1.00 | Each | 5000.00 | 2250.00 | 2250.00 | 3000.00 | 3000.00 | 4000.00 | 4000.00 | 2250.00 | Katyayni Engineering And Services
9.00 | Supply & Fixing of Pressure Switch including connection complete etc. as required. (make: Danfoss, Model : KP 36 or Equivalent approved make) | 2.00 | Each | 2500.00 | 4500.00 | 9000.00 | 1500.00 | 3000.00 | 9000.00 | 18000.00 | 3000.00 | CENTRE TAP ENGINEERING
10.00 | Supply & Fixing of pressure gauge of 100 mm dia , 0-21 kg/sq.cm range with 15 mm dia stop cock valve complete etc. as required. | 2.00 | Each | 1500.00 | 3500.00 | 7000.00 | 1000.00 | 2000.00 | 3500.00 | 7000.00 | 2000.00 | CENTRE TAP ENGINEERING
| Total in Figures |  |  |  |  | 1018200.00 |  | 1089850.00 |  | 1208000.00
Lowest Amount Quoted BY: Katyayni Engineering And Services(1018200.00)

## BOQ Summary
BOQ Summary Details Tender Title: Annual Maintenance Contract of Fire Hydrant, Sprinkler system and Ventilation system at Integration Operational offices building, Mumbai for 2 Years (2021-23) Tender ID: 2021_AAI_71898_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Katyayni Engineering And Services | 1018200.00 | L1
| 2 | CENTRE TAP ENGINEERING | 1089850.00 | L2
| 3 | Manish Electricals | 1208000.00 | L3