## BoQ1
Government eProcurement System Created By: KASI R Created Date/Time: 15-Mar-2021 02:41 PM Tender Title: Provision of outdoor feeder panels for fire station, MT section and cargo including cable laying at Coimbatore International Airport. Tender ID: 2021_AAI_71900_1
Tender Inviting Authority: Asst.Gen.Manager (E-E), Airports Authority of India, Coimbatore International Airport, Coimbatore - 641014.
Name of Work: Provison of outdoor feeder panels for fire station, MT section & cargo i/c cable laying at Coimbatore International Airport.
Tender ID: 2021_AAI_71900_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | vk sam engineering(GSTN-33AMZPS4037L1ZA) |  | LAKSHMI ELECTRICAL ENTERPRISES(GSTN-33AACFL6352N1Z4) |  | BR Power Control and Automation Services(GSTN-06AREPS4024K1ZP) |  | C P MONCHESTER ELECTRICALS(GSTN-33AJOPP7842E1ZY) |  | SARASWAT ENGINEERING SERVICES(GSTN-27AAZFS6239C1ZO) |  | jaydeep agency corporation(GSTN-24ACIPP6157B1ZQ) |  | GRENEL POWERS PVT.LTD.(GSTN-33AAECG2313H1Z5) |  | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED(GSTN-07ABDCS2796Q1ZH) |  | CHENNAI ENGINEERING SERVICES(GSTN-33AADFC4373K1ZH) |  | Manoprabha Electricals(GSTN-33AGNPM4749D3Z9) |  | Industrial Traders(GSTN-09ACJPC1773F1ZQ) |  | POWER ELECTRICAL WORKS(GSTN-33AADPT3125C1Z8) |  | Mona Generator Services Pvt. Ltd.(GSTN-07AAFCM4263P1ZZ) |  | KALKI ELECTRICALS(GSTN-29AGGPD2370J1ZE) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5) |  | EANDA ENGINEERING SOLUTIONS PVT LTD(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.01 | Supply of following size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor power cable conforming to IS 7098 (Part 1) amended upto date. 3.5 X 300 Sq.mm | 3000.00 | Mtr |  | 1114.00 | 3342000.00 | 990.00 | 2970000.00 | 1143.00 | 3429000.00 | 1116.00 | 3348000.00 | 991.00 | 2973000.00 | 1000.00 | 3000000.00 | 1200.00 | 3600000.00 | 900.00 | 2700000.00 | 1019.00 | 3057000.00 | 1088.00 | 3264000.00 | 1195.00 | 3585000.00 | 999.00 | 2997000.00 | 1000.00 | 3000000.00 | 960.00 | 2880000.00 | 1015.00 | 3045000.00 | 1000.00 | 3000000.00 | 2700000.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
1.02 | Supplying and making cable end termination with brass compression gland and aluminium lugs for following size of PVC insulated PVC sheathed/ XLPE aluminium conductor cable of 1.1 kV grade as required. 3.5C 300 Sq.mm | 12.00 | set |  | 950.00 | 11400.00 | 700.00 | 8400.00 | 1767.00 | 21204.00 | 1800.00 | 21600.00 | 1760.00 | 21120.00 | 1450.00 | 17400.00 | 936.00 | 11232.00 | 750.00 | 9000.00 | 1999.00 | 23988.00 | 600.00 | 7200.00 | 790.00 | 9480.00 | 850.00 | 10200.00 | 630.00 | 7560.00 | 2400.00 | 28800.00 | 800.00 | 9600.00 | 3000.00 | 36000.00 | 7200.00 | Manoprabha Electricals
1.03 | Laying and fixing of one number XLPE/ PVC insulated PVC sheathed aluminium/copper conductor cable of 1.1 KV grade of following sizes on wall/ surface as required. Above 185 Sq.mm upto 400 Sq.mm (Clamped with 40X3mm MS flat clamp) | 1242.00 | Mtr |  | 70.00 | 86940.00 | 95.00 | 117990.00 | 139.00 | 172638.00 | 72.00 | 89424.00 | 116.00 | 144072.00 | 45.00 | 55890.00 | 182.00 | 226044.00 | 150.00 | 186300.00 | 199.00 | 247158.00 | 50.00 | 62100.00 | 198.00 | 245916.00 | 40.00 | 49680.00 | 200.00 | 248400.00 | 120.00 | 149040.00 | 150.00 | 186300.00 | 200.00 | 248400.00 | 49680.00 | POWER ELECTRICAL WORKS
1.04 | Laying and fixing of one number XLPE/ PVC insulated PVC sheathed aluminium/copper conductor cable of 1.1 KV grade of following sizes on cable tray as required(With Cable tie). Above 185 Sq.mm upto 400 Sq.mm | 60.00 | Mtr |  | 65.00 | 3900.00 | 50.00 | 3000.00 | 109.00 | 6540.00 | 90.00 | 5400.00 | 93.00 | 5580.00 | 45.00 | 2700.00 | 150.00 | 9000.00 | 80.00 | 4800.00 | 149.00 | 8940.00 | 50.00 | 3000.00 | 590.00 | 35400.00 | 30.00 | 1800.00 | 125.00 | 7500.00 | 100.00 | 6000.00 | 120.00 | 7200.00 | 150.00 | 9000.00 | 1800.00 | POWER ELECTRICAL WORKS
1.05 | Supplying and laying of following size HDPE pipe, PE-63, 6kg/cm2, ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm depth) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. 110mm dia (List of approved makes/ ISI marked) | 1640.00 | Mtr |  | 575.00 | 943000.00 | 510.00 | 836400.00 | 526.00 | 862640.00 | 450.00 | 738000.00 | 623.00 | 1021720.00 | 375.00 | 615000.00 | 341.00 | 559240.00 | 385.00 | 631400.00 | 799.00 | 1310360.00 | 200.00 | 328000.00 | 248.00 | 406720.00 | 525.00 | 861000.00 | 665.00 | 1090600.00 | 460.00 | 754400.00 | 420.00 | 688800.00 | 380.00 | 623200.00 | 328000.00 | Manoprabha Electricals
1.06 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required. Above 185 Sq.mm upto 400 Sq.mm | 1640.00 | Mtr |  | 60.00 | 98400.00 | 90.00 | 147600.00 | 133.00 | 218120.00 | 63.00 | 103320.00 | 93.00 | 152520.00 | 45.00 | 73800.00 | 112.00 | 183680.00 | 80.00 | 131200.00 | 149.00 | 244360.00 | 12.00 | 19680.00 | 70.00 | 114800.00 | 30.00 | 49200.00 | 149.00 | 244360.00 | 100.00 | 164000.00 | 60.00 | 98400.00 | 150.00 | 246000.00 | 19680.00 | Manoprabha Electricals
1.07 | Supply and making of straght through cable jointing with cast resin compound, including ferrule and other joiinting materias, XLPE alumium conducor cable of 11KV grade as required. 3.5C X 300 Sqmm | 10.00 | Each |  | 4100.00 | 41000.00 | 4500.00 | 45000.00 | 7172.00 | 71720.00 | 4500.00 | 45000.00 | 4862.00 | 48620.00 | 2450.00 | 24500.00 | 8394.00 | 83940.00 | 9500.00 | 95000.00 | 9999.00 | 99990.00 | 5000.00 | 50000.00 | 11000.00 | 110000.00 | 4000.00 | 40000.00 | 2300.00 | 23000.00 | 4000.00 | 40000.00 | 6500.00 | 65000.00 | 1400.00 | 14000.00 | 14000.00 | EANDA ENGINEERING SOLUTIONS PVT LTD
1.08 | Supply, Installation, Testing and Commissioning of LT Panel, cubicle type, made out of 2mm thick CRCA sheet steel, totally enclosed, IP-54, protection free standing, floor mounting, dust and vermin proof, outdoor, compartmentalized, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with bus bars extendanble on both sides, interconnections with suitable size of copper leads/ solid aluminium strips/ cables. Incoming : 2 Nos. MCCB, 400Amps, 4 Pole, 35 kA with adjustable setting, Electronic trip unit with O/C, S/C & Neutral protection. Bus Coupler 1 Nos. MCCB, 400Amps, 4 Pole, 35 kA with adjustable setting, thermal magnetic release with O/C & S/C protection. Busbars 4P aluminum bus bars of 500A capacity with heat shrinkable coloured sleeves i/c SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 35 KA for 1 sec. Instruments & accessories 1 No. 96mmX95mm digital type Voltmeter suitable range for 3phase,4 wire operation with LED display and selector switch backup by 3 nos of 2Amp MCB - 2 sets. 3 Nos of LED type phase indicating lamps (RYB) with controlled by 2Amp MCB - 3 set. 1 Set Rotary operating mechanism and terminal extension spreaders with door interlock for all the MCCB's. Outgoing : 2 Nos. MCCB, 250Amps, 4 Pole, 35 kA with adjustable setting, thermal magnetic release with O/C & S/C protection. 4 Nos. MCCB, 160Amps, 4 Pole, 35 kA with adjustable setting, thermal magnetic release with O/C & S/C protection. | 3.00 | Each |  | 339650.00 | 1018950.00 | 360000.00 | 1080000.00 | 286461.00 | 859383.00 | 180000.00 | 540000.00 | 293695.00 | 881085.00 | 385000.00 | 1155000.00 | 250000.00 | 750000.00 | 537000.00 | 1611000.00 | 509999.00 | 1529997.00 | 432080.00 | 1296240.00 | 300000.00 | 900000.00 | 450000.00 | 1350000.00 | 100000.00 | 300000.00 | 220000.00 | 660000.00 | 315000.00 | 945000.00 | 190000.00 | 570000.00 | 300000.00 | Mona Generator Services Pvt. Ltd.
1.09 | SITC of LT panel, cubicle type , made out of 2mm thick CRCA sheet for frame work and covers (1.6mm thick for internal partitions), 3mm thick for gland plates i/c. cleaning & finishing complete with 7 tank process for powder coating , totally enclosed IP42, free standing, Floor mounting, dust and vermin proof, indoor, compartmentalized, suitable for operation on 3 phase and neutral, 415V , 50Hz AC system with extensible type TPN aluminum bus bars of high conductivity, SMC bus bar supports with short circuit withstand capacity of 50kA for 1 sec., bottom base channel of MS section not less than 100mm X 50mm X 5mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth of size 25mm X 5mm at the rear with 2 no’s earth stud solid connections from main bus bar to switchgears with required size of Al. bus bars and control wiring with 2.5sqmm PVC insulated copper conductor Single core cable , cable alleys, cable gland plates in two half , supply & installation of following switchgears, metering instruments and accessories in the Main Essential LT panel and as per specifications. Incomer: a) 400A, 50kA, 4 pole MCCB with adjustable setting, Electronic trip unit with O/C, S/C & Neutral protection.-2No b) 400/5 Amps CTs-02 set c) LED type indicating lamps with control fuse -02 set d) 0-500 volts Voltmeter (Digital type) with selector switch -02 set e) Ammeter (digital type & in-built selector switch) with CTs (Suppressed scale)- 2 set Bus Bar a) TPN Aluminum bus bar suitable for 500 Amps with heat shrinkable coloured sleeves i/c SMC bus bar supports & their spacing etc. for withstanding fault level of 50kA for 1 sec. Bus coupler a) 400 Amps, 50 kA, 4 pole MCCB confirming to IS-13947-2 1993 as amended up-to-date - 01 No. Outgoing feeders having the following: i) 160 A, 50kA, 4 pole MCCB -01 Nos ii) 125A, 50 kA, 4 pole MCCB -13 Nos | 1.00 | Each |  | 505150.00 | 505150.00 | 475000.00 | 475000.00 | 473687.00 | 473687.00 | 300000.00 | 300000.00 | 516335.00 | 516335.00 | 576000.00 | 576000.00 | 415000.00 | 415000.00 | 322000.00 | 322000.00 | 799999.00 | 799999.00 | 665000.00 | 665000.00 | 600000.00 | 600000.00 | 560000.00 | 560000.00 | 310000.00 | 310000.00 | 350000.00 | 350000.00 | 545000.00 | 545000.00 | 300000.00 | 300000.00 | 300000.00 | C P MONCHESTER ELECTRICALS, EANDA ENGINEERING SOLUTIONS PVT LTD
1.10 | Earthing with GI earth plate 600 mm X 600 mm X 6mm thick including accessories, and providing masonary enclosure with cover plate having locking arrangements and watering pipe of 2.7 Meter long etc. with charcoal/coke and salt as required. | 8.00 | set |  | 10500.00 | 84000.00 | 6000.00 | 48000.00 | 18354.00 | 146832.00 | 4500.00 | 36000.00 | 10634.00 | 85072.00 | 5800.00 | 46400.00 | 6216.00 | 49728.00 | 6800.00 | 54400.00 | 6999.00 | 55992.00 | 5000.00 | 40000.00 | 10000.00 | 80000.00 | 8500.00 | 68000.00 | 9000.00 | 72000.00 | 8000.00 | 64000.00 | 6500.00 | 52000.00 | 20000.00 | 160000.00 | 36000.00 | C P MONCHESTER ELECTRICALS
1.11 | Supply & laying 25 mm X 5 mm G.I strip at 0.50 Meter below ground as strip earth electrode, including connection/terminating with G.I nut, bolt, spring, washer etc. as required | 100.00 | Mtr |  | 210.00 | 21000.00 | 175.00 | 17500.00 | 185.00 | 18500.00 | 180.00 | 18000.00 | 237.00 | 23700.00 | 120.00 | 12000.00 | 131.00 | 13100.00 | 180.00 | 18000.00 | 139.00 | 13900.00 | 200.00 | 20000.00 | 140.00 | 14000.00 | 160.00 | 16000.00 | 120.00 | 12000.00 | 200.00 | 20000.00 | 130.00 | 13000.00 | 150.00 | 15000.00 | 12000.00 | jaydeep agency corporation, Mona Generator Services Pvt. Ltd.
1.12 | Dismantling bituminous road by manually/ mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 meters lead as per direction of Engineer-in-charge and Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand :4 graded stone aggregate 20 mm nominal size) excluding the cost of centering and shuttering - All work up to plinth level including form work etc as required. | 9.00 | Cum |  | 7500.00 | 67500.00 | 7000.00 | 63000.00 | 3631.00 | 32679.00 | 9000.00 | 81000.00 | 8700.00 | 78300.00 | 375.00 | 3375.00 | 8549.00 | 76941.00 | 850.00 | 7650.00 | 7999.00 | 71991.00 | 1000.00 | 9000.00 | 4975.00 | 44775.00 | 5000.00 | 45000.00 | 10611.11 | 95499.99 | 6000.00 | 54000.00 | 1500.00 | 13500.00 | 40000.00 | 360000.00 | 3375.00 | jaydeep agency corporation
1.13 | SITC of On-Load manual Change over Switch-Sheet Steel enclouser (conforms to IEC 60947-3), FP 63A, 415V AC supply | 1.00 | Each |  | 6900.00 | 6900.00 | 5000.00 | 5000.00 | 6692.00 | 6692.00 | 18006.00 | 18006.00 | 8041.00 | 8041.00 | 5500.00 | 5500.00 | 6860.00 | 6860.00 | 10500.00 | 10500.00 | 6599.00 | 6599.00 | 6000.00 | 6000.00 | 10000.00 | 10000.00 | 8532.00 | 8532.00 | 6080.01 | 6080.01 | 40000.00 | 40000.00 | 5500.00 | 5500.00 | 30000.00 | 30000.00 | 5000.00 | LAKSHMI ELECTRICAL ENTERPRISES
| Total in Figures |  |  |  |  | 6230140.00 |  | 5816890.00 |  | 6319635.00 |  | 5343750.00 |  | 5959165.00 |  | 5587565.00 |  | 5984765.00 |  | 5781250.00 |  | 7470274.00 |  | 5770220.00 |  | 6156091.00 |  | 6056412.00 |  | 5417000.00 |  | 5210240.00 |  | 5674300.00 |  | 5611600.00
Lowest Amount Quoted BY: KALKI ELECTRICALS(5210240.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of outdoor feeder panels for fire station, MT section and cargo including cable laying at Coimbatore International Airport. Tender ID: 2021_AAI_71900_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | KALKI ELECTRICALS | 5210240.00 | L1
| 2 | C P MONCHESTER ELECTRICALS | 5343750.00 | L2
| 3 | Mona Generator Services Pvt. Ltd. | 5417000.00 | L3
| 4 | jaydeep agency corporation | 5587565.00 | L4
| 5 | EANDA ENGINEERING SOLUTIONS PVT LTD | 5611600.00 | L5
| 6 | Awasthi Electric Works | 5674300.00 | L6
| 7 | Manoprabha Electricals | 5770220.00 | L7
| 8 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED | 5781250.00 | L8
| 9 | LAKSHMI ELECTRICAL ENTERPRISES | 5816890.00 | L9
| 10 | SARASWAT ENGINEERING SERVICES | 5959165.00 | L10
| 11 | GRENEL POWERS PVT.LTD. | 5984765.00 | L11
| 12 | POWER ELECTRICAL WORKS | 6056412.00 | L12
| 13 | Industrial Traders | 6156091.00 | L13
| 14 | vk sam engineering | 6230140.00 | L14
| 15 | BR Power Control and Automation Services | 6319635.00 | L15
| 16 | CHENNAI ENGINEERING SERVICES | 7470274.00 | L16