## BoQ1
Government eProcurement System Created By: DOMA JAWALEKAR Created Date/Time: 09-Apr-2021 06:08 PM Tender Title: SITC of Pressure Pump and other accessories for make up tank of HVAC plant at Aurangabad Airport. Tender ID: 2021_AAI_72781_1
Tender Inviting Authority: Asstt. Gen.Manager (Engg.-Electrical), Airports Authority of India, Aurangabad Airport, Aurangabad - 431007 (Maharashtra).
Name of Work: SITC of Pressure Pump and other accessories for make-up tank of HVAC plant at Aurangabad Airport.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | AIRTECH ENGINEERS(GSTN-27AJHPB7042D1ZM) |  | NAQVI BROTHERS(GSTN-09ADHPN6210D1ZT)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply , Installation , Testing and Commissioning of automatic Pressure Motor Pump set of 1 HP, suitable to operate on single phase, 230V, 50Hz AC supply with following specifications. Head 42 meter, Suction X delivery - 25 X 25 mm, RPM 2750, copper winding, discharge - 48 LPM, warranty - 18 months, high performance corrosion resistance , impeller made of brass, pump shaft made up of carbon steel , carbon ceramic mechanical seat etc. along with alignment and required accessories for SITC etc. as required. | 2.00 | Job |  | 35000.00 | 70000.00 | 10000.00 | 20000.00 | 20000.00 | NAQVI BROTHERS
2.00 | Supply of single phase, DOL starter, 1.5 HP having thermal protection range from 9-13 Amp with HRC fuse of suitable rating etc. as required. | 2.00 | Each |  | 4500.00 | 9000.00 | 7500.00 | 15000.00 | 9000.00 | AIRTECH ENGINEERS
3.00 | Supply and fixing of 100 mm , B class - MS pipe(80mtrs) along with C class short 100 mm Elbows(06 Nos.) in existing trench confirming to IS 1239 part-I (2004) etc. as required. | 1.00 | Job |  | 95000.00 | 95000.00 | 150000.00 | 150000.00 | 95000.00 | AIRTECH ENGINEERS
4.00 | Supply of High accuracy Pressure Gauge - range 0 to 150 PSI / 0 to 10.6 Kg per sq.cm. as required. | 6.00 | Each |  | 2000.00 | 12000.00 | 2000.00 | 12000.00 | 12000.00 | AIRTECH ENGINEERS, NAQVI BROTHERS
5.00 | Supply of High accuracy Stainless steel vertical analog Temperature Gauge - range 0 to 50 degree Celsius as required. | 14.00 | Each |  | 1500.00 | 21000.00 | 3500.00 | 49000.00 | 21000.00 | AIRTECH ENGINEERS
6.00 | Supply of 100 mm , PN 1.6, cast iron , EPDM rubber lining seat , Butterfly Wafer valve with handlever (Stem made up of AISI 401 stainless steel) as required. | 5.00 | Each |  | 4500.00 | 22500.00 | 4500.00 | 22500.00 | 22500.00 | AIRTECH ENGINEERS, NAQVI BROTHERS
7.00 | Supply of Daikin make chiller spare(Single screw water cooled chillers PFS 330.3 ) : Discharge Pressure transducer (Part No. SE8121019). | 2.00 | Each |  | 14000.00 | 28000.00 | 8500.00 | 17000.00 | 17000.00 | NAQVI BROTHERS
8.00 | Supply of Daikin make chiller spare(Single screw water cooled chillers PFS 330.3 ) : Suction Pressure transducer as required. | 2.00 | Each |  | 14000.00 | 28000.00 | 8500.00 | 17000.00 | 17000.00 | NAQVI BROTHERS
9.00 | Supply of Daikin make chiller spare(Single screw water cooled chillers PFS 330.3 ) : Anti freeze thermostat (Range:- 25 degree Celsius to 15 degree Celsius) as required. | 3.00 | Each |  | 18000.00 | 54000.00 | 4500.00 | 13500.00 | 13500.00 | NAQVI BROTHERS
10.00 | Supply of Daikin make chiller spare (Single screw water cooled chillers PFS 330.3 ) : HRC fuse of rating 400 Amp., 1000 V ac, 50 kA (Siemens, 3NE3 232-0B or equivalent) as required. | 6.00 | Each |  | 450.00 | 2700.00 | 10000.00 | 60000.00 | 2700.00 | AIRTECH ENGINEERS
11.00 | Supply of Daikin make chiller spare (Single screw water cooled chillers PFS 330.3 ) : Water Flow switch (Make : Honeywell, WFS-1001-H) as required. | 10.00 | Each |  | 4500.00 | 45000.00 | 3500.00 | 35000.00 | 35000.00 | NAQVI BROTHERS
12.00 | Supply of Daikin make chiller spare(Single screw water cooled chillers PFS 330.3 ) : Chilled water temperture sensor (Make : Jumo, PT 100, range : - 20 to 80 degree Celsius) as required. | 3.00 | Each |  | 6500.00 | 19500.00 | 1500.00 | 4500.00 | 4500.00 | NAQVI BROTHERS
13.00 | Supply of Daikin make chiller spare (Single screw water cooled chillers PFS 330.3 ) : Oil Pressure switch (Part No. SE 8121 019) as required. | 2.00 | Each |  | 12000.00 | 24000.00 | 6000.00 | 12000.00 | 12000.00 | NAQVI BROTHERS
14.00 | Descaling of following Daikin make (McQuay) chillers condenser copper tubes by with suitable chemical such as sulfuric/ sulphamic acid etc. with maintaining pH (without damaging condenser tubes), circulation up to such hrs. by opening both sides caps of condenser & brushing of condenser by using nylon brush with manually/ machine to remove hard scale of inside condenser tubes. The scaling should be removed to reduce the high discharge pressure upto 825kPa in chiller unit & ensuring sucessful operation of 3 compressors in each chiller after descaling as per daiking specification. Chiller Model/ Rating : Single screw water cooled chillers PFS 330.3 (04 Nos), Chiller Sr. No. W08430162, W08430163, W08430164 & W08430165. | 4.00 | Job |  | 55000.00 | 220000.00 | 45000.00 | 180000.00 | 180000.00 | NAQVI BROTHERS
| Total in Figures |  |  |  |  | 650700.00 |  | 607500.00
Lowest Amount Quoted BY: NAQVI BROTHERS(607500.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of Pressure Pump and other accessories for make up tank of HVAC plant at Aurangabad Airport. Tender ID: 2021_AAI_72781_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | NAQVI BROTHERS | 607500.00 | L1
| 2 | AIRTECH ENGINEERS | 650700.00 | L2