## BoQ1
Government eProcurement System Created By: Lakhan Pal Singh Solanki Created Date/Time: 18-Jun-2021 04:31 PM Tender Title: SITC of 02 Nos of 250 KVA DG Sets at Kargil Airport Tender ID: 2021_AAI_75523_1
Tender Inviting Authority: AGM (ENGG-ELECT), AAI, SRINAGAR INTERNATIONAL AIRPORT, SRINAGAR, J&K-190007.
Name of Work: SITC of 02 Nos of 250 KVA DG Sets at Kargil Airport.
Contract No: <Enter Contract No Details>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ECS ENGINEERING PVT LTD(GSTN-09AABCE5944P1Z1) |  | ARNAV ENGINEERING CONSULTANCY SERVICES(GSTN-07ABKFA7102Q1Z4) |  | Mona Generator Services Pvt. Ltd.(GSTN-07AAFCM4263P1ZZ) |  | National Engineering(GSTN-01AJFPM5466Q1ZS) |  | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION(GSTN-09AOTPS2578C1ZC)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | DG Set. Supply Installation Testing Commissioning of "Silent Type" Radiator Cooled, Diesel Generating Set along with having Prime mover power rating of 250 KVA at 0.8 lagging power factor, 415 volts, 1500 RPM, 3 phase system, as per ISO 8528 and consisting of the following: (a) Diesel Engine: 4 stroke, 12/16 cylinder, electronic governor, power command control module, radiator cooled, electric start, of suitable BHP at 1500 RPM suitable for above output of alternator at 40 Degree C, 50% RH & at 1000 Meter MSL and conforming to BS 5514, BS 649, IS 10000, capable of taking 10% over loading for one hour after 12 hours of continuous operation. The engine will be fitted complete with all the required accessories. (b) Alternator: Synchronous alternator rated for 250 KVA, 415 volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at 40 Degree C, 50% RH & at 1000 Meter MSL. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self-regulated through AVR, QDCT for synchronising, terminal arrangement i/c 1000A alumunium bus-duct box with other associated equipment conforming to IS:4722 / BS 2613 suitable for tropical conditions and with class F / H insulation. (c) Base Frame & Foundation: Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on existing concrete foundation and vibration isolation arrangement as per recommendations of manufacturer. (d) Fuel Tank: Day service fuel tank of 990 litres capacity fabricated out of 3 mm thick M.S. sheet complete with all standard accessories and fuel piping between fuel tank and diesel engine with MS class 'C' pipes of suitable dia. Complete with valves, level indications & accessories as required as per specifications. (e) Exhaust System: Dry Exhaust manifold with residential exhaust silencer and catalytic convertor. (f) Starting System: 24V DC starting system comprising of starter motors: voltage regulator and arrangement for initial excitation complete with suitable nos. of batteries with MS battery stand etc. as required as per specifications. (g) Acoustic Enclosure : Acoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere as per specifications. (h) The work should be as per Central Electrical Authority / Pollution control board standards. (i) Suitable space heater/cold kit accessory to be provided to suit the environmental conditions of Kargil. | 2.00 | Set |  | 1750000.00 | 3500000.00 | 1250000.00 | 2500000.00 | 1424777.00 | 2849554.00 | 1567400.00 | 3134800.00 | 1600000.00 | 3200000.00 | 2500000.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
2.00 | Fabricating, Installing, Testing and commissioning of automatic mains failure control Panel, IP 54 suitable for 415 V+/-10%, 3 phase, 4 wire 50 Hz AC supply system made up of 2 mm thick CRCA sheet duly powder coated frame work and 3 mm thick for gland plates including auto by pass panel suitable for 250 KVA silent type DG set complete with digital AMF microprocessor based relay, timers, set of CTs for metering and protection and energy analyser to indicate currents, phase and line voltages, frequency, power factor, KWH, KVARH,provision for overload, short circuit, restricted earth fault, under frequency and other accessories required including control cabling from AMF panel to diesel engine and elsewhere, if required all complete inter locking etc complete as required. | 2.00 | JOB |  | 412000.00 | 824000.00 | 255000.00 | 510000.00 | 127777.00 | 255554.00 | 424100.00 | 848200.00 | 450000.00 | 900000.00 | 255554.00 | Mona Generator Services Pvt. Ltd.
3.00 | Supplying and fixing of exhaust gas piping of 150 mm dia. for 250 KVA D.G. Set welded black MS, B (medium) Class pipe conforming to IS:1239 cut to required lengths and installed with necessary bends, supports and clamps, anti-vibration mountings, insulation of exhaust system with 50 mm thick mineral wool / Rockwool having density not less than 120 Kg / Cucm, wiremesh & cladding with 0.6 mm thick aluminum sheet etc. as required as per specifications. | 15.00 | Meter |  | 4500.00 | 67500.00 | 3900.00 | 58500.00 | 8667.00 | 130005.00 | 3300.00 | 49500.00 | 35000.00 | 525000.00 | 49500.00 | National Engineering
4.00 | ESSENTIAL LT PANEL Supply, Installation, Testing and Commissioning of cubicle type LT panel, IP 54 suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars for high conductivity, SMC bus bar supports, with short circuit withstand capacity as per design subject to minimum 50 KA for 1 sec , bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common Copper earth bus bar of size as per IS 3043 subject to minimum 50 mm x 6 mm at the rear with 2 Nos. earth stud, solid / flexible connections from main earth bus bar to switchgears with required size of Cooper / Aluminium conductors / bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half including provision of SPD's. Surge Protection Devices (SPDS) (Type 2 / Class B) i/c providing following switchgears / accessories as per specifications. Suitable capacity , Direct Low Pressure (DLP) Assembly with automatic valve, push in connector for tube, Clean agent, mounting bracket, End of Line adopter and low pressure switch for monitoring system activation. i) Linear Pneumatic Heat detection tube with all necessary & supports ii) Master Control Unit for controlling each system, complete with pressure switches, buzzers and electronic hooters, including all necessary accessories + electrical wiring to make each entire system functional. (Panel shall conform to IEC 61439/1-2 & shall be IP-54 & of Form-4b construction). Incomer 2 Nos. MCCB, 400 Amps, 4 Pole, 35 kA , (Ics = Icu = 100%) with adjustable setting , thermal magnetic release with O/ C & S / C protection,Digital KWH Meter with voltage and current display RS485 module of class-0.5 accuracy with suitable range of cast resin CT including connections etc as required. Each Incomer shall have one set of the following items: Intelligent multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with communication facility (RS485 port), THD and Individual order harmonics upto 31st Order. LED display with required Nos CTs, 800 / 5,15 VA, class 1.0 and control circuit wiring with 2 Amp MCB for controlling. 1 Set of Indication Lamps, LED type, R,Y,B Phase indicating lamp with 2 Amp MCB for controlling. Bus Coupler 1 Nos. MCCB, 400 Amps, 4 Pole, 35 kA , (Ics = Icu = 100%) with adjustable setting , thermal magnetic release with 1 Set of ON/ OFF Indicating LED Lamps with 2 Amp MCB. | 1.00 | Job |  | 534000.00 | 534000.00 | 355000.00 | 355000.00 | 617777.00 | 617777.00 | 459600.00 | 459600.00 | 400000.00 | 400000.00 | 355000.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
4.10 | Bus Bar TPN aluminium extensible type main bus bars of minimum 500 Amps. capacity with heat shrinkable coloured sleeves having 100% neutral bus as that of phase i/c DMC / SMC bus bars supports at required intervals complete for cross section, size supports & having spacing etc. for withstanding fault level of 35 kA capacity for 1 sec. Outgoings 2 Nos. MCCB, 100 Amps, 4 Pole, 35 kA , (Ics = Icu = 100%) with adjustable setting , thermal magnetic release etc as required. 3 Nos. MCCB, 63 Amps, 4 Pole, 35 kA , (Ics = Icu = 100%) with adjustable setting , thermal magnetic release etc as required. 04 Nos, 63 Amps , 4 Pole , 10 KA , C series , MCB etc complete as required. 02 Nos, 40 Amps , 4 Pole , 10 KA , C series , MCB etc complete as required. Note : 1 No ON, OFF indication lamp (LED type) with 2 Amp SP MCB for each outgoing. Space heater with thermostat and MCB Manual interlocking between incomers
5.00 | NON-ESSENTIAL LT PANEL Supply, Installation, Testing and Commissioning of cubicle type LT panel, IP 54 suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars for high conductivity, SMC bus bar supports, with short circuit withstand capacity as per design subject to minimum 50 KA for 1 sec , bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common Copper earth bus bar of size as per IS 3043 subject to minimum 50 mm x 6 mm at the rear with 2 Nos. earth stud, solid / flexible connections from main earth bus bar to switchgears with required size of Cooper / Aluminium conductors / bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half including provision of SPD's. Surge Protection Devices (SPDS) shall be provided at main LT incoming feeders (Type 1+2 / Class B) i/c providing following switchgears / accessories as per specifications. Suitable capacity , Direct Low Pressure (DLP) Assembly with automatic valve, push in connector for tube, Clean agent, mounting bracket, End of Line adopter and low pressure switch for monitoring system activation. i) Linear Pneumatic Heat detection tube with all necessary & supports ii) Master Control Unit for controlling each system, complete with pressure switches, buzzers and electronic hooters, including all necessary accessories + electrical wiring to make each entire system functional. (Panel shall conform to IEC 61439/1-2 & shall be IP-54 & of Form-4b construction). Incomer 2 Nos. MCCB, 630 Amps, 4 Pole, 35 kA , (Ics = Icu = 100%) with adjustable setting , thermal magnetic release with O/ C & S / C protection,Digital KWH Meter with voltage and current display RS485 module of class-0.5 accuracy with suitable range of cast resin CT including connections etc as required. Each Incomer shall have one set of the following items: Intelligent multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with communication facility (RS485 port), THD and Individual order harmonics upto 31st Order. LED display with required Nos CTs, 800 / 5,15 VA, class 1.0 and control circuit wiring with 2 Amp MCB for controlling. 1 Set of Indication Lamps, LED type, R,Y,B Phase indicating lamp with 2 Amp MCB for controlling. | 1.00 | Job |  | 762000.00 | 762000.00 | 450000.00 | 450000.00 | 617777.00 | 617777.00 | 649100.00 | 649100.00 | 500000.00 | 500000.00 | 450000.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
5.10 | Bus Coupler 1 Nos. MCCB, 630 Amps, 4 Pole, 35 kA , (Ics = Icu = 100%) with adjustable setting , thermal magnetic release with 1 Set of ON/ OFF Indicating LED Lamps with 2 Amp MCB. Bus Bar TPN aluminium extensible type main bus bars of minimum 630 Amps. capacity with heat shrinkable coloured sleeves having 100% neutral bus as that of phase i/c DMC / SMC bus bars supports at required intervals complete for cross section, size supports & having spacing etc. for withstanding fault level of 35 kA capacity for 1 sec. Outgoings 2 Nos. MCCB, 400 Amps, 4 Pole, 35 kA , (Ics = Icu = 100%) with adjustable setting , thermal magnetic release etc as required. 1 Nos. MCCB, 250 Amps, 4 Pole, 35 kA , (Ics = Icu = 100%) with adjustable setting , thermal magnetic release etc as required. 2 Nos. MCCB, 100 Amps, 4 Pole, 35 kA , (Ics = Icu = 100%) with adjustable setting , thermal magnetic release etc as required. 3 Nos. MCCB, 63 Amps, 4 Pole, 35 kA , (Ics = Icu = 100%) with adjustable setting , thermal magnetic release etc as required. 04 Nos, 63 Amps , 4 Pole , 10 KA , C series , MCB etc complete as required. 02 Nos, 40 Amps , 4 Pole , 10 KA , C series , MCB etc complete as required. Note : 1 No ON, OFF indication lamp (LED type) with 2 Amp SP MCB for each outgoing. Space heater with thermostat and MCB Manual interlocking between incomers
6.00 | Supply of following size of 1.1 kv grade multicore aluminium conductor, XLPE insulated and PVC sheathed armoured cable as per IS: 7098:1988 (Part-I) with upto date amendments.
6.10 | 3.5x150 sq. mm | 200.00 | Meter |  | 655.00 | 131000.00 | 650.00 | 130000.00 | 637.00 | 127400.00 | 600.00 | 120000.00 | 450.00 | 90000.00 | 90000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
6.20 | 3.5x240 sq. mm | 200.00 | Meter |  | 1055.00 | 211000.00 | 1050.00 | 210000.00 | 997.00 | 199400.00 | 1000.00 | 200000.00 | 650.00 | 130000.00 | 130000.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
7.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade Above 95 sq. mm and upto 185 sq. mm in the existing masonry open duct as required. | 100.00 | Meter |  | 120.00 | 12000.00 | 120.00 | 12000.00 | 69.00 | 6900.00 | 20.00 | 2000.00 | 100.00 | 10000.00 | 2000.00 | National Engineering
8.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade Above 185 sq. mm and upto 400 sq. mm in the existing masonry open duct as required. | 100.00 | Meter |  | 150.00 | 15000.00 | 180.00 | 18000.00 | 103.00 | 10300.00 | 30.00 | 3000.00 | 100.00 | 10000.00 | 3000.00 | National Engineering
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of above 95 sq. mm and upto 185 sq. mm in the existing RCC/ HUME/ METAL pipe as required | 50.00 | Meter |  | 120.00 | 6000.00 | 135.00 | 6750.00 | 77.00 | 3850.00 | 30.00 | 1500.00 | 100.00 | 5000.00 | 1500.00 | National Engineering
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of above 185 sq. mm and upto 400 sq. mm size in the existing RCC/ HUME/ METAL pipe as required | 50.00 | Meter |  | 150.00 | 7500.00 | 195.00 | 9750.00 | 101.00 | 5050.00 | 40.00 | 2000.00 | 100.00 | 5000.00 | 2000.00 | National Engineering
11.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade Above 95 sq. mm and upto 185 sq. mm on wall surface as required. | 50.00 | Meter |  | 120.00 | 6000.00 | 145.00 | 7250.00 | 117.00 | 5850.00 | 40.00 | 2000.00 | 100.00 | 5000.00 | 2000.00 | National Engineering
12.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade above 185 sq. mm and upto 400 sq. mm size on wall surface as required. | 50.00 | Meter |  | 150.00 | 7500.00 | 210.00 | 10500.00 | 157.00 | 7850.00 | 50.00 | 2500.00 | 100.00 | 5000.00 | 2500.00 | National Engineering
13.00 | Supply & making end termination with brass compression grands and aluminium lugs for PVC insulated & PVC sheathed aluminium conductor cable of 1.1 KV grade of the following sizes as reqd.
13.10 | 3.5x150 sq. mm | 6.00 | SET |  | 800.00 | 4800.00 | 350.00 | 2100.00 | 837.00 | 5022.00 | 900.00 | 5400.00 | 250.00 | 1500.00 | 1500.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
13.20 | 3.5x240 sq. mm. | 8.00 | SET |  | 1200.00 | 9600.00 | 450.00 | 3600.00 | 1217.00 | 9736.00 | 1200.00 | 9600.00 | 350.00 | 2800.00 | 2800.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
14.00 | Supply & laying , testing and commissioning of M.S. heavy class pipe confirming to IS : 1239 of following sizes etc. in welded construction with fittings such as bends, tees, reducer etc. on surface / reccess and excavation and refilling the trench etc. as required.as required.
14.10 | 25 mm dia | 15.00 | Meter |  | 350.00 | 5250.00 | 320.00 | 4800.00 | 367.00 | 5505.00 | 300.00 | 4500.00 | 350.00 | 5250.00 | 4500.00 | National Engineering
14.20 | 50 mm dia | 40.00 | Meter |  | 600.00 | 24000.00 | 430.00 | 17200.00 | 617.00 | 24680.00 | 400.00 | 16000.00 | 450.00 | 18000.00 | 16000.00 | National Engineering
15.00 | Providing and fixing of Nitrile rubber Insulation on following size MS pipe line on surface / reccess including anticorrosive black paint with 25 mm insulation & GI netting cloth etc. as required.
15.10 | 25 mm dia | 15.00 | Meter |  | 350.00 | 5250.00 | 450.00 | 6750.00 | 171.00 | 2565.00 | 250.00 | 3750.00 | 300.00 | 4500.00 | 2565.00 | Mona Generator Services Pvt. Ltd.
15.20 | 50 mm dia | 40.00 | Meter |  | 600.00 | 24000.00 | 550.00 | 22000.00 | 287.00 | 11480.00 | 400.00 | 16000.00 | 400.00 | 16000.00 | 11480.00 | Mona Generator Services Pvt. Ltd.
16.00 | Supply, fixing and testing of following valves of pressure rating 1.6 MPa as per IS 778, class-2 in the H.S.D. Fuel Handling System piping complete with companion flanges, nut bolts, gaskets, supports and painted etc. as per specifications :
16.10 | 25 mm dia Ball Valve | 4.00 | JOB |  | 125.00 | 500.00 | 550.00 | 2200.00 | 637.00 | 2548.00 | 750.00 | 3000.00 | 110.00 | 440.00 | 440.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
16.20 | 50 mm dia Ball Valve | 4.00 | JOB |  | 350.00 | 1400.00 | 750.00 | 3000.00 | 1327.00 | 5308.00 | 1000.00 | 4000.00 | 150.00 | 600.00 | 600.00 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION
17.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 2.00 | Nos. |  | 18000.00 | 36000.00 | 19500.00 | 39000.00 | 16177.00 | 32354.00 | 15000.00 | 30000.00 | 24500.00 | 49000.00 | 30000.00 | National Engineering
18.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 2.00 | Nos. |  | 6000.00 | 12000.00 | 9600.00 | 19200.00 | 9700.00 | 19400.00 | 5000.00 | 10000.00 | 9500.00 | 19000.00 | 10000.00 | National Engineering
19.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 4.00 | Nos. |  | 3000.00 | 12000.00 | 7500.00 | 30000.00 | 10100.00 | 40400.00 | 6000.00 | 24000.00 | 5600.00 | 22400.00 | 12000.00 | ECS ENGINEERING PVT LTD
20.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground/laying in existing GI/RCC/HUME pipe as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | 20.00 | Mtr |  | 1450.00 | 29000.00 | 750.00 | 15000.00 | 1197.00 | 23940.00 | 1100.00 | 22000.00 | 1200.00 | 24000.00 | 15000.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
21.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground/laying in existing GI/RCC/HUME pipe as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 20.00 | Mtr |  | 225.00 | 4500.00 | 180.00 | 3600.00 | 197.00 | 3940.00 | 140.00 | 2800.00 | 250.00 | 5000.00 | 2800.00 | National Engineering
22.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 40.00 | Mtr |  | 1350.00 | 54000.00 | 690.00 | 27600.00 | 1157.00 | 46280.00 | 1100.00 | 44000.00 | 950.00 | 38000.00 | 27600.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
23.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 50.00 | Mtr |  | 140.00 | 7000.00 | 135.00 | 6750.00 | 327.00 | 16350.00 | 140.00 | 7000.00 | 250.00 | 12500.00 | 6750.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
24.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 25.00 | Mtr |  | 1850.00 | 46250.00 | 1150.00 | 28750.00 | 1670.00 | 41750.00 | 1350.00 | 33750.00 | 1500.00 | 37500.00 | 28750.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
25.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 30.00 | Mtr |  | 640.00 | 19200.00 | 450.00 | 13500.00 | 587.00 | 17610.00 | 500.00 | 15000.00 | 1500.00 | 45000.00 | 13500.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
26.00 | Providing and fixing testing joint, made of 25 mm X 5 mm thick copper strip, 125 mm long, with 4 nos. of tinned brass bolts, nuts, check nuts and spring washers etc. complete as required. | 2.00 | Job |  | 400.00 | 800.00 | 650.00 | 1300.00 | 1347.00 | 2694.00 | 350.00 | 700.00 | 1500.00 | 3000.00 | 700.00 | National Engineering
27.00 | Providing and fixing testing joint, made of 25 mm X 5 mm thick G.I. strip, 125 mm long, with 4 nos. of tinned G.I. bolts, nuts, check nuts and spring washers etc. complete as required. | 4.00 | Job |  | 200.00 | 800.00 | 220.00 | 880.00 | 277.00 | 1108.00 | 180.00 | 720.00 | 950.00 | 3800.00 | 720.00 | National Engineering
28.00 | Providing, laying and fixing 100mm dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (70 cm deep) and re-filling etc as required | 100.00 | Mtr |  | 1550.00 | 155000.00 | 1200.00 | 120000.00 | 1177.00 | 117700.00 | 800.00 | 80000.00 | 950.00 | 95000.00 | 80000.00 | National Engineering
29.00 | Supply and fixing of high voltage synthetic insulating mat made of synthetic Elastomer suitable for upto 3.3 KV conforming to IS 15652:2006 with minimum width of 1 metre and thickness of 2.0 mm +/- 10 % (Class-A). Insulating mat should be flexible , anti skid, fire reatrdant, water and moisture proof with no adverse effect of acids,alkalies and transformer oil. Insulating mat should be fixed with suitable adhesive/chemibond , resin,water proofing compound and other sealing materials as per specifications. Insulating mats should be ISI marked alongwith CM/L nos at every meter. | 25.00 | Sq. Mtr |  | 750.00 | 18750.00 | 700.00 | 17500.00 | 1327.00 | 33175.00 | 1200.00 | 30000.00 | 2800.00 | 70000.00 | 17500.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
30.00 | Dismantling of existing complete 250 KVA DG set system including engine, alternator, connected exhaust pipe, acoustic enclosure, cable connections, terminations and all associated accessories from existing installed location to another location within the premises of Airport as directed by Engineer- in- charge etc complete as required. | 2.00 | JOB |  | 15000.00 | 30000.00 | 15000.00 | 30000.00 | 23777.00 | 47554.00 | 5000.00 | 10000.00 | 50000.00 | 100000.00 | 10000.00 | National Engineering
31.00 | Dismantling of existing LT Ess/Non-Ess/AMF panel including bus bar, cable connections, terminations and all associated accessories from existing installed location to another location within the premises of Airport as directed by Engineer- in- charge etc complete as required. | 3.00 | JOB |  | 7500.00 | 22500.00 | 15000.00 | 45000.00 | 14000.00 | 42000.00 | 2500.00 | 7500.00 | 20000.00 | 60000.00 | 7500.00 | National Engineering
| Total in Figures |  |  |  |  | 6606100.00 |  | 4737480.00 |  | 5390366.00 |  | 5853920.00 |  | 6418290.00
Lowest Amount Quoted BY: ARNAV ENGINEERING CONSULTANCY SERVICES(4737480.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of 02 Nos of 250 KVA DG Sets at Kargil Airport Tender ID: 2021_AAI_75523_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | ARNAV ENGINEERING CONSULTANCY SERVICES | 4737480.00 | L1
| 2 | Mona Generator Services Pvt. Ltd. | 5390366.00 | L2
| 3 | National Engineering | 5853920.00 | L3
| 4 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION | 6418290.00 | L4
| 5 | ECS ENGINEERING PVT LTD | 6606100.00 | L5