## BoQ1
Government eProcurement System Created By: MANTRIMAYUM CHINGLENSANA SINGH Created Date/Time: 28-May-2021 04:32 PM Tender Title: Replacement of LT Panels in Operational Area at Imphal Airport Tender ID: 2021_AAI_77150_1
Tender Inviting Authority: Asstt. General Manager (Engg-E)-I, AAI, Imphal Airport.
Name of Work: Replacement of L.T. Panels in Operational Area at Imphal Airport
Contract No: 2021_AAI_77150_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ECS ENGINEERING PVT LTD(GSTN-09AABCE5944P1Z1) |  | jaydeep agency corporation(GSTN-24ACIPP6157B1ZQ) |  | Yash Energy Pvt. Ltd(GSTN-24AAACY3771H1ZA) |  | ROHILKHAND ELECTRICALS AND FABRICATORS(GSTN-09ADIPB0122B1ZH) |  | Rekha Enterprises(GSTN-27ADZPB3409Q1ZV) |  | SHAKTI TECHNO FAB PRODUCTS(GSTN-09AAGPB2824D1Z8) |  | ARNAV ENGINEERING CONSULTANCY SERVICES(GSTN-07ABKFA7102Q1Z4) |  | Incotech Engineers Pvt Ltd(GSTN-19AAACI5242B1ZZ) |  | SHRI KARNI LIGHT HOUSE(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of MV Switch Board Outdoor Double Door Type Feeder Pillar made out of 3mm Thick CRCA Sheet Steel for Outer Shell and 2mm Thick CRCA Sheet for Inner Partition, dust tight, vermin proof, Totally enclosed, cubicle type, floor mounting, free standing, provided with rain guard on top, suitable for operation at 415 V, 3 Phase, 4 Wire, 50 Hz, AC System complete with all accessories, interconnection, connection, earthing, painting, provided with bottom base channel and locking arrangements including providing RCC Pedestal, grouting the Panel etc., as required and comprising of the following: (A) One No. of 250 A, 50 KA, 4P MCCBs with Microprocessor Based Releases for OC/SC/EF Protection as Incomer, C.T. operated Digital Meter [EM 6400 of Conzerve/Equivalent], ON/OFF/TRIP Indication and Phase Indication Lamps, as required. (B) One No. of 200 A, 50 KA, 4P MCCB Microprocessor Based Releases for OC/SC/EF Protection, C.T. operated Digital Meter [EM 6400 of Conzerve/Equivalent], ON/OFF/TRIP Indication and Phase Indication Lamps, as required. (C) Two Nos. of 63 A, 36 KA, 4P MCCB with Thermal Magnetic Releases for Protection as Outgoing with Individual Timer and 100A 4P Contactors for Street Lighting, ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required. (D) One No. of 63 A, 36 KA, 4P MCCB with Thermal Magnetic Releases for Protection as Outgoing with ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required. (E) One Set of 400 Amps Al. Bus Bars with at Par Neutral BUS BAR as required. (F) All accessories such as fuses, auxillary contactors, auxillary switches, etc., as required. ALL AS ABOVE 1 (A) To 1 (F) | 3.00 | Jobs | 100.00 | 256175.00 | 768525.00 | 350000.00 | 1050000.00 | 247950.00 | 743850.00 | 269320.00 | 807960.00 | 230000.00 | 690000.00 | 310000.00 | 930000.00 | 370850.00 | 1112550.00 | 237463.00 | 712389.00 | 314700.00 | 944100.00 | 690000.00 | Rekha Enterprises
2.00 | SITC of MV Switch Board Outdoor Double Door Type Feeder Pillar made out of 3mm Thick CRCA Sheet Steel for Outer Shell and 2mm Thick CRCA Sheet for Inner Partition, dust tight, vermin proof, Totally enclosed, cubicle type, floor mounting, free standing, provided with rain guard on top, suitable for operation at 415 V, 3 Phase, 4 Wire, 50 Hz, AC System complete with all accessories, interconnection, connection, earthing, painting, provided with bottom base channel and locking arrangements including providing RCC Pedestal, grouting the Panel etc., as required and comprising of the following: (A) One No. of 200 A, 50 KA, 4P MCCBs with Microprocessor Based Releases for OC/SC/EF Protection as Incomer, C.T. operated Digital Meter [EM 6400 of Conzerve/Equivalent], ON/OFF/TRIP Indication and Phase Indication Lamps, as required. (B) Two Nos. of 63 A, 36 KA, 4P MCCB with Thermal Magnetic Releases for Protection as Outgoing with Individual Timer and 100A 4P Contactors for Street Lighting, ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required. (C) One No. of 63 A, 36 KA, 4P MCCB with Thermal Magnetic Releases for Protection as Outgoing with ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required. (D) One Set of 400 Amps Al. Bus Bars with at Par Neutral BUS BAR as required. (E) All accessories such as fuses, auxillary contactors, auxillary switches, etc., as required. ALL AS ABOVE 2 (A) To 2 (E) | 2.00 | Jobs | 100.00 | 204000.00 | 408000.00 | 300000.00 | 600000.00 | 176065.00 | 352130.00 | 192800.00 | 385600.00 | 195000.00 | 390000.00 | 262000.00 | 524000.00 | 365700.00 | 731400.00 | 162323.00 | 324646.00 | 295950.00 | 591900.00 | 324646.00 | Incotech Engineers Pvt Ltd
3.00 | Fabrication, SITC of MV Switch Board Non-Essential/Eseential Panel made of 14 SWG CRCA Sheet Steel, dust tight, vermin proof, Totally enclosed, cubicle type, floor mounting, free standing, extensible on both sides, suitable for indoor operation at 433 V, 3 Phase, 4 Wire, 50 Hz, A.C.System complete with all accessories, interconnection, connection, earthing, painting, etc., as required and comprising of the following: (A) Two Nos. of 250 A, 50 KA, 4P MCCBs with Microprocessor Based Releases for OC/SC/EF Protection as INCOMERS with ON/OFF/TRIP Indication Lamps and Phase Indication Lamps, Interlocking Facility with Incomers and Buscouplers as required. (B) One No. 250 A, 50 KA, 4P MCCBs as Bus Coupler with ON/OFF Indication Lamps as required. (C) Two No. of 125 A, 50 KA, 4P MCCB with Microprocessor Based Releases for OC/SC/EF Protection as Outgoing, C.T. operated Digital VAF Meter, ON/OFF/TRIP Indication Lamps and Phase Indication Lamps as required. (D) Four Nos. of 63 A, 35 KA, 4P MCCB with Thermal Magnetic Releases for Protection as Outgoing, ON/OFF/TRIP Indication Lamps as required. (E) One Set of 400 Amps Al. Bus Bars with at Par Neutral BUS BARS as required. (F) All accessories such as fuses, auxillary contactors, auxillary switches, etc. including providing Empty Cubicle Space (2 Nos.) as required. ALL AS ABOVE 3 (A) To 3 (F) | 2.00 | Jobs | 100.00 | 338000.00 | 676000.00 | 324000.00 | 648000.00 | 341230.00 | 682460.00 | 425500.00 | 851000.00 | 350000.00 | 700000.00 | 385000.00 | 770000.00 | 375700.00 | 751400.00 | 410915.00 | 821830.00 | 301800.00 | 603600.00 | 603600.00 | SHRI KARNI LIGHT HOUSE
4.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
4.10 | 3.5 X 240 Sq. mm (62mm) | 1.00 | Sets | 100.00 | 1500.00 | 1500.00 | 1400.00 | 1400.00 | 2282.00 | 2282.00 | 380.00 | 380.00 | 1834.65 | 1834.65 | 800.00 | 800.00 | 550.00 | 550.00 | 1700.00 | 1700.00 | 750.00 | 750.00 | 380.00 | ROHILKHAND ELECTRICALS AND FABRICATORS
4.20 | 3.5 X 185 Sq.mm (57mm) | 6.00 | Sets | 100.00 | 1200.00 | 7200.00 | 1150.00 | 6900.00 | 1844.00 | 11064.00 | 275.00 | 1650.00 | 1572.50 | 9435.00 | 700.00 | 4200.00 | 430.00 | 2580.00 | 1445.00 | 8670.00 | 650.00 | 3900.00 | 1650.00 | ROHILKHAND ELECTRICALS AND FABRICATORS
4.30 | 3.5 X 95 Sq.mm (45mm) | 6.00 | Sets | 100.00 | 700.00 | 4200.00 | 500.00 | 3000.00 | 758.00 | 4548.00 | 220.00 | 1320.00 | 1062.50 | 6375.00 | 600.00 | 3600.00 | 355.00 | 2130.00 | 820.00 | 4920.00 | 550.00 | 3300.00 | 1320.00 | ROHILKHAND ELECTRICALS AND FABRICATORS
4.40 | 4 X 25 Sq.mm (28) | 10.00 | Sets | 100.00 | 450.00 | 4500.00 | 200.00 | 2000.00 | 510.00 | 5100.00 | 185.00 | 1850.00 | 552.50 | 5525.00 | 400.00 | 4000.00 | 255.00 | 2550.00 | 605.00 | 6050.00 | 250.00 | 2500.00 | 1850.00 | ROHILKHAND ELECTRICALS AND FABRICATORS
5.00 | Supply of 30V, 20A, DC Battery charger with thyrister technology rectifier suitable to operate on 230V, 50Hz, single phase AC Power supply with charging arrangement for Trickle / Booster including with suitable range digital meter for both AC/DC for measuring current and voltage regulator, selector switch indication lamp etc., as required. | 2.00 | Each | 100.00 | 20000.00 | 40000.00 | 100000.00 | 200000.00 | 86950.00 | 173900.00 | 75000.00 | 150000.00 | 200000.00 | 400000.00 | 70000.00 | 140000.00 | 4500.00 | 9000.00 | 170400.00 | 340800.00 | 65000.00 | 130000.00 | 9000.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
6.00 | Dismantling of LT Panels which is associated with existing perimeter lighting system from existing site and shift to AAI Premises job include removing all termination, etc., and shift as per instruction of Engineering In-Charge etc. as required. | 6.00 | Each | 100.00 | 10000.00 | 60000.00 | 5000.00 | 30000.00 | 4825.00 | 28950.00 | 7500.00 | 45000.00 | 10500.00 | 63000.00 | 5000.00 | 30000.00 | 5500.00 | 33000.00 | 6250.00 | 37500.00 | 6500.00 | 39000.00 | 28950.00 | Yash Energy Pvt. Ltd
7.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 3.00 | Each | 100.00 | 10000.00 | 30000.00 | 4000.00 | 12000.00 | 8015.00 | 24045.00 | 7800.00 | 23400.00 | 3400.00 | 10200.00 | 11000.00 | 33000.00 | 6500.00 | 19500.00 | 12200.00 | 36600.00 | 3500.00 | 10500.00 | 10200.00 | Rekha Enterprises
8.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 100.00 | Mtr | 100.00 | 285.00 | 28500.00 | 200.00 | 20000.00 | 240.00 | 24000.00 | 140.00 | 14000.00 | 978.00 | 97800.00 | 400.00 | 40000.00 | 195.00 | 19500.00 | 271.00 | 27100.00 | 120.00 | 12000.00 | 12000.00 | SHRI KARNI LIGHT HOUSE
9.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 50.00 | Mtr | 100.00 | 200.00 | 10000.00 | 200.00 | 10000.00 | 140.00 | 7000.00 | 25.00 | 1250.00 | 180.00 | 9000.00 | 300.00 | 15000.00 | 155.00 | 7750.00 | 222.00 | 11100.00 | 100.00 | 5000.00 | 1250.00 | ROHILKHAND ELECTRICALS AND FABRICATORS
| Total in Figures |  |  |  |  | 2038425.00 |  | 2583300.00 |  | 2059329.00 |  | 2283410.00 |  | 2383169.65 |  | 2494600.00 |  | 2691910.00 |  | 2333305.00 |  | 2346550.00
Lowest Amount Quoted BY: ECS ENGINEERING PVT LTD(2038425.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of LT Panels in Operational Area at Imphal Airport Tender ID: 2021_AAI_77150_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | ECS ENGINEERING PVT LTD | 2038425.00 | L1
| 2 | Yash Energy Pvt. Ltd | 2059329.00 | L2
| 3 | ROHILKHAND ELECTRICALS AND FABRICATORS | 2283410.00 | L3
| 4 | Incotech Engineers Pvt Ltd | 2333305.00 | L4
| 5 | SHRI KARNI LIGHT HOUSE | 2346550.00 | L5
| 6 | Rekha Enterprises | 2383169.65 | L6
| 7 | SHAKTI TECHNO FAB PRODUCTS | 2494600.00 | L7
| 8 | jaydeep agency corporation | 2583300.00 | L8
| 9 | ARNAV ENGINEERING CONSULTANCY SERVICES | 2691910.00 | L9