## BoQ1
Government eProcurement System Created By: MD Sadrul Huda Created Date/Time: 16-Jun-2021 01:15 PM Tender Title: Provision of Inset type fitting for intersection of Runway and Taxiway at C A Bhavnagar Tender ID: 2021_AAI_77699_1
Tender Inviting Authority: Sr. Manager (E-E)
Name of Work: Provision of Inset type fitting for intersection of Runway / Taxiway at C.A. Bhavnagar.
Contract No: 2021_AAI_77699_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Taral Electricals(GSTN-24ACMPR0280M1Z9) |  | Manish Electricals(GSTN-22ABLPM9012E1ZY) |  | Techno Electricals(GSTN-24AAGFT9086M1ZG)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of Bi-directional Inset Type High Intensity Runway Edge Light Fitting suitable for use with 2 x 105 W, 6.6 Amp Halogen Lamp, complete with all accessories etc. confirming to particulars specifications etc. and complete as required | 3.00 | Each |  | 76992.00 | 230976.00 | 62000.00 | 186000.00 | 70000.00 | 210000.00 | 186000.00 | Manish Electricals
2.00 | Supply of 2 x 4 Sq.mm copper flexible secondary lead of following length made out of multistranded, annealed, PVC sheathed, unshielded, EPR insulated, antitermite & antirodent cable of 5 kv grade with moulded plug and receptacle as required as per particular specifications. a) 35 Mtr | 2.00 | Each |  | 6966.00 | 13932.00 | 6650.00 | 13300.00 | 6500.00 | 13000.00 | 13000.00 | Techno Electricals
3.00 | Cutting of cable groove with kerf cutting machine for laying following number of 2 x 4 Sqmm secondary leads meant for inset type runway fitting on the concrete/ bituminous runway surface including kerfing, chiseling, cleaning and filling the groove with sealant compound after putting sealant primer after laying secondary lead including jute covering for protection etc. as required. a) 01 Run of Cable (For laying 35 Mtr Secondary Lead) | 40.00 | Mtr |  | 1100.00 | 44000.00 | 600.00 | 24000.00 | 500.00 | 20000.00 | 20000.00 | Techno Electricals
4.00 | Excavation for cable trenches in soft soil, depth upto 1.2 m including dressing of sides lift upto 1.5 m, including getting out the excavated soil, refilling with sand and or good soil after laying of cable / pipe etc in layers of 20 cm, ramming, watering and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 80.00 | Mtr |  | 244.00 | 19520.00 | 120.00 | 9600.00 | 135.00 | 10800.00 | 9600.00 | Manish Electricals
5.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 metres in width, and lift upto 1.5 metres, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres. | 10.00 | Mtr |  | 269.00 | 2690.00 | 850.00 | 8500.00 | 700.00 | 7000.00 | 2690.00 | Taral Electricals
6.00 | Supply and fixing of 5 KV grade plug and receptacle of type -I class "B" connector and making field connections by crimping the plug and receptacle with the existing PVC insulated and PVC sheathed copper conductor cable including filling the gap with water sealant material, applying PVC HT insulation tape etc complete as required for the following size of cable. a) Single Core 16 Sq.mm | 2.00 | Set |  | 519.00 | 1038.00 | 400.00 | 800.00 | 450.00 | 900.00 | 800.00 | Manish Electricals
7.00 | Installation, testing and commissioning of Bi-directional Inset Type High Intensity Runway Edge Light Fitting by making suitable hole with help of core cutting machine in the bitumen/pavement area of runway and fixing the fitting using quick setting sealant compound such as plasticised sulphur cement/dobefill resin compound including connection with secondary cable, positioning of isolation transformer in housing box, making good the runway to the original finish etc. as required. | 2.00 | Nos |  | 6049.00 | 12098.00 | 9000.00 | 18000.00 | 6500.00 | 13000.00 | 12098.00 | Taral Electricals
8.00 | Laying of 1 No. PVC insulated and PVC sheathed copper conductor cable of grade 5 KV and size 25 Sq.mm / 16 Sq.mm / 6 Sq.mm / Secondary lead in the existing RCC / Hume / Stoneware / GI pipe / HDPE / DWC Pipe etc. complete as required. (Cable Supplied by AAI) | 70.00 | Mtr |  | 31.00 | 2170.00 | 15.00 | 1050.00 | 25.00 | 1750.00 | 1050.00 | Manish Electricals
9.00 | Laying of 1 No PVC insulated and PVC sheathed copper conductor cable of grade 5 KV and size 25 Sq.mm/16 Sq.mm/ 6 Sq.mm direct in ground including excavation, sand cushioning, protective covering and refelling the trench etc. as required. | 230.00 | Mtr |  | 257.00 | 59110.00 | 350.00 | 80500.00 | 250.00 | 57500.00 | 57500.00 | Techno Electricals
10.00 | Earthing with GI earth pipe 4.5 mtr long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe with charcoal or coke and salt as required. | 2.00 | Nos |  | 6722.00 | 13444.00 | 7000.00 | 14000.00 | 5000.00 | 10000.00 | 10000.00 | Techno Electricals
11.00 | Supply, Installation, Testing & Commissioning of Remote Control Panel Cum Display unit at Control tower fabricated from CRCA sheet of 2 mm thick with suitable height suitable for remote operation of CCR and comprise the following interconnection etc. with terminal block etc. as required as per specification etc. as required by Engineer-In-Charge. 1) Runway Circuit A & B 2) Taxiway Circuit A & B (Proposed Taxiway Fitting on Runway) 3) PAPI Circuit - 02 Nos 4) Simple Approach Light - 02 Nos 5) High Mast - 02 Nos (For Apron) 6) Wind Sock - 01 No 7) H-Indicator - 01 No 8) End Light Circuit A & B 9) Inset End Light Circuit A & B 10) Isolation Bay Circuit (Taxiway + High Mast) 11) Operational Signage's Board 12) Spares | 1.00 | Each |  | 149096.00 | 149096.00 | 225000.00 | 225000.00 | 160000.00 | 160000.00 | 149096.00 | Taral Electricals
12.00 | Supply of control cable of size 2.5 Sq.mm 61 cores, 1.1KV annealed electrolytic copper conductor, armoured, PVC insulated, PVC sheathed as per IS : 1554-I & IS : 7098-I upto date. | 125.00 | Mtr |  | 2383.00 | 297875.00 | 1830.00 | 228750.00 | 2181.00 | 272625.00 | 228750.00 | Manish Electricals
13.00 | Supply of control cable of size 1.5 Sq.mm 8 cores, 1.1KV annealed electrolytic copper conductor, armoured, PVC insulated, PVC sheathed as per IS : 1554-I & IS : 7098-I upto date. | 100.00 | Mtr |  | 244.00 | 24400.00 | 310.00 | 31000.00 | 210.00 | 21000.00 | 21000.00 | Techno Electricals
14.00 | Laying of 01 No. Control Cable of size 2.5 sq. mm., 61 cores, 1.1KV grade in the existing RCC/ HUME/ METAL pipe as required. | 100.00 | Mtr |  | 49.00 | 4900.00 | 60.00 | 6000.00 | 30.00 | 3000.00 | 3000.00 | Techno Electricals
15.00 | Laying of 01 No. Control Cable of size 2.5 sq. mm., 61 cores, 1.1KV grade in the existing masonry open duct as required. | 25.00 | Mtr |  | 49.00 | 1225.00 | 90.00 | 2250.00 | 30.00 | 750.00 | 750.00 | Techno Electricals
16.00 | Laying of 01 No. Control Cable of size 1.5 sq. mm., 8 cores, 1.1KV grade in the existing masonry open duct as required. | 100.00 | Mtr |  | 49.00 | 4900.00 | 20.00 | 2000.00 | 300.00 | 30000.00 | 2000.00 | Manish Electricals
17.00 | Supply installation tesing and comissioning of Termination box made of MS Sheet suitable for 61 core 2.5 sqmm 1.1 KV grade copper conductor with suitable size connector strip complete connection as required. | 2.00 | Nos |  | 9166.00 | 18332.00 | 15000.00 | 30000.00 | 10000.00 | 20000.00 | 18332.00 | Taral Electricals
18.00 | SITC of C.I. Transformer housing box water tight round type metal container of out side dia of 330 mm, height 450 mm made of 10 mm thick cast iron moulding all round except on top surface which is 15 mm thick etc. complete as required. | 2.00 | Nos |  | 6722.00 | 13444.00 | 4800.00 | 9600.00 | 7200.00 | 14400.00 | 9600.00 | Manish Electricals
19.00 | Supply and fixing of 6 mm thick M.S. powder coated cover plate to cover the CI transformer bousing box of 330 mm out side dia having suitable holes to fasten the cover with nut bolts arrangement etc. as required. | 2.00 | Nos |  | 2139.00 | 4278.00 | 1150.00 | 2300.00 | 450.00 | 900.00 | 900.00 | Techno Electricals
20.00 | Supply of 4 x 25 Sq.mm sizes of 1.1 KV grade multicore aluminium conductor PVC insulated / XLPE insulated and PVC sheathed armoured cable as per IS-1554 (Part-I) 1988/IS-7098 (Part-I) 1985 respectively with upto date ammendments. | 150.00 | Mtr |  | 232.00 | 34800.00 | 180.00 | 27000.00 | 175.00 | 26250.00 | 26250.00 | Techno Electricals
21.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.(Upto 35 Sq.mm) | 150.00 | Mtr |  | 257.00 | 38550.00 | 350.00 | 52500.00 | 250.00 | 37500.00 | 37500.00 | Techno Electricals
22.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ GI / HDPE / DWC pipe as required.(Upto 35 Sq.mm) | 30.00 | Mtr |  | 49.00 | 1470.00 | 30.00 | 900.00 | 25.00 | 750.00 | 750.00 | Techno Electricals
23.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 4 x 25 Sq.mm (28mm) size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 8.00 | Set |  | 281.00 | 2248.00 | 220.00 | 1760.00 | 200.00 | 1600.00 | 1600.00 | Techno Electricals
24.00 | Supplying and making straight through joint with cast resin compound including ferrules and other jointing materials for 4 x 25 Sq.mm size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 1.00 | Nos |  | 2200.00 | 2200.00 | 2000.00 | 2000.00 | 2000.00 | 2000.00 | 2000.00 | Manish Electricals, Techno Electricals
25.00 | Supply of 7 mtrs. height GI OCTAGONAL continuously tapered galvanised street light pole with minimum 1000 mm long Three arm GI bracket (length and tilt angle of bracket shall be based on design) for installation of LED street light luminaire, suitable for wind velocity as per IS 875 (but not less than 50 m/sec.), fabricated out of 3 mm thick high tensile sheet steel in single piece construction having 130mm bottom, 70 mm top, suitable for installation on a precast foundation with supply of 4 nos. of foundation bolts & anchor plate, rigid flange plate (200 x 200 x 12mm min.) welded with the base of pole for fixing on foundation bolts complete as required for structural stability as specified, weather proof and vandal resistant door flush with the exterior surface containing a terminal plate of 5 mm thick bakelite sheet with 32 Amp heavy duty connector for loop in loop out cable terminations suitable for upto Three numbers 31/2 x 25 Sq.mm cables, including supply of 2A, 10kA, DP, C series, MCB for each fixture connections, earthing bolts for continuous earth connection complete, as required as per technical specifications. | 2.00 | Nos |  | 16254.00 | 32508.00 | 14500.00 | 29000.00 | 18000.00 | 36000.00 | 29000.00 | Manish Electricals
26.00 | Supply of 7 mtrs. height GI OCTAGONAL continuously tapered galvanised street light pole with minimum 1000 mm long four arm GI bracket (length and tilt angle of bracket shall be based on design) for installation of LED street light luminaire, suitable for wind velocity as per IS 875 (but not less than 50 m/sec.), fabricated out of 3 mm thick high tensile sheet steel in single piece construction having 130mm bottom, 70 mm top, suitable for installation on a precast foundation with supply of 4 nos. of foundation bolts & anchor plate, rigid flange plate (200 x 200 x 12mm min.) welded with the base of pole for fixing on foundation bolts complete as required for structural stability as specified, weather proof and vandal resistant door flush with the exterior surface containing a terminal plate of 5 mm thick bakelite sheet with 32 Amp heavy duty connector for loop in loop out cable terminations suitable for upto Three numbers 31/2 x 25 Sq.mm cables, including supply of 2A, 10kA, DP, C series, MCB for each fixture connections, earthing bolts for continuous earth connection complete, as required as per technical specifications. | 2.00 | Nos |  | 16804.00 | 33608.00 | 12400.00 | 24800.00 | 19000.00 | 38000.00 | 24800.00 | Manish Electricals
27.00 | Erection of 7 Mtr.high G.I. OCTAGONAL street light pole & bracket with all accessories by providing and making reinforced M 20 cement concrete foundation including excavation and refilling including positioning of template & foundation bolts (supplied with pole to match with pole base plate) & providing and fixing of DWC HDPE pipe of size 40 mm dia (2 pieces of min. 0.75 m length) in the foundation for loop-in-loop-out of the cable to the pole complete as required and as specified. | 4.00 | Job |  | 6355.00 | 25420.00 | 2500.00 | 10000.00 | 3000.00 | 12000.00 | 10000.00 | Manish Electricals
28.00 | Supply of Electromechanical Time Switches. (Make : Hager, Model No. EH711 or equivalent) | 5.00 | Nos |  | 3055.00 | 15275.00 | 3500.00 | 17500.00 | 5000.00 | 25000.00 | 15275.00 | Taral Electricals
29.00 | Supply of 70 Watt LED type Road/ Street light with minimum protection level IP 66, pressure die cast housing with epoxy powder coated prismatic poly carbonate cover with individual LED lenses and complete assembly with LED, driver and accessories pre-wired up to terminal block i/c suitable mounting accessories etc. as required. [ Make : Wipro, Model No. LR02-781-XXX-57-G2 or equivalent as approved by EIC ] | 15.00 | Nos |  | 3177.00 | 47655.00 | 4200.00 | 63000.00 | 3500.00 | 52500.00 | 47655.00 | Taral Electricals
30.00 | Installation, Testing and Commissioning of LED street light fitting with all accessories on existing 7 Mtr high G.I. OCTAGONAL street light pole including supplying and drawing of 3C x 2.5 Sq.mm. FRLSH PVC insulated PVC sheathed flexible copper conductor cable from loop-in-loop-out box upto the individual streetlight fittings, connection etc. complete as required & as specified. | 14.00 | Nos |  | 794.00 | 11116.00 | 250.00 | 3500.00 | 450.00 | 6300.00 | 3500.00 | Manish Electricals
31.00 | Supply of 1.0 Sq.mm size of copper conductor PVC insulated flexible, heat resistant flame retardent grade wires suitable for domestic and industrial purpose. Conferming to IS:694. | 450.00 | Mtr |  | 15.00 | 6750.00 | 15.00 | 6750.00 | 15.00 | 6750.00 | 6750.00 | Taral Electricals, Manish Electricals, Techno Electricals
32.00 | Supply of 1.5 Sq.mm size of copper conductor PVC insulated flexible, heat resistant flame retardent grade wires suitable for domestic and industrial purpose. Conferming to IS:694. | 270.00 | Mtr |  | 22.00 | 5940.00 | 21.00 | 5670.00 | 18.00 | 4860.00 | 4860.00 | Techno Electricals
33.00 | Supply of 2.5 Sq.mm size of copper conductor PVC insulated flexible, heat resistant flame retardent grade wires suitable for domestic and industrial purpose. Conferming to IS:694. | 270.00 | Mtr |  | 35.00 | 9450.00 | 28.00 | 7560.00 | 25.00 | 6750.00 | 6750.00 | Techno Electricals
| Total in Figures |  |  |  |  | 1184418.00 |  | 1144590.00 |  | 1122885.00
Lowest Amount Quoted BY: Techno Electricals(1122885.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Inset type fitting for intersection of Runway and Taxiway at C A Bhavnagar Tender ID: 2021_AAI_77699_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Techno Electricals | 1122885.00 | L1
| 2 | Manish Electricals | 1144590.00 | L2
| 3 | Taral Electricals | 1184418.00 | L3