## BoQ1
Government eProcurement System Created By: SHALENDERA KUMAR Created Date/Time: 01-Jul-2021 05:21 PM Tender Title: Replacement of Old Light Fittings at Perimeter Road Near NH-150 with Hybrid Solar LED Light at Imphal Airport Tender ID: 2021_AAI_78395_1
Tender Inviting Authority: Asstt. General Manager (Engg-Electrical)-II, AAI, Imphal Airport.
Name of Work: Replacement of Old Light Fittings at Perimeter Road Near NH-150 with Hybrid Solar LED Light at Imphal Airport.
Contract No: 2021_AAI_78395_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | jaydeep agency corporation(GSTN-24ACIPP6157B1ZQ) |  | RVD INFRA SOLUTION PVT.LTD.(GSTN-24AAGCR7767L1ZQ) |  | Robust Electric(GSTN-07AUQPM6882L3ZL) |  | SHARMA TRADE AGENCY(GSTN-18ABDFM0295M2ZV) |  | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED(GSTN-07ABDCS2796Q1ZH) |  | Thokchom Okendro Singh(GSTN-14CFSPS8987M1Z1)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of ALL IN ONE Integrated Hybrid Solar Street Light Fixture of not less than 3000 Lumens with Lumen Efficacy of Minimum 150 Lumens/Watt to achieve 3-5 Lux at a Point with Solar Module of 12 V of Capacity not less than 35 Wp made of Monocrystalline Cells, Maintenance Free Lithium Ferro Phosphate (LiFePO4) Battery of Autonomy of Minimum 12 Hrs and Capacity not less than 250 WHr, Housing made of High grade aluminum die-cast/extruded aluminium with good heat dissipation facility, suitable for climatic condition of -10 to +50 Deg C, Humidity of 95% and meeting IP 65 and IK08 requirements etc., complete but without PIR Sensor as required. | 36.00 | Each | 100.00 | 28000.00 | 1008000.00 | 20400.00 | 734400.00 | 29600.00 | 1065600.00 | 21000.00 | 756000.00 | 25400.00 | 914400.00 | 25970.05 | 934921.80 | 734400.00 | RVD INFRA SOLUTION PVT.LTD.
2.00 | Supply of ALL IN ONE Integrated Hybrid Solar Street Light Fixture of not less than 4500 Lumens with Lumen Efficacy of Minimum 150 Lumens/Watt to achieve 3-5 Lux at a Point with Solar Module of 12 V of Capacity not less than 60 Wp made of Monocrystalline Cells, Maintenance Free Lithium Ferro Phosphate (LiFePO4) Battery of Autonomy of Minimum 12 Hrs and Capacity not less than 380 WHr, Housing made of High grade aluminum die-cast/extruded aluminium with good heat dissipation facility, suitable for climatic condition of -10 to +50 Deg C, Humidity of 95% and meeting IP 65 and IK08 requirements etc., complete but without PIR Sensor as required. | 78.00 | Each | 100.00 | 34000.00 | 2652000.00 | 24600.00 | 1918800.00 | 44600.00 | 3478800.00 | 25200.00 | 1965600.00 | 28500.00 | 2223000.00 | 38824.00 | 3028272.00 | 1918800.00 | RVD INFRA SOLUTION PVT.LTD.
3.00 | Supply of following Height GI OCTAGONAL continuously tapered (Bottom and Top dia of the pole not be less than 130 mm & 70mm respectively) Street Light Pole suitable for Wind Velocity as per IS 875, fabricated out of 3 mm thick High Tensile Steel Sheet/Plate in single section with rigid flange plate (250x250x12mm Thick min.) welded with the base of pole for fixing on foundation bolts for installation on a precast foundation including supply of 4 Nos. of foundation bolt (M 24 750mm) and providing weather proof and vandal resistant door flush with the exterior surface containing a terminal plate of 5mm thick backelite sheet with 32A heavy duty connector for loop-in loop-out cable termination suitable for 2 Nos. 4 core 16 sqmm. cable and 6 A DP MCB, Earthing Studs etc., complete as required.
3.10 | 4 Mtrs. High | 36.00 | Each | 100.00 | 8000.00 | 288000.00 | 6000.00 | 216000.00 | 5999.00 | 215964.00 | 8400.00 | 302400.00 | 14500.00 | 522000.00 | 7500.00 | 270000.00 | 215964.00 | Robust Electric
3.20 | 6 Mtrs. High | 78.00 | Each | 100.00 | 11000.00 | 858000.00 | 8160.00 | 636480.00 | 8450.00 | 659100.00 | 11400.00 | 889200.00 | 17500.00 | 1365000.00 | 8076.92 | 629999.76 | 629999.76 | Thokchom Okendro Singh
4.00 | Supply, Fabrication and Installation of 500 mm long, 40 mm Dia. of "C" class GI pipe bracket with 75 mm Dia. MS cape (to be fixed on the top of pole) with suitable arrangements including sockets, brackets, nuts, bolts, painting etc., complete as requierd. | 114.00 | Job | 100.00 | 385.00 | 43890.00 | 1260.00 | 143640.00 | 504.00 | 57456.00 | 600.00 | 68400.00 | 1250.00 | 142500.00 | 552.63 | 62999.82 | 43890.00 | jaydeep agency corporation
5.00 | Installation of 4 / 6 Mtr. Height Octagonal Street Light Pole with all accessories in RCC foundation with 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) foundation of size 50x50x150 cm (120 cm below the ground and 30 cm above the ground) (or as per OEM's Standard which ever is better) including excavation and refilling, positioning of template and foundation bolts (supplied with pole to match with pole base plate) and providing and fixing of PE 63, PN 4, HDPE pipe of size 40 mm dia (2 pieces of each minimum 0.75 Mtr length) in the foundation for loop-in loop-out of the cable, numbering the pole etc., complete as required. | 114.00 | Each | 100.00 | 3500.00 | 399000.00 | 3600.00 | 410400.00 | 2850.00 | 324900.00 | 3000.00 | 342000.00 | 3500.00 | 399000.00 | 7058.87 | 804711.18 | 324900.00 | Robust Electric
6.00 | Installation, Testing and Commissioning of all-in-one solar street light fixture with all accessories on existing arm/pole of Height 6 Mtr. with suitable fixing arrangements, providing and wiring with 3x2.5 Sqmm FRLS copper wire from MCB to Fixture etc., complete as required. | 114.00 | Each | 100.00 | 285.00 | 32490.00 | 720.00 | 82080.00 | 451.00 | 51414.00 | 480.00 | 54720.00 | 250.00 | 28500.00 | 615.79 | 70200.06 | 28500.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
7.00 | Supply of following size XLPE insulated PVC sheathed armoured aluminium conductor cable of 1.1 KV Grade confirming to IS:7098 (Part 1) with upto date amendment etc., complete as required. 4 core x 16 Sqmm. | 4440.00 | Meter | 100.00 | 150.00 | 666000.00 | 132.00 | 586080.00 | 124.00 | 550560.00 | 147.60 | 655344.00 | 190.00 | 843600.00 | 121.62 | 539992.80 | 539992.80 | Thokchom Okendro Singh
8.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc., conforming to IS 16205, Part 24/2018 complete with fitting, cutting, jointing etc., direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. 63 mm dia (OD-63 mm & ID-51 mm nominal) | 3450.00 | Meter | 100.00 | 110.00 | 379500.00 | 192.00 | 662400.00 | 208.00 | 717600.00 | 216.00 | 745200.00 | 165.00 | 569250.00 | 157.50 | 543375.00 | 379500.00 | jaydeep agency corporation
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/ HDPE pipe etc., as required. Upto 35 sq. mm | 4180.00 | Meter | 100.00 | 27.00 | 112860.00 | 12.00 | 50160.00 | 31.00 | 129580.00 | 24.00 | 100320.00 | 35.00 | 146300.00 | 24.30 | 101574.00 | 50160.00 | RVD INFRA SOLUTION PVT.LTD.
10.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 7400.00 | Meter | 100.00 | 38.00 | 281200.00 | 19.00 | 140600.00 | 37.00 | 273800.00 | 24.00 | 177600.00 | 30.00 | 222000.00 | 39.60 | 293040.00 | 140600.00 | RVD INFRA SOLUTION PVT.LTD.
11.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4 X 16 sq. mm (28mm) | 228.00 | Set | 100.00 | 200.00 | 45600.00 | 240.00 | 54720.00 | 245.00 | 55860.00 | 240.00 | 54720.00 | 250.00 | 57000.00 | 792.00 | 180576.00 | 45600.00 | jaydeep agency corporation
12.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc., (with charcoal / coke and salt) as required. | 13.00 | Set | 100.00 | 4950.00 | 64350.00 | 7200.00 | 93600.00 | 5099.00 | 66287.00 | 6000.00 | 78000.00 | 3850.00 | 50050.00 | 5077.80 | 66011.40 | 50050.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
13.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 65.00 | Meter | 100.00 | 190.00 | 12350.00 | 312.00 | 20280.00 | 189.00 | 12285.00 | 240.00 | 15600.00 | 137.00 | 8905.00 | 220.50 | 14332.50 | 8905.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
14.00 | Dismantling of the Existing Street Light Pole i/c Existing Street Light Fitting and Foundation and Shifting Pole and Fitting to the AAI Store as required. | 102.00 | Job | 100.00 | 250.00 | 25500.00 | 360.00 | 36720.00 | 450.00 | 45900.00 | 600.00 | 61200.00 | 1000.00 | 102000.00 | 262.85 | 26810.70 | 25500.00 | jaydeep agency corporation
| Total in Figures |  |  |  |  | 6868740.00 |  | 5786360.00 |  | 7705106.00 |  | 6266304.00 |  | 7593505.00 |  | 7566817.02
Lowest Amount Quoted BY: RVD INFRA SOLUTION PVT.LTD.(5786360.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Old Light Fittings at Perimeter Road Near NH-150 with Hybrid Solar LED Light at Imphal Airport Tender ID: 2021_AAI_78395_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | RVD INFRA SOLUTION PVT.LTD. | 5786360.00 | L1
| 2 | SHARMA TRADE AGENCY | 6266304.00 | L2
| 3 | jaydeep agency corporation | 6868740.00 | L3
| 4 | Thokchom Okendro Singh | 7566817.02 | L4
| 5 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED | 7593505.00 | L5
| 6 | Robust Electric | 7705106.00 | L6