## BoQ1
Government eProcurement System Created By: Dadan Singh Created Date/Time: 12-Jul-2021 11:53 AM Tender Title: Miscellaneous Electrical Works Related to Operational Area, Residential Colony and ATC Building at Raja Bhoj Airport, Bhopal. SH. Electrical works for Anti Hijacking Tender ID: 2021_AAI_79500_1
Tender Inviting Authority: AGM(E-E)-II, AAI, R.B. Airport, Bhopal
Name of Work: Miscellaneous Electrical Works Related to Operational Area, Residential Colony and ATC Building at Raja Bhoj Airport, Bhopal. SH: Electrical works for Anti-Hijacking Room.
Contract No: AAI/BPL/ENGG(E)/NIT-03/2021-22
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | S S Electricals(GSTN-23ADFFS7417K1ZV) |  | SKYLINE ENGINEERS(GSTN-27APZPD0679L1Z4) |  | surbhi association(GSTN-23AGKPD2522N1ZK) |  | Yash Energy Pvt. Ltd(GSTN-24AAACY3771H1ZA) |  | Manish Electricals(GSTN-22ABLPM9012E1ZY) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5) |  | ABHISHEK INTEGRATIONS LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, installation, testing and commissioning of dust, damp and vermin proof cubicle free floor, indoor type factory built sheet steel enclosed modular bolted construction, suitable for operation on 415 ±10% volts, 50 Hz AC 3 phase 4 wire supply system fabricated out of CRCA sheet steel of 2.0 mm thick for frame work and 2.0 mm thick for doors/ covers, 3mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium bus bars of high conductivity, DMC/SMC bus bar supports, bottom base channel of section not less than ISMC 75mm, entire panel shall have a common copper earth bar of suitable size with 2 nos earth studs, including control wiring with 1.5sqmm. PVC insulated FRLS copper conductor Single Core cable for voltage & 2.5sq.mm for current circuits, cable alleys, cable gland plates, danger notice plates, etc. necessary metering protections & indications and mounted with the following switch gears. INCOMER i) 100 Amps. 4P , MCCB '36KA, (Ics = Icu= 36KA) with thermal magnetic release having O/L & S/C protection equiped with extendable Rotary Handle and Spreader Terminals - 02 Set ii) 6 Nos. Phase indication LED lamps with 2Amp MCB, 'ON/OFF' indicating light with 2A MCB. iii) Multifunction meter, class 0.5 with LCD Display shown V,A,Hz & PF - 2 Nos. iv) Current Transformer CT 100/5A , CL-1 , 5 VA - 6 Nos. AUTO TRANSFER SWITCH i) 4 pole, 100 Amps. Open execution type with complete protection - 1 No. BUS-BAR TPN aluminium main bus bars of minimum of 300 Amp capacity with heat shrinkable coloured sleeves and i/c DMC/SMC bus bars supports at required intervals complete. OUTGOING i) 63 Amps. 4P, MCCB '36KA, (Ics = Icu= 36KA) with thermal magnetic release having O/L & S/C protection equiped extendable Rotary Handle and Spreader Terminals - 02 Set ii) 32 Amps. 4P, MCCB '36KA, (Ics = Icu= 36KA) with thermal magnetic release having O/L & S/C protection equiped extendable Rotary Handle and Spreader Terminals - 01 Set iii) ON‐OFF indication lamps (LED type) with 2 Amp control MCBs. - 4 Set | 1.00 | Job |  | 134750.00 | 134750.00 | 235000.00 | 235000.00 | 143500.00 | 143500.00 | 189610.00 | 189610.00 | 185000.00 | 185000.00 | 149000.00 | 149000.00 | 144100.00 | 144100.00 | 134750.00 | S S Electricals
2.00 | Supply & Installation of wall mounted fan, 400 mm sweep suitable for operation on 240V, 50Hz A.C. supply with Pull Code Control operations and High speed motor etc. complete as required. | 7.00 | Each |  | 2920.00 | 20440.00 | 3500.00 | 24500.00 | 2200.00 | 15400.00 | 2340.00 | 16380.00 | 3500.00 | 24500.00 | 2000.00 | 14000.00 | 2035.00 | 14245.00 | 14000.00 | Awasthi Electric Works
3.00 | Supply of 300 mm sweep heavy duty exhaust fan suitable for operation on 240V, 50Hz A.C. supply, 1400 rpm complete as required. | 3.00 | Each |  | 2150.00 | 6450.00 | 4000.00 | 12000.00 | 2000.00 | 6000.00 | 2266.00 | 6798.00 | 3000.00 | 9000.00 | 2250.00 | 6750.00 | 2695.00 | 8085.00 | 6000.00 | surbhi association
4.00 | Supply of 36 Watt recess mounting type LED indoor light fitting (Natural White) suitable for mounting on 600 mm X 600 mm grid channel with with minimum output of 3600 lumens, suitable for 140-270 volt, 50 Hz, PF>0.95, luminaire should have Extruded aluminium / CRCA / Standard ally housing. Luminaire should have minimum IP protection should be IP 20. Total power consumption of fitting (including driver loss) should not more than 110 % of rated capacity of LED Light fitting, complete with all accessories as required. | 28.00 | Each |  | 1380.00 | 38640.00 | 1700.00 | 47600.00 | 2250.00 | 63000.00 | 1246.00 | 34888.00 | 1500.00 | 42000.00 | 1600.00 | 44800.00 | 1540.00 | 43120.00 | 34888.00 | Yash Energy Pvt. Ltd
5.00 | Supply of 12 W High efficient recess mounted downlighter with minimum output of 1200 lumens, suitable for 140-270 volt, 50 Hz, PF>0.95, luminaire should have Extruded aluminium/CRCA/ Standard ally housing. Luminaire should have minimum IP protection should be IP 20. Total power consumption of fitting (including driver loss) should not more than 110 % of rated capacity of LED Light fitting, complete with all accessories as required. | 6.00 | Each |  | 610.00 | 3660.00 | 600.00 | 3600.00 | 800.00 | 4800.00 | 430.00 | 2580.00 | 510.00 | 3060.00 | 850.00 | 5100.00 | 836.00 | 5016.00 | 2580.00 | Yash Energy Pvt. Ltd
6.00 | Supply of Aesthetically designed Rechargeable LED Lantern with long backup time feature with minimum 3 watt / 5 watt, Rechargeable Li-ion battery capacity and suitable charging from 160-270V AC supply 50HZ etc as required. | 1.00 | Each |  | 1650.00 | 1650.00 | 3200.00 | 3200.00 | 1500.00 | 1500.00 | 2266.00 | 2266.00 | 4500.00 | 4500.00 | 2200.00 | 2200.00 | 1100.00 | 1100.00 | 1100.00 | ABHISHEK INTEGRATIONS LIMITED
7.00 | Supply, Installation, Testing & Commissioning of Ceiling Mounted Inverter Cassette Type 3.80 TR / 4.0 TR Three Phase Air Conditioning unit including indoor, outdoor unit fitted with rotary compressor, copper condensor and first charge refrigerant R410A / eco friendly green gas only, cordless remote control, auto air swing louvers, connection copper lead wire between outdoor and indoor unit, connection copper lead wire upto 1.5 Meter, including floor stand for Outdoor unit, condense water outlet and excluding connection of copper pipe of required size, insulation complete etc as required. Outdoor / Indoor units should be of same make (Brand). | 3.00 | Nos. |  | 113850.00 | 341550.00 | 120000.00 | 360000.00 | 99500.00 | 298500.00 | 105704.00 | 317112.00 | 125000.00 | 375000.00 | 98000.00 | 294000.00 | 132000.00 | 396000.00 | 294000.00 | Awasthi Electric Works
8.00 | Supply, Installation, Testing & Commissioning of 1.5 Ton (5 Star) Inverter Split type wall mounted Air conditioning unit, Single phase, including indoor, outdoor unit fitteded with rotary compressor, copper condensor and first charge refrigerant R410A / eco friendly green gas only. The Condensing unit working range should be capable of providing cooling between + 5 Deg C to 50 Deg C including connection of copper pipe of required size upto 3 Meter, insulation, cordless remote control, auto air swing louvers, wall stand for outdoor unit, connection copper lead wire condense water outlet pipe 2 Meter complete etc as required. Outdoor / Indoor units should be of same make (Brand). | 1.00 | Nos. |  | 44550.00 | 44550.00 | 40000.00 | 40000.00 | 40000.00 | 40000.00 | 37716.00 | 37716.00 | 36000.00 | 36000.00 | 32000.00 | 32000.00 | 49500.00 | 49500.00 | 32000.00 | Awasthi Electric Works
9.00 | Supply and Connection of Copper refrigerant piping for Cassette type Airconditioning for complete with suction / liquid line, insulation with all accessories complete etc as required. | 35.00 | Meter |  | 1540.00 | 53900.00 | 1800.00 | 63000.00 | 900.00 | 31500.00 | 880.00 | 30800.00 | 700.00 | 24500.00 | 1200.00 | 42000.00 | 825.00 | 28875.00 | 24500.00 | Manish Electricals
10.00 | Supply & Fixing of suitable size of Electrical power cable for Cassette type Airconditioning between Indoor & Outdoor units complete etc as required. | 35.00 | Meter |  | 250.00 | 8750.00 | 1300.00 | 45500.00 | 160.00 | 5600.00 | 288.00 | 10080.00 | 150.00 | 5250.00 | 90.00 | 3150.00 | 127.00 | 4445.00 | 3150.00 | Awasthi Electric Works
11.00 | Supply, Installation, Testing & Commissioning of automatic programmable AC switching system for the Operation of 02 Nos. (01 No. Running + 01 No. Standby) split type Air conditioner Units to change over the system 04 Hours complete etc as required. | 1.00 | Nos. |  | 12650.00 | 12650.00 | 4000.00 | 4000.00 | 4000.00 | 4000.00 | 6481.00 | 6481.00 | 6500.00 | 6500.00 | 5000.00 | 5000.00 | 7150.00 | 7150.00 | 4000.00 | SKYLINE ENGINEERS, surbhi association
12.00 | Supply of 3.5 core x 70 Sqmm. XLPE insulated PVC Sheathed Armoured Aluminium Conductor Power Cable of 1.1 KV Grade confirming to IS:7098 (Part 1) with upto date amendment etc. complete as required. | 300.00 | Meter |  | 350.00 | 105000.00 | 360.00 | 108000.00 | 335.00 | 100500.00 | 297.00 | 89100.00 | 340.00 | 102000.00 | 350.00 | 105000.00 | 363.00 | 108900.00 | 89100.00 | Yash Energy Pvt. Ltd
13.00 | Supply of 2 core x 1.5 Sqmm. XLPE insulated PVC Sheathed Armoured Copper Conductor Cable of 1.1 KV Grade confirming to IS:7098 (Part 1) with upto date amendment etc. complete as required. | 150.00 | Meter |  | 100.00 | 15000.00 | 75.00 | 11250.00 | 110.00 | 16500.00 | 62.00 | 9300.00 | 60.00 | 9000.00 | 95.00 | 14250.00 | 74.00 | 11100.00 | 9000.00 | Manish Electricals
14.00 | Installation of exhaust fan of size 300 mm sweep in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. | 3.00 | Each |  | 330.00 | 990.00 | 250.00 | 750.00 | 200.00 | 600.00 | 566.00 | 1698.00 | 300.00 | 900.00 | 350.00 | 1050.00 | 110.00 | 330.00 | 330.00 | ABHISHEK INTEGRATIONS LIMITED
15.00 | Installation, testing and commissioning of pre-wired, Recess Fitting / Surface Fitting / Downlighter Fittings of all types, complete with all accessories and LED lamp etc. directly on ceiling / wall, including connections with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 34.00 | Each |  | 440.00 | 14960.00 | 250.00 | 8500.00 | 80.00 | 2720.00 | 453.00 | 15402.00 | 200.00 | 6800.00 | 50.00 | 1700.00 | 88.00 | 2992.00 | 1700.00 | Awasthi Electric Works
16.00 | Supplying and making end termination with brass compression gland and aluminium lugs for size of 3.5 x 70 sq.mm. PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. | 4.00 | Set |  | 880.00 | 3520.00 | 500.00 | 2000.00 | 300.00 | 1200.00 | 1278.00 | 5112.00 | 700.00 | 2800.00 | 250.00 | 1000.00 | 493.00 | 1972.00 | 1000.00 | Awasthi Electric Works
17.00 | Earthing with G. I. pipe 4.5 m long x 40 mm dia. (Drilling of 300 mm dia, 4.5 Mtr deep by using Borewell machine) including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. including charcoal or coke and salt complete as required. | 2.00 | Set |  | 16500.00 | 33000.00 | 5000.00 | 10000.00 | 5000.00 | 10000.00 | 13197.00 | 26394.00 | 7000.00 | 14000.00 | 5000.00 | 10000.00 | 5500.00 | 11000.00 | 10000.00 | SKYLINE ENGINEERS, surbhi association, Awasthi Electric Works
18.00 | Providing and fixing 25mm X 5 mm GI strip on surface or in recess for connections etc. as required. | 30.00 | Meter |  | 200.00 | 6000.00 | 110.00 | 3300.00 | 120.00 | 3600.00 | 156.00 | 4680.00 | 400.00 | 12000.00 | 120.00 | 3600.00 | 44.00 | 1320.00 | 1320.00 | ABHISHEK INTEGRATIONS LIMITED
19.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Above 35 sq. mm and upto 95 sq. mm size in the existing masonry open duct as required. | 30.00 | Meter |  | 110.00 | 3300.00 | 50.00 | 1500.00 | 30.00 | 900.00 | 40.00 | 1200.00 | 20.00 | 600.00 | 50.00 | 1500.00 | 44.00 | 1320.00 | 600.00 | Manish Electricals
20.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Above 35 sq. mm and upto 95 sq. mm size in the existing RCC/ HUME/ METAL pipe as required. | 20.00 | Meter |  | 140.00 | 2800.00 | 30.00 | 600.00 | 30.00 | 600.00 | 45.00 | 900.00 | 20.00 | 400.00 | 50.00 | 1000.00 | 55.00 | 1100.00 | 400.00 | Manish Electricals
21.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Above 35 sq. mm and upto 95 sq. mm (clamped with 25 x 3 mm MS flat clamp) size on wall surface as required. | 250.00 | Meter |  | 140.00 | 35000.00 | 100.00 | 25000.00 | 30.00 | 7500.00 | 74.00 | 18500.00 | 60.00 | 15000.00 | 80.00 | 20000.00 | 143.00 | 35750.00 | 7500.00 | surbhi association
22.00 | Supply and Installation of Microprocessor based 2 Zone non-expandable conventional fire alarm panel. The Panel should be equiped of 2 Zone capacity to take maximum 20 detections per zone, reset function inbuilt and alarm & Fault Display by individual LEDs for each detector group. 240 volts AC power supply, automatic battery charges, 2 nos X 12 volt sealed maintenance free batteries complete etc as required. | 1.00 | Nos. |  | 9570.00 | 9570.00 | 8000.00 | 8000.00 | 12000.00 | 12000.00 | 13130.00 | 13130.00 | 20000.00 | 20000.00 | 5500.00 | 5500.00 | 8250.00 | 8250.00 | 5500.00 | Awasthi Electric Works
23.00 | Supply and Installation of 2 Channel wireless auto dialer (GSM based) voice message. 40 (20+20) seconds voice recording. 9 nos of tel./mobile 16 digit each. View numbers & user setting any time. Standard telephone key pads. Work with all types of GSM network. Easy menu based programming. 1 levels of password protection complete etc as required. | 1.00 | Nos. |  | 9110.00 | 9110.00 | 13500.00 | 13500.00 | 7000.00 | 7000.00 | 14263.00 | 14263.00 | 23000.00 | 23000.00 | 9000.00 | 9000.00 | 16500.00 | 16500.00 | 7000.00 | surbhi association
24.00 | Supply and Installation of Conventional Type Smoke Detector with LED indication, with mounting base complete etc as required. | 19.00 | Nos. |  | 1080.00 | 20520.00 | 800.00 | 15200.00 | 1200.00 | 22800.00 | 1100.00 | 20900.00 | 3000.00 | 57000.00 | 1000.00 | 19000.00 | 1595.00 | 30305.00 | 15200.00 | SKYLINE ENGINEERS
25.00 | Supply and Installation of Conventional Type Heat Detector with LED indication, with mounting base complete etc as required. | 1.00 | Nos. |  | 1430.00 | 1430.00 | 800.00 | 800.00 | 2580.00 | 2580.00 | 1263.00 | 1263.00 | 3000.00 | 3000.00 | 1000.00 | 1000.00 | 2013.00 | 2013.00 | 800.00 | SKYLINE ENGINEERS
26.00 | Supply and Installation of Conventional Type Hooter complete etc as required. | 1.00 | Nos. |  | 1200.00 | 1200.00 | 450.00 | 450.00 | 2500.00 | 2500.00 | 1376.00 | 1376.00 | 4200.00 | 4200.00 | 650.00 | 650.00 | 2013.00 | 2013.00 | 450.00 | SKYLINE ENGINEERS
27.00 | Supply and Installation of Manual call points complete etc as required. | 1.00 | Nos. |  | 1140.00 | 1140.00 | 600.00 | 600.00 | 201.00 | 201.00 | 1426.00 | 1426.00 | 350.00 | 350.00 | 500.00 | 500.00 | 385.00 | 385.00 | 201.00 | surbhi association
| Total in Figures |  |  |  |  | 929530.00 |  | 1047850.00 |  | 805001.00 |  | 879355.00 |  | 986360.00 |  | 792750.00 |  | 936886.00
Lowest Amount Quoted BY: Awasthi Electric Works(792750.00)

## BOQ Summary
BOQ Summary Details Tender Title: Miscellaneous Electrical Works Related to Operational Area, Residential Colony and ATC Building at Raja Bhoj Airport, Bhopal. SH. Electrical works for Anti Hijacking Tender ID: 2021_AAI_79500_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Awasthi Electric Works | 792750.00 | L1
| 2 | surbhi association | 805001.00 | L2
| 3 | Yash Energy Pvt. Ltd | 879355.00 | L3
| 4 | S S Electricals | 929530.00 | L4
| 5 | ABHISHEK INTEGRATIONS LIMITED | 936886.00 | L5
| 6 | Manish Electricals | 986360.00 | L6
| 7 | SKYLINE ENGINEERS | 1047850.00 | L7