## BoQ1
Government eProcurement System Created By: Saubhik Pan Created Date/Time: 18-Oct-2021 01:51 PM Tender Title: Provision of UPS System and Active Harmonic Filters for the GLF System in CCR hall at NSCBI Airport Tender ID: 2021_AAI_80010_1
Tender Inviting Authority: AIRPORTS AUTHORITY OF INDIA
Name of Work: Provision of UPS System and Active Harmonic Filters for the GLF System in CCR hall at NSCBI Airport.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | K KUMAR RAJA PROJECTS PVT LIMITED(GSTN-37AABCK5644G1ZI) |  | Labotek(GSTN-07AAEFL9553B1ZD) |  | ISSAR INDUSTRIES(GSTN-07AAQPG9724P1ZV)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH: A - ELECTRICAL WORKS Supply, Installation, Testing & Commissioning (SITC) of 300KVA (Nominal Capacity) UPS unit, 3-phase-4 wire, suitable for operating condition 415±15%, 3ph, 50Hz ± 10% IGBT rectifier and PWM Controlled IGBT inverter based online double conversion type DSP controlled UPS, True Sinewave, suitable for operation for constant current regulators with 100% unbalanced load at output at full load condition along with standard features like 100% rated static bypass, maintenance bypass facilities, battery monitoring features integrated with UPS controller, IP20 capable of running at 100% load and having provision of upgrading the UPS to run in load sharing mode with suitable isolator confirming to the specification attached along with K-13 copper wound transformer (with Galvonic Isolation) suitable for the system, but without batteries, as per specifications attached and as directed by Engineer-In-Charge (EIC). | 4.00 | jobs | 3038263.82 | 4000000.00 | 16000000.00 | 4100000.00 | 16400000.00 | 4202500.00 | 16810000.00 | 16000000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
2.00 | Design, Selection & SITC (Supply, Installation, Testing & Commissioning) of VRLA/SMF battery bank, mounted in suitable rack (as per recommendation of battery manufacturer) consisting of 12 V VRLA/SMF battery capable of providing backup for at least 30 mins. at full rated load of above mentioned UPS (as per item no.1) along with necessary inter-cell connectors, interconnection of UPS and Battery bank using suitable size rated fire resistant Nyvin copper cables (as recommended by battery manufacturer) and as per specifications attached and as directed by EIC. | 4.00 | sets | 1590750.00 | 3600000.00 | 14400000.00 | 3993000.00 | 15972000.00 | 3998000.00 | 15992000.00 | 14400000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
3.00 | Design, Supply, Installation, Testing & Commissioning of Battery Monitoring System for UPS Battery (Battery Monitoring System - BMS) related to item no. 2 and as per attached specification (Complete with including all hardware, installation accessories, software, cable for communication with remote and colored Inktank type printer with cartridges) having the facility of data reading, recording, analyzing & exporting with suitable format. | 1.00 | job | 1342840.45 | 1800000.00 | 1800000.00 | 4100000.00 | 4100000.00 | 4250000.00 | 4250000.00 | 1800000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
4.00 | Design, fabrication (TTA assembly), Supply, Installation, testing & commissioning of both side extendable, floor mounted type, fully compartmentalized, front operated, back openable, LT cubicle panel suitable for incoming and outgoing cable entry from bottom as per IEC61439-1 & 2 as per following: Bus Bars: 1600A, 3phase with 100% Neutral Aluminum bus bar- 1 set. Incomers & Bus coupler: 2 Nos Incomer and 1No. Buscoupler - 1250 Amp 415V(Uimp=12KV), 65KA (Icu @415V=Ics=Icw for 1 sec) 4Pole EDO (Electrically operated Draw-out) type microprocessor controlled Modular ACB with LSIG release (zone: O/L, S/C, Instantaneous & ground fault) comprising of atleast 5 current settings in LSIG and 5 time settings in LSG, IDMTL settings for proper co-ordination with upstream relay protection system, thermal memory in O/L, alarms & protection options for current imbalance, maximum demand, voltage unbalance, overvoltage, under voltage, reverse power & phase sequence, capability of load shedding and reconnection, in-built metering through rogowsky CT and LCD display of V,I,,W, VAR, VA, Wh, VARh, VAh, Pf , percentage loading bar graph, 10 trip history date & time stamped, interrupted current value upto short circuit level and percentage wear indication; Two separate microprocessor shall be used for protection and measurement. Continuous display to be ensured through 24 Volt DC from SMPS/in panel battery module. Neutral protection shall be settable 20% to 100%. ACB shall be capable of communicating data on Ethernet protocol and on-line parameterization capable. Incoming ACB & outgoing ACBs/MCCBs shall be Zone Selective Interlocked. 2 nos. Panel mounted Front display module connected with release of all ACB in the panel to show all metering and operating assistances of trips, electrical & mechanical counters, % contact wear & load profile. 3 Sets – ON ,OFF ,Trip, Spring Charged, ready to close indication LED lamps with back-up MCB. 2 Sets - R,Y,B Phase indication LED lamp with back up MCB. 1 set for 3 nos. ACBs- Electrical interlocking so that only two ACBs can be made ON at a time with PLC Based Auto Bus Transfer System. Outgoings: 4 Nos - 800 Amp 415V(Uimp=12KV), 65KA (Icu @415V=Ics=Icw for 1 sec) 4Pole EDO (Electrically operated Draw-out) type microprocessor controlled Modular ACB with LSIG release (zone: O/L, S/C, Instantaneous & ground fault) comprising of at least 5 current settings in LSIG and 5 time settings in LSG, IDMTL settings for proper co-ordination with upstream relay protection system, thermal memory in O/L, alarms & protection options for current imbalance, maximum demand, voltage unbalance, overvoltage, under voltage, reverse power & phase sequence, capability of load shedding and reconnection, in-built metering through rogowsky CT and LCD display of V,I,,W, VAR, VA, Wh, VARh, VAh, Pf , percentage loading bar graph, 10 trip history date & time stamped, interrupted current value upto short circuit level and percentage wear indication; Two separate microprocessor shall be used for protection and measurement. Continuous display to be ensured through 24 Volt DC from SMPS/in panel battery module. ACB shall have door interlock and ready to close contact. Neutral protection shall be settable 20% to 100%. ACB shall be capable of communicating data on Ethernet protocol and on-line parameterization capable. Incoming ACB & outgoing ACBs/MCCBs shall be Zone Selective Interlocked. 4 Sets - ON, OFF, Trip, Spring Charged, ready to close indication LED lamps with back-up MCB. Communication: All ACBs shall be connected on Modbus TCP-IP to be centrally monitored from LAN through web server within the panel or central Power Monitoring software/Power SCADA. Breaker status, trip history, counters, % contact wear, settings, pre-alarm, metering data shall be obtained from communication. Suitable Industrial grade Ethernet Switch shall be there to obtain the data remotely and local RJ45 port shall be there to communicate with all ACBs through Laptop for parameterization and data collection. Power supply module(s) & Battery back-up for 24V DC to support continuous display and communication. 4 Nos. 250A 4P MCCB 65kA Fault rated with double break roto active mechanism O/L, S/C release, ROH , Spreader. | 1.00 | job | 2805780.00 | 3800000.00 | 3800000.00 | 4500000.00 | 4500000.00 | 4650000.00 | 4650000.00 | 3800000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
5.00 | Design, fabrication, Supply, Installation, testing & commissioning of both side extendable, floor mounted type, fully compartmentalized, front operated, back openable, LT cubicle panel suitable for incoming and outgoing cable entry from bottom as per IEC61439-1 & 2 CPRI/ ERDA tested. Incomers: 4 Nos - 800 Amp 415V(Uimp=12KV), 65KA (Icu @415V=Ics=Icw for 1 sec) 4Pole EDO (Electrically operated Draw-out) type microprocessor controlled Modular ACB with LSIG release (zone: O/L, S/C, Instantaneous & ground fault) comprising of at least 5 current settings in LSIG and 5 time settings in LSG, IDMTL settings for proper co-ordination with upstream relay protection system, thermal memory in O/L, alarms & protection options for current imbalance, maximum demand, voltage unbalance, overvoltage, under voltage, reverse power & phase sequence, capability of load shedding and reconnection, in-built metering through rogowsky CT and LCD display of V,I,,W, VAR, VA, Wh, VARh, VAh, Pf , percentage loading bar graph, 10 trip history date & time stamped, interrupted current value upto short circuit level and percentage wear indication; Two separate microprocessor shall be used for protection and measurement. Continuous display to be ensured through 24 Volt DC from SMPS/in panel battery module. ACB shall have door interlock and ready to close contact. Neutral protection shall be settable from 20% to 100%. ACB shall be capable of communicating data on Ethernet protocol and on-line parameterization capable. Incoming ACB & outgoing ACBs/MCCBs shall be Zone Selective Interlocked. 1No. Buscoupler - 1250 Amp 415V(Uimp=12KV), 65KA (Icu @415V=Ics=Icw for 1 sec) 4Pole EDO (Electrically operated Draw-out) type microprocessor controlled Modular ACB with LSIG release (zone: O/L, S/C, Instantaneous & ground fault) comprising of atleast 5 current settings in LSIG and 5 time settings in LSG, IDMTL settings for proper co-ordination with upstream relay protection system, thermal memory in O/L, alarms & protection options for current imbalance, maximum demand, voltage unbalance, overvoltage, under voltage, reverse power & phase sequence, capability of load shedding and reconnection, in-built metering through rogowsky CT and LCD display of V,I,,W, VAR, VA, Wh, VARh, VAh, Pf , percentage loading bar graph, 10 trip history date & time stamped, interrupted current value upto short circuit level and percentage wear indication; Two separate microprocessor shall be used for protection and measurement. Continuous display to be ensured through 24 Volt DC from SMPS/in panel battery module. Neutral protection shall be settable from 20% to 100%. ACB shall be capable of communicating data on Ethernet protocol and on-line parameterization capable. Incoming ACB & outgoing ACBs/MCCBs shall be Zone Selective Interlocked. 2 nos. Panel mounted Front display module connected with release of all ACB in the panel to show all metering and operating assistance of trips, electrical & mechanical counters, % contact wear & load profile. 5 Sets - ON, OFF, Trip, Spring Charged, ready to close indication LED lamps with back-up MCB. 4 Sets - R,Y,B Phase indication LED lamp with back up MCB. 4 Sets - 800/5A CT Class-1.0 VA 15VA required for AHF Sensing in each incoming. Bus Bars: 1600A, 3phase with 100% Neutral Aluminum bus bar- 1 set. Outgoings: 6 Nos - 800 Amp 415V(Uimp=12KV), 65KA (Icu @415V=Ics=Icw for 1 sec) 4Pole EDO (Electrically operated Draw-out) type microprocessor controlled Modular ACB with LSIG release (zone: O/L, S/C, Instantaneous & ground fault) comprising of atleast 5 current settings in LSIG and 5 time settings in LSG, IDMTL settings for proper co-ordination with upstream relay protection system, thermal memory in O/L, alarms & protection options for current imbalance, maximum demand, voltage unbalance, overvoltage, under voltage, reverse power & phase sequence, capability of load shedding and reconnection, in-built metering through rogowsky CT and LCD display of V,I,,W, VAR, VA, Wh, VARh, VAh, Pf , percentage loading bar graph, 10 trip history date & time stamped, interrupted current value upto short circuit level and percentage wear indication; Two separate microprocessor shall be used for protection and measurement. Continuous display to be ensured through 24 Volt DC from SMPS/in panel battery module. ACB shall have door interlock and ready to close contact. Neutral protection shall be settable from 20% to 100%. ACB shall be capable of communicating data on Ethernet protocol and on-line parameterization capable. Incoming ACB & outgoing ACBs/MCCBs shall be Zone Selective Interlocked. 6 Sets - ON,OFF, Trip, Spring Charged, ready to close indication LED lamps with back-up MCB. Communication: All ACBs shall be connected on Modbus TCP-IP to be centrally monitored from LAN through web server within the panel or central Power Monitoring software/Power SCADA. Breaker status, trip history, counters, % contact wear, settings, pre-alarm, metering data shall be obtained from communication. Suitable Industrial grade Ethernet Switch shall be there to obtain the data remotely and local RJ45 port shall be there to communicate with all ACBs through Laptop for parameterization and data collection. Power supply module(s) & Battery back-up for 24V DC to support continuous display and communication. 4 Nos. 250A 4P MCCB 65kA Fault rated with double break roto active mechanism O/L, S/C release, ROH, Spreader for AHF. 2 Nos. 400A 4P MCCB 65kA Fault rated with double break roto active mechanism O/L, S/C release, ROH, Spreader. | 1.00 | job | 4150090.00 | 5400000.00 | 5400000.00 | 4500000.00 | 4500000.00 | 4550000.00 | 4550000.00 | 4500000.00 | Labotek
6.00 | Design, selection (within following range of capacity) and SITC of 415 V AC, 50Hz, 3 Ph 4 wire, Active Harmonic Filter (AHF) along with performance check, housed in floor-mounted free standing type metallic enclosure having IP-42 protection suitable for Indoor Application having provision of Bottom and Top Cable entry for harmonic mitigation at the level of 2nd to 51st Harmonics and capable for Power Factor Correction upto 0.80-lagging nature when primary source is DG set and 0.99 when primary source is Commercial supply with Auto changeover (with auto & manual mode selection) facility as required as per specifications attached. (a) at least 100A | 4.00 | Nos. | 530250.00 | 1260000.00 | 5040000.00 | 1850000.00 | 7400000.00 | 1850050.00 | 7400200.00 | 5040000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
7.00 | Design, Selection, supply, installation, testing and commissioning of (not less than 22 TR with provision of 22 TR standby) split type air-conditioning system to maintain the indoor ambience of 26°C, 60±5% RH and noise level upto 70 dB of UPS room and battery room (Approx. maximum Area: 120sq.m. floor area with room ht. of 4m) against outdoor ambience of 50°C. The system should comprise of wall mounted type indoor unit connected to suitable outdoor units having air cooled condenser & energy efficient scroll compressor using green refrigerant (407C/equivalent) along with refrigerant piping, nitrogen flushing followed by leak testing and refrigerant filling and thermally insulated condensate drain piping up to designated common pit as per OEM recommendation, as per specifications attached and as directed by Engineer-in-charge. | 1.00 | job | 997375.00 | 2200000.00 | 2200000.00 | 7500000.00 | 7500000.00 | 7500500.00 | 7500500.00 | 2200000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
8.00 | Earthing with copper earth plate 600 mm x 600 mm x 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal / coke and salt as required. | 8.00 | sets | 10155.55 | 20000.00 | 160000.00 | 40000.00 | 320000.00 | 45000.00 | 360000.00 | 160000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
9.00 | Earthing with GI earth plate 600 mm x 600 mm x 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal / coke and salt as required. | 2.00 | sets | 5801.44 | 10000.00 | 20000.00 | 25000.00 | 50000.00 | 26000.00 | 52000.00 | 20000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
10.00 | Providing and fixing 50 mm x 6 mm copper strip in 80 mm dia. G.I pipe from earth electrode including connection zawith brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 215.00 | mtrs. | 757.50 | 4000.00 | 860000.00 | 1550.00 | 333250.00 | 1650.00 | 354750.00 | 333250.00 | Labotek
11.00 | Providing and fixing 50 mm x 6 mm GI strip in 80 mm dia G.I pipe from earth electrode including connection with GI nut, bolt, spring, washer excavation and re-filling etc. as required. | 150.00 | mtrs. | 555.50 | 1000.00 | 150000.00 | 800.00 | 120000.00 | 900.00 | 135000.00 | 120000.00 | Labotek
12.00 | Providing and fixing 50 mm x 6 mm GI strip on surface or in recess for connections etc. as required. | 20.00 | mtrs. | 199.98 | 350.00 | 7000.00 | 800.00 | 16000.00 | 900.00 | 18000.00 | 7000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
13.00 | Supplying and installing following size of Hot dip Galvanized perforated type cable trays of following sections along with connectors, necessary wall support made of RS Angle including bolts & nuts etc. and painting as required. a) 450 mm wide X 50 mm X 2mm thick | 55.00 | m | 1104.94 | 2000.00 | 110000.00 | 1550.00 | 85250.00 | 1650.00 | 90750.00 | 85250.00 | Labotek
14.00 | Supplying and installing following size of Hot dip Galvanized perforated type cable trays of following sections along with connectors, necessary wall support made of RS Angle including bolts & nuts etc. and painting as required. b) 150 mm wide X 50 mm X 2mm thick | 30.00 | m | 322.19 | 1200.00 | 36000.00 | 1200.00 | 36000.00 | 1250.00 | 37500.00 | 36000.00 | K KUMAR RAJA PROJECTS PVT LIMITED, Labotek
15.00 | Supply Fabrication & installation of 8 mm thick chequered plate duty painted for covering Cable trench, with lifting hook and straighter/supports along with provision of MS angle iron structure in cable trench etc. inside the substation yard. | 25.00 | sqm | 821.13 | 7000.00 | 175000.00 | 20000.00 | 500000.00 | 25000.00 | 625000.00 | 175000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
16.00 | Providing & fixing of Carbon dioxide (CO2) type fire extinguishers conforming to IS 2878-1976 and cylinder fully charged of 4.5 Kg capacity hanged on wall with bracket component as required. | 4.00 | nos. | 2601.76 | 8000.00 | 32000.00 | 19500.00 | 78000.00 | 19550.00 | 78200.00 | 32000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
17.00 | Providing & fixing of First Aid box as approved by St. John Ambulance Brigade / Indian red Cross conforming to IS 2217 -1963 | 4.00 | nos. | 821.13 | 2500.00 | 10000.00 | 3500.00 | 14000.00 | 3550.00 | 14200.00 | 10000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
18.00 | Supply & fixing of fire retardant/ extinguishing Electrical insulated synthetic mat of 2.0 mm thick +/- 10% confirming to BIS: DOC NO. ET-02 (5440) meeting requirements of IS: 15652 :2006 (with up to date amendment), suitable for all voltages not exceeding 3.3 KV and having minimum width of 1000 mm +/- 20mm and including supply of required quantity of adhesive/ compound and fixing the same at size as per site requirements. | 30.00 | mtrs. | 1726.09 | 1200.00 | 36000.00 | 2800.00 | 84000.00 | 2890.00 | 86700.00 | 36000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
19.00 | Supply of following size power cables of 1.1 KV grade, XLPE Insulated PVC Sheathed aluminum conductor cable, armored, and PVC sheathed conforming to IS 7098 Part-I with up-to-date amendments. (a) 4 C X95 Sq. mm | 800.00 | mtrs. | 454.50 | 700.00 | 560000.00 | 1200.00 | 960000.00 | 1250.00 | 1000000.00 | 560000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
20.00 | Supply of following size power cables of 1.1 KV grade, XLPE Insulated PVC Sheathed aluminum conductor cable, armored, and PVC sheathed conforming to IS 7098 Part-I with up-to-date amendments. (b) 4 C X 120 Sq. mm | 300.00 | mtrs. | 619.13 | 900.00 | 270000.00 | 1500.00 | 450000.00 | 1600.00 | 480000.00 | 270000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
21.00 | Supply of following size power cables of 1.1 KV grade, XLPE Insulated PVC Sheathed aluminum conductor cable, armored, and PVC sheathed conforming to IS 7098 Part-I with up-to-date amendments. (c ) 3½ X 240 sq. mm | 380.00 | mtrs. | 1010.00 | 1400.00 | 532000.00 | 2010.00 | 763800.00 | 2500.00 | 950000.00 | 532000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
22.00 | Supply of following size power cables of 1.1 KV grade, round wire armoured FR PVC Insulated multi-stranded, flexible, copper conductor cable, PVC sheathed conforming to IS 1554 with up to date amendments. (a) 1 C X120 Sq. mm | 1800.00 | mtrs. | 1064.54 | 3600.00 | 6480000.00 | 2000.00 | 3600000.00 | 2500.00 | 4500000.00 | 3600000.00 | Labotek
23.00 | Supplying and making end termination with brass compression gland and aluminum lugs for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1 KV grade as required. (a) 4 X 95 sq. mm | 16.00 | each | 456.52 | 1000.00 | 16000.00 | 890.00 | 14240.00 | 895.00 | 14320.00 | 14240.00 | Labotek
24.00 | Supplying and making end termination with brass compression gland and aluminum lugs for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1 KV grade as required. (b) 4 X 120 sq. mm | 8.00 | each | 470.66 | 1200.00 | 9600.00 | 910.00 | 7280.00 | 925.00 | 7400.00 | 7280.00 | Labotek
25.00 | Supplying and making end termination with brass compression gland and aluminum lugs for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1 KV grade as required. (c ) 3½ X 240 sq. mm | 12.00 | each | 763.56 | 1800.00 | 21600.00 | 2000.00 | 24000.00 | 2500.00 | 30000.00 | 21600.00 | K KUMAR RAJA PROJECTS PVT LIMITED
26.00 | Supplying and making end termination with brass compression gland and copper lugs for following size of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 KV grade as required. (a) 1 X120 sq. mm | 120.00 | each | 454.50 | 300.00 | 36000.00 | 310.00 | 37200.00 | 325.00 | 39000.00 | 36000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
27.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL pipe as required. (a) Upto 35 sq. mm Aluminium | 5.00 | mtrs. | 31.31 | 40.00 | 200.00 | 70.00 | 350.00 | 80.00 | 400.00 | 200.00 | K KUMAR RAJA PROJECTS PVT LIMITED
28.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL pipe as required. (b) Above 35 sq. mm and upto 95 sq. mm Aluminium | 5.00 | mtrs. | 48.48 | 50.00 | 250.00 | 75.00 | 375.00 | 85.00 | 425.00 | 250.00 | K KUMAR RAJA PROJECTS PVT LIMITED
29.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL pipe as required. (c ) Above 95 sq. mm and upto 185 sq. mm Aluminium | 5.00 | mtrs. | 65.65 | 50.00 | 250.00 | 80.00 | 400.00 | 90.00 | 450.00 | 250.00 | K KUMAR RAJA PROJECTS PVT LIMITED
30.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL pipe as required. (d) Above 185 sq. mm and upto 400 sq. mm Aluminium | 15.00 | mtrs. | 115.14 | 60.00 | 900.00 | 85.00 | 1275.00 | 95.00 | 1425.00 | 900.00 | K KUMAR RAJA PROJECTS PVT LIMITED
31.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. (a) Upto 35 sq. mm Aluminium | 15.00 | mtrs. | 24.24 | 40.00 | 600.00 | 70.00 | 1050.00 | 80.00 | 1200.00 | 600.00 | K KUMAR RAJA PROJECTS PVT LIMITED
32.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. (b) Above 35 sq. mm and upto 95 sq. mm Aluminium | 640.00 | mtrs. | 39.39 | 50.00 | 32000.00 | 75.00 | 48000.00 | 85.00 | 54400.00 | 32000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
33.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. (c ) Above 95 sq. mm and upto 185 sq. mm Aluminium | 240.00 | mtrs. | 54.54 | 50.00 | 12000.00 | 90.00 | 21600.00 | 95.00 | 22800.00 | 12000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
34.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. (d) Above 185 sq. mm and upto 400 sq. mm Aluminium | 300.00 | mtrs. | 98.98 | 60.00 | 18000.00 | 95.00 | 28500.00 | 98.00 | 29400.00 | 18000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
35.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. (a) upto 35 sq. mm (clamped with 1mm thick saddle) Aluminium | 120.00 | mtrs. | 32.32 | 90.00 | 10800.00 | 85.00 | 10200.00 | 98.00 | 11760.00 | 10200.00 | Labotek
36.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. (b) Above 35 sq. mm and upto 95 sq. mm (clamped with 25 X 3 mm MS flat clamp) Aluminium | 10.00 | mtrs. | 72.72 | 150.00 | 1500.00 | 85.00 | 850.00 | 90.00 | 900.00 | 850.00 | Labotek
37.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. (c ) Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40 X 3 mm MS flat clamp) Aluminium | 25.00 | mtrs. | 91.91 | 180.00 | 4500.00 | 90.00 | 2250.00 | 98.00 | 2450.00 | 2250.00 | Labotek
38.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. (d) Above 185 sq. mm and upto 400 sq. mm (clamped with 40 X 3 mm MS flat clamp) Aluminium | 120.00 | mtrs. | 150.49 | 200.00 | 24000.00 | 95.00 | 11400.00 | 98.00 | 11760.00 | 11400.00 | Labotek
39.00 | Laying of one number PVC insulated copper conductor power cable of 1.1 KV grade of following size in the existing masonry open duct as required. (a) 1 C X120 Sq. mm | 1600.00 | mtrs. | 58.58 | 40.00 | 64000.00 | 80.00 | 128000.00 | 85.00 | 136000.00 | 64000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
40.00 | Dismantling of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL/HDPE pipe as required. (a) Upto 35 sq. mm | 15.00 | mtrs. | 34.34 | 30.00 | 450.00 | 35.00 | 525.00 | 45.00 | 675.00 | 450.00 | K KUMAR RAJA PROJECTS PVT LIMITED
41.00 | Dismantling of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL/HDPE pipe as required. (b) Above 35 sq. mm and upto 95 sq. mm | 15.00 | mtrs. | 54.54 | 30.00 | 450.00 | 35.00 | 525.00 | 40.00 | 600.00 | 450.00 | K KUMAR RAJA PROJECTS PVT LIMITED
42.00 | Dismantling of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL/HDPE pipe as required. (c ) Above 95 sq. mm and upto 185 sq. mm | 15.00 | mtrs. | 65.65 | 40.00 | 600.00 | 40.00 | 600.00 | 50.00 | 750.00 | 600.00 | K KUMAR RAJA PROJECTS PVT LIMITED, Labotek
43.00 | Dismantling of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL/HDPE pipe as required. (d) Above 185 sq. mm and upto 400 sq. mm | 15.00 | mtrs. | 90.90 | 40.00 | 600.00 | 45.00 | 675.00 | 50.00 | 750.00 | 600.00 | K KUMAR RAJA PROJECTS PVT LIMITED
44.00 | Dismantling of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. (a) Upto 35 sq. mm | 15.00 | mtrs. | 34.34 | 30.00 | 450.00 | 30.00 | 450.00 | 35.00 | 525.00 | 450.00 | K KUMAR RAJA PROJECTS PVT LIMITED, Labotek
45.00 | Dismantling of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. (b) Above 35 sq. mm and upto 95 sq. mm | 15.00 | mtrs. | 54.54 | 30.00 | 450.00 | 35.00 | 525.00 | 40.00 | 600.00 | 450.00 | K KUMAR RAJA PROJECTS PVT LIMITED
46.00 | Dismantling of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. (c ) Above 95 sq. mm and upto 185 sq. mm | 30.00 | mtrs. | 60.60 | 40.00 | 1200.00 | 35.00 | 1050.00 | 45.00 | 1350.00 | 1050.00 | Labotek
47.00 | Dismantling of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. (d) Above 185 sq. mm and upto 400 sq. mm | 30.00 | mtrs. | 90.90 | 40.00 | 1200.00 | 40.00 | 1200.00 | 55.00 | 1650.00 | 1200.00 | K KUMAR RAJA PROJECTS PVT LIMITED, Labotek
48.00 | SH: B - CIVIL WORKS Dismantling steel work in built-up sections in angels, tees, flats and channels including all gusset plates, bolts, nuts, cutting rivets, welding etc. including dismembering and stacking within 50 mtrs. lead. | 2500.00 | Kg | 4.78 | 15.00 | 37500.00 | 18.00 | 45000.00 | 20.00 | 50000.00 | 37500.00 | K KUMAR RAJA PROJECTS PVT LIMITED
49.00 | Brick work with common burnt clay F.P.S (non-modular) bricks of class designation 7.5 in super structure above plinth level upto floor V level in all shapes and sizes in: Cement mortar 1:4 (1 cement: 4 coarse sand) | 41.00 | Cum | 8994.23 | 9000.00 | 369000.00 | 6200.00 | 254200.00 | 6450.00 | 264450.00 | 254200.00 | Labotek
50.00 | Demolishing cement concrete manually / by mechanical means including disposal of material within 50 mtrs. lead as per direction of Engineer -in-charge. Nominal concrete 1:3:6 or richer mixer (i/c equivalent design mix). | 11.00 | Cum | 2001.09 | 2000.00 | 22000.00 | 1200.00 | 13200.00 | 1350.00 | 14850.00 | 13200.00 | Labotek
51.00 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil. | 28.00 | Cum | 290.58 | 350.00 | 9800.00 | 210.00 | 5880.00 | 230.00 | 6440.00 | 5880.00 | Labotek
52.00 | Providing and lying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:4:8 (1 Cement : 4 Coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size). | 6.00 | Cum | 6668.12 | 6750.00 | 40500.00 | 10500.00 | 63000.00 | 10750.00 | 64500.00 | 40500.00 | K KUMAR RAJA PROJECTS PVT LIMITED
53.00 | Brick work with common burnt clay F.P.S (non-modular) bricks of class designation 7.5 in foundation and plinth in : Cement mortar 1:4 (1 cement : 4 coarse sand) | 9.00 | Cum | 7343.79 | 7500.00 | 67500.00 | 9500.00 | 85500.00 | 9750.00 | 87750.00 | 67500.00 | K KUMAR RAJA PROJECTS PVT LIMITED
54.00 | Cement concrete flooring 1:2:4 (1 cement: 2 coarse: 4 graded stone aggregate) finished with a floating coat of neat cement, including cement slurry, but excluding the cost of nosing of steps etc. complete. 40 mm thick with 20 mm nominal size stone aggregate. | 31.00 | Sqm | 573.97 | 9000.00 | 279000.00 | 410.00 | 12710.00 | 440.00 | 13640.00 | 12710.00 | Labotek
55.00 | 12 mm cement plaster of mix : 1:6 (1 cement : 6 fine sand) | 217.00 | Sqm | 292.83 | 400.00 | 86800.00 | 260.00 | 56420.00 | 275.00 | 59675.00 | 56420.00 | Labotek
56.00 | 15 mm cement plaster on the rough side of single brick wall of mix ; 1:6 (1 cement : 6 fine sand). | 182.00 | Sqm | 337.29 | 450.00 | 81900.00 | 290.00 | 52780.00 | 310.00 | 56420.00 | 52780.00 | Labotek
57.00 | Neat cement punning. | 67.00 | Sqm | 72.27 | 50.00 | 3350.00 | 213.00 | 14271.00 | 225.00 | 15075.00 | 3350.00 | K KUMAR RAJA PROJECTS PVT LIMITED
58.00 | Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters : 35 mm thick including ISI marked Stainless Steel but hinges with necessary screws. | 8.00 | sqm | 2172.99 | 6000.00 | 48000.00 | 6230.00 | 49840.00 | 6450.00 | 51600.00 | 48000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
59.00 | Providing and fixing aluminium sliding door bolts, ISI marked anodized (anodic coating not less than grade AC 10 as per IS : 1868), transparent or dyed to required colour or shade, with nuts and screws etc. complete : 300 X 16 mm. | 6.00 | Each | 296.17 | 450.00 | 2700.00 | 350.00 | 2100.00 | 380.00 | 2280.00 | 2100.00 | Labotek
60.00 | Providing and fixing aluminium tower bolts, ISI marked, anodized (anodic coating not less than grade AC 10 as per IS:1868) transparent or dyed to required colour or shade, with necessary screws etc. complete : 300 X 10 mm. | 6.00 | Sqm | 134.52 | 400.00 | 2400.00 | 199.00 | 1194.00 | 220.00 | 1320.00 | 1194.00 | Labotek
61.00 | Providing and fixing aluminium handles, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868 ) transparent or dyed to required colour or shade, with necessary screws etc. complete : 125 mm. | 3.00 | Sqm | 68.70 | 300.00 | 900.00 | 150.00 | 450.00 | 180.00 | 540.00 | 450.00 | Labotek
62.00 | Providing and fixing aluminium exruded section body tubular type universal hydraulic door closer (having brand logo with IS :3564, embossed on the body, door weight upto 36 kg to 80 kg and door width from 701 mm to 1000 mm), with double speed adjustment with necessary accessories and screws etc. complete. | 4.00 | Each | 980.82 | 4500.00 | 18000.00 | 2000.00 | 8000.00 | 2500.00 | 10000.00 | 8000.00 | Labotek
63.00 | Providing and fixing aluminium hanging floor door stopper, ISI marked, anodized (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade, with necessary screws etc. complete. Twin rubber stopper. | 3.00 | Each | 71.47 | 3500.00 | 10500.00 | 65.00 | 195.00 | 70.00 | 210.00 | 195.00 | Labotek
64.00 | Distempering with 1st quality acrylic distemper (ready mixed) of approved manufacturer, of required shade and colour complete, as per manufacturer's specification. Two or more coats on new work. | 383.00 | Sqm | 100.37 | 150.00 | 57450.00 | 90.00 | 34470.00 | 95.00 | 36385.00 | 34470.00 | Labotek
65.00 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade : Two or more coats on new work. | 15.00 | Sqm | 139.99 | 150.00 | 2250.00 | 89.00 | 1335.00 | 92.00 | 1380.00 | 1335.00 | Labotek
66.00 | Providing and fixing tiled false celling of specified materials of size 595 X 595 mm in true horizontal level, suspended on inner locking metal grid of hot dipped galvanized steel section (galvanized @ 120 grams/ sqm, both side inclusive) consisting of main "T" runner with suitably spaced joints to get required length and of size 24 X 38 mm made from 0.30 mm thick (minimum) sheet, 1200 mm long spaced between main "T" at 600 mm center to center to form a grid of 1200 X 600 mm and secondary cross "T" of length 600 mm and size 24 X25 mm made of 0.30 mm thick (minimum) sheet to be interlocked at middle of the 1200 X 600 mm panel to form grids of 600 X 600 mm and wall angle of size 24 X 24 X 0.3 mm and laying false ceiling tiles of approved texture in the grid including, required cutting/making, opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc. Main "T" runners to be suspended from ceiling using GI slotted cleats of size 27 X 37 X 25 X 1.6 mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4 mm GI adjustable rods with galvanized butterfly level clips of size 85 X 30 X 0.8 mm spaced at 1200 mm center to center along main T, bottom exposed width of 24 mm of all T-sections shall be pre-painted with polyester paint, all complete for all heights as per specifications, drawings and as directed by Engineer-in-charge. GI Metal Ceiling Lay in plain Tegular edge Global white tiles of size 595 X 595 mm. and 0.5 mm thick with 8 mm drop; made of GI sheet having galvanizing of 100 gms/sqm (both sides inclusive) and electro statically polyester powder coated of thickness 60 microns (minimum), including factory painted after bending. | 122.00 | Sqm | 1349.26 | 1500.00 | 183000.00 | 8050.00 | 982100.00 | 8055.00 | 982710.00 | 183000.00 | K KUMAR RAJA PROJECTS PVT LIMITED
67.00 | Buy Back Item Taking away after dismantling steel work in built up sections in angles, tees, flats and channels including all guest plates, bolts, nuts, cutting rivets, welding etc. including dismembering and stacking within 50 meters lead. | 2500.00 | Kg | -18.00 | 10.00 | -25000.00 | 25.00 | -62500.00 | 36.00 | -90000.00 | -90000.00 | ISSAR INDUSTRIES
| Total in Figures |  |  |  |  | 59633150.00 |  | 69744965.00 |  | 71935015.00
Comparative Chart(eAuction)
Sl.No | Bidder Name | Auction Start Price | Quoted Rate in Figures and Words
|  |  | Bidder Price | Amount in Words
1 | Labotek | 59633150 | 42533150.00 | Four Crore Twenty Five Lakh Thirty Three Thousand One Hundred and Fifty
2 | ISSAR INDUSTRIES | 59633150 | 45033150.00 | Four Crore Fifty Lakh Thirty Three Thousand One Hundred and Fifty
3 | K KUMAR RAJA PROJECTS PVT LIMITED | 59633150 | 59433150.00 | Five Crore Ninty Four Lakh Thirty Three Thousand One Hundred and Fifty
Lowest Amount Quoted BY: Labotek(4.253315E7)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of UPS System and Active Harmonic Filters for the GLF System in CCR hall at NSCBI Airport Tender ID: 2021_AAI_80010_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | K KUMAR RAJA PROJECTS PVT LIMITED | 59633150.00 | L1
| 2 | Labotek | 69744965.00 | L2
| 3 | ISSAR INDUSTRIES | 71935015.00 | L3