## BoQ1
Government eProcurement System Created By: SHALENDERA KUMAR Created Date/Time: 12-Jul-2021 04:53 PM Tender Title: Improvement of Illumination of Apron Area at Imphal Airport. Tender ID: 2021_AAI_80523_1
Tender Inviting Authority: Asstt. General Manager (Engg-E)-II, AAI, Imphal Airport.
Name of Work: Improvement of Illumination of Apron Area at Imphal Airport
Contract No: 2021_AAI_80523_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | RVD INFRA SOLUTION PVT.LTD.(GSTN-24AAGCR7767L1ZQ) |  | jaydeep agency corporation(GSTN-24ACIPP6157B1ZQ) |  | SAHA COMMERCIAL CONSTRUCTION(GSTN-19AASFS6288A1ZN) |  | SHARMA TRADE AGENCY(GSTN-18ABDFM0295M2ZV) |  | D.D.METAL CORPORATION(GSTN-18ACGPD4624F2ZW)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing and Commissioning of 12 Meter, Height, Hot Dip Galvanised High Mast Tower in Double equel section of 4 mm bottom and 3 mm top thick with minimum bottom dia. of 360 mm suitable for wind speed of minimum 180 KM/Hr, with raising lowering system comprising of head frame, luminaries' carriage suitable to install 12 Nos. of LED Luminaries in assymmetrical arrangement, double drum winch, 6 mm diameter SS wire rope, trailing cable of 2 Runs of 5C X 2.5 Sq.mm, connector, integral power tool motor of rating not less than 1 HP, manual handle, junction box, lightening finial of GI Single Spike of suitable length mounting clamps and bolts, foundation bolts manufactured from special steel along with nuts, washers, anchor plate and template including providing and laying power cables (up to a distance of 15 Mtr) between panel and mast of capacity 2 times of total current rating of fittings providing and fixing suitable rated MCB in base compartment, providing foundation with M 20 grade concrete as per size of OEM Design with all materials and labour, providing necessary tools and plants for erection and testing of high mast pole and high mast two coat painted with alluminium pain etc., as required. | 5.00 | Jobs | 100.00 | 156000.00 | 780000.00 | 350000.00 | 1750000.00 | 221000.00 | 1105000.00 | 210000.00 | 1050000.00 | 246000.00 | 1230000.00 | 780000.00 | RVD INFRA SOLUTION PVT.LTD.
2.00 | Fabrication, S.I.T.C of Outdoor MV Feeder Pillar Panel with double door arrangement made out of 3mm thick outer sheet and 2mm thick inner sheet and partition CRCA sheet steel, dust tight, vermin proof, totally enclosed, cubicle type WITH TOP CANOPY FOR RAIN PROTECTION, floor mounting, free standing, suitable for operation at 433 V, 3 phase, 4 wire, 50 Hz, A.C. Power Supply System complete with all accessories, interconnection, connection, earthing, painting, grouting, providing pedastal UPTO THE HEIGHT OF 450 MM, Cable Entry provision etc. as required and comprising of following: 40A FPN MCB as Incomer, 3 Nos. 16 A TPN MCB as Outgoing, Two Timer, 25 A TP Contactor for the automatic switching of Luminaries with Auto/Manual Switching Option, power tool control with 2 Nos. 16A Contactors for raise and lower with push button arrangements, Phase Indication LED Lamps for Incomer, One VAF meter with bus section of 60A in all three phase and nuetral etc., as required. | 7.00 | Jobs | 100.00 | 25200.00 | 176400.00 | 46000.00 | 322000.00 | 49650.00 | 347550.00 | 60000.00 | 420000.00 | 40000.00 | 280000.00 | 176400.00 | RVD INFRA SOLUTION PVT.LTD.
3.00 | Fabrication, S.I.T.C of Outdoor MV Feeder Pillar Panel with double door arrangement made out of 3mm thick outer sheet and 2mm thick inner sheet and partition CRCA sheet steel, dust tight, vermin proof, totally enclosed, cubicle type WITH TOP CANOPY FOR RAIN PROTECTION, floor mounting, free standing, suitable for operation at 433 V, 3 phase, 4 wire, 50 Hz, A.C. Power Supply System complete with all accessories, interconnection, connection, earthing, painting, grouting, providing pedastal UPTO THE HEIGHT OF 450 MM, Cable Entry provision etc. as required and comprising of following: A. Two Nos. of 160 A, 50 KA, 4P MCCBs with Microprocessor Based Releases for OC/SC/EF Protection as INCOMERS with ON/OFF/TRIP Indication Lamps and Phase Indication Lamps, Interlocking Facility with Incomers and Buscouplers as required. B. One No. 160 A, 50 KA, 4P MCCBs as Bus Coupler with ON/OFF Indication Lamps as required. C. Four Nos. of 63 A, 36 KA, 4P MCCB with Thermal Magnetic Releases for Protection as Outgoing, ON/OFF/TRIP Indication Lamps as required. D. One Set of 300 Amps Al. Bus Bars with at Par Neutral BUS BARS as required. E. All accessories such as fuses, auxillary contactors, auxillary switches, etc. including providing Empty Cubicle Space (2 Nos.) as required. ALL AS ABOVE 3 (A) To 3 (E) | 1.00 | Jobs | 100.00 | 84000.00 | 84000.00 | 280000.00 | 280000.00 | 255000.00 | 255000.00 | 140000.00 | 140000.00 | 27000.00 | 27000.00 | 27000.00 | D.D.METAL CORPORATION
4.00 | Supply of LED light fitting with Wattage of maximum 350W with high power LEDs, system efficay not less than 110 lumen/watt, suitable optics for uniform light distribution, integral control driver with minimum 3kV surge suppressor, fitting made up of high pressure die-cast aluminium housing with suitable thermal management arrangement, toughned glass with IP 65 protection, 50,000 burning hours, suitable to operate on single phase AC supply, inline with technical specifications etc., complete as required. | 10.00 | Each | 100.00 | 14400.00 | 144000.00 | 10000.00 | 100000.00 | 12350.00 | 123500.00 | 14000.00 | 140000.00 | 15000.00 | 150000.00 | 100000.00 | jaydeep agency corporation
5.00 | Supply of LED light fitting with Wattage of maximum 300W with high power LEDs, system efficay not less than 110 lumen/watt, suitable optics for uniform light distribution, integral control driver with minimum 3kV surge suppressor, fitting made up of high pressure die-cast aluminium housing with suitable thermal management arrangement, toughned glass with IP 65 protection, 50000 burning hours, suitable to operate on single phase AC supply, inline with technical specifications etc., complete as required. | 10.00 | Each | 100.00 | 12600.00 | 126000.00 | 9000.00 | 90000.00 | 10400.00 | 104000.00 | 15000.00 | 150000.00 | 14000.00 | 140000.00 | 90000.00 | jaydeep agency corporation
6.00 | Supply of LED light fitting with Wattage of maximum 180W with high power LEDs, system efficay not less than 110 lumen/watt, suitable optics for uniform light distribution, integral control driver with minimum 3kV surge suppressor, fitting made up of high pressure die-cast aluminium housing with suitable thermal management arrangement, toughned glass with IP 65 protection, 50000 burning hours, suitable to operate on single phase AC supply, inline with technical specifications etc., complete as required. | 28.00 | Each | 100.00 | 11400.00 | 319200.00 | 6000.00 | 168000.00 | 7000.00 | 196000.00 | 9500.00 | 266000.00 | 8800.00 | 246400.00 | 168000.00 | jaydeep agency corporation
7.00 | Supply of LED Type twin dome red aviation obstruction light fitting suitable for operation on single phase AC power supply etc. as required. | 10.00 | Each | 100.00 | 6000.00 | 60000.00 | 2500.00 | 25000.00 | 7290.00 | 72900.00 | 3300.00 | 33000.00 | 4500.00 | 45000.00 | 25000.00 | jaydeep agency corporation
8.00 | Installation, Testing and Commissioning of LED flood lights and twin dome aviation luminaire up to maximum 350W, suitable for apron flood lighting system and having wide distribution with provision of suitable length 3core x 2.5Sq.mm copper conductor cable for light connection with all accessories suitable for site requirement etc. as required. | 98.00 | Each | 100.00 | 420.00 | 41160.00 | 250.00 | 24500.00 | 400.00 | 39200.00 | 350.00 | 34300.00 | 1500.00 | 147000.00 | 24500.00 | jaydeep agency corporation
9.00 | Supply of 3.5C x 95 Sq.mm, XLPE insulated and PVC sheathed armoured aluminium conductor power cable of 1.1 KV grade conforming to IS 7098 (Part-1) with upto date ammendments etc., complete as required | 180.00 | Mtr | 100.00 | 360.00 | 64800.00 | 450.00 | 81000.00 | 550.00 | 99000.00 | 480.00 | 86400.00 | 500.00 | 90000.00 | 64800.00 | RVD INFRA SOLUTION PVT.LTD.
10.00 | Supply of 4C x 16 Sq.mm, XLPE insulated and PVC sheathed armoured aluminium conductor power cable of 1.1 KV grade conforming to IS 7098 (Part-1) with upto date ammendments etc complete as required | 300.00 | Mtr | 100.00 | 132.00 | 39600.00 | 132.00 | 39600.00 | 160.00 | 48000.00 | 160.00 | 48000.00 | 120.00 | 36000.00 | 36000.00 | D.D.METAL CORPORATION
11.00 | Supply of 6C x 2.5 Sq.mm XLPE insulated and PVC sheathed armoured Copper conductor control cable of 1.1 KV grade conforming to IS 7098 (Part-1) with upto date amendments etc.,complete as required. | 150.00 | Mtr | 100.00 | 420.00 | 63000.00 | 225.00 | 33750.00 | 280.00 | 42000.00 | 270.00 | 40500.00 | 255.00 | 38250.00 | 33750.00 | jaydeep agency corporation
12.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3.5C X 95 Sq.mm (45mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 2.00 | Sets | 100.00 | 360.00 | 720.00 | 350.00 | 700.00 | 550.00 | 1100.00 | 700.00 | 1400.00 | 3700.00 | 7400.00 | 700.00 | jaydeep agency corporation
13.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3.5C X 50 Sq.mm (35mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 1.00 | Sets | 100.00 | 360.00 | 360.00 | 250.00 | 250.00 | 479.00 | 479.00 | 600.00 | 600.00 | 800.00 | 800.00 | 250.00 | jaydeep agency corporation
14.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 4C X 25 Sq.mm (28mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 8.00 | Sets | 100.00 | 300.00 | 2400.00 | 200.00 | 1600.00 | 350.00 | 2800.00 | 500.00 | 4000.00 | 300.00 | 2400.00 | 1600.00 | jaydeep agency corporation
15.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 4C X 16 Sq.mm (28mm) of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 6.00 | Sets | 100.00 | 240.00 | 1440.00 | 200.00 | 1200.00 | 350.00 | 2100.00 | 350.00 | 2100.00 | 300.00 | 1800.00 | 1200.00 | jaydeep agency corporation
16.00 | Supplying and making end termination with brass compression gland and copper lugs for 6C X 2.5 Sq.mm (28mm) of PVC insulated and PVC sheathed / XLPE copper conductor control cable of 1.1 KV grade as required. | 4.00 | Sets | 100.00 | 120.00 | 480.00 | 200.00 | 800.00 | 350.00 | 1400.00 | 350.00 | 1400.00 | 300.00 | 1200.00 | 480.00 | RVD INFRA SOLUTION PVT.LTD.
17.00 | Supplying and laying of 63 mm dia. HDPE, PE63 PN-6 pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984, Part II complete with fitting and cutting, jointing etc. in the existing trench, complete as required. | 130.00 | Mtr | 100.00 | 300.00 | 39000.00 | 180.00 | 23400.00 | 295.00 | 38350.00 | 360.00 | 46800.00 | 350.00 | 45500.00 | 23400.00 | jaydeep agency corporation
18.00 | Supplying and laying of 63 mm dia (OD-63 mm & ID-51 mm nominal) DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. | 120.00 | Mtr | 100.00 | 180.00 | 21600.00 | 195.00 | 23400.00 | 230.00 | 27600.00 | 330.00 | 39600.00 | 550.00 | 66000.00 | 21600.00 | RVD INFRA SOLUTION PVT.LTD.
19.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. in the existing trench, complete as required. | 160.00 | Mtr | 100.00 | 240.00 | 38400.00 | 150.00 | 24000.00 | 140.00 | 22400.00 | 330.00 | 52800.00 | 400.00 | 64000.00 | 22400.00 | SAHA COMMERCIAL CONSTRUCTION
20.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC/HDPE pipe as required. Above 35 sq. mm and upto 95 sq. mm | 90.00 | Mtr | 100.00 | 60.00 | 5400.00 | 30.00 | 2700.00 | 65.00 | 5850.00 | 80.00 | 7200.00 | 170.00 | 15300.00 | 2700.00 | jaydeep agency corporation
21.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC/HDPE pipe as required. Upto 35 sq. mm | 400.00 | Mtr | 100.00 | 36.00 | 14400.00 | 30.00 | 12000.00 | 50.00 | 20000.00 | 70.00 | 28000.00 | 150.00 | 60000.00 | 12000.00 | jaydeep agency corporation
22.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Above 35 sq. mm and upto 95 sq. mm | 30.00 | Mtr | 100.00 | 144.00 | 4320.00 | 30.00 | 900.00 | 50.00 | 1500.00 | 100.00 | 3000.00 | 150.00 | 4500.00 | 900.00 | jaydeep agency corporation
23.00 | sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 35 sq. mm and upto 95 sq. mm | 60.00 | Mtr | 100.00 | 96.00 | 5760.00 | 30.00 | 1800.00 | 35.00 | 2100.00 | 80.00 | 4800.00 | 200.00 | 12000.00 | 1800.00 | jaydeep agency corporation
24.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 16.00 | Each | 100.00 | 4800.00 | 76800.00 | 4950.00 | 79200.00 | 8500.00 | 136000.00 | 5000.00 | 80000.00 | 11000.00 | 176000.00 | 76800.00 | RVD INFRA SOLUTION PVT.LTD.
25.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 80.00 | Mtr | 100.00 | 180.00 | 14400.00 | 250.00 | 20000.00 | 450.00 | 36000.00 | 170.00 | 13600.00 | 550.00 | 44000.00 | 13600.00 | SHARMA TRADE AGENCY
26.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 48.00 | Mtr | 100.00 | 156.00 | 7488.00 | 200.00 | 9600.00 | 125.00 | 6000.00 | 170.00 | 8160.00 | 350.00 | 16800.00 | 6000.00 | SAHA COMMERCIAL CONSTRUCTION
27.00 | Providing, laying and fixing of 60mm dia. G.I. pipe (medium class) in PCC Road complete with G.I. fittings including trenching (50 cm deep) and re-positioning same with PCC etc., as required (Note: Excavation of suitable size PCC Road cutting and laying of pipe in trench and re-positioning same with PCC) | 12.00 | Mtr | 100.00 | 720.00 | 8640.00 | 1000.00 | 12000.00 | 965.00 | 11580.00 | 1000.00 | 12000.00 | 900.00 | 10800.00 | 8640.00 | RVD INFRA SOLUTION PVT.LTD.
28.00 | Provision of MS, C-Type Channel barricading around the mast (Size 100x50x5mm thick) of 1.5mtr x 1.5mtr x 0.60mtr height above ground level (Below ground level grouting depth: 40CM) with one section entry gate, provision vertival sections 8Nos. & Horizantal section 2Nos required and full barricading painted with aviation abstraction colour of white and red strip etc. as required. | 7.00 | Jobs | 100.00 | 30000.00 | 210000.00 | 25000.00 | 175000.00 | 22500.00 | 157500.00 | 40000.00 | 280000.00 | 20000.00 | 140000.00 | 140000.00 | D.D.METAL CORPORATION
29.00 | Dismantling of existing LED Luminaires from existing high mast of height not more than 10 meter handing over to AAI stores etc. as required. | 56.00 | Each | 100.00 | 2400.00 | 134400.00 | 125.00 | 7000.00 | 250.00 | 14000.00 | 100.00 | 5600.00 | 550.00 | 30800.00 | 5600.00 | SHARMA TRADE AGENCY
30.00 | Dismantling of existing 10M High Mast including control panels and dismantling of cable terminals from control panel at apron area, loading, unloading, shifting and handing over to AAI warehouse and demolishing of projected RCC existing foundation and leveling the same with PCC and disposal of material as per direction of Engineer - in - charge. | 4.00 | Jobs | 100.00 | 10000.00 | 40000.00 | 5000.00 | 20000.00 | 12500.00 | 50000.00 | 20000.00 | 80000.00 | 9000.00 | 36000.00 | 20000.00 | jaydeep agency corporation
31.00 | Demolishing cement concrete (PCC/RCC) by manually / mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | 4.00 | Cum | 100.00 | 3600.00 | 14400.00 | 2500.00 | 10000.00 | 3500.00 | 14000.00 | 15000.00 | 60000.00 | 3000.00 | 12000.00 | 10000.00 | jaydeep agency corporation
32.00 | Providing and laying in position cement concrete 1:2:4 (1cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation / road crossing etc., including form work etc as required. | 3.00 | Cum | 100.00 | 6600.00 | 19800.00 | 4500.00 | 13500.00 | 6500.00 | 19500.00 | 4000.00 | 12000.00 | 9000.00 | 27000.00 | 12000.00 | SHARMA TRADE AGENCY
33.00 | Installation, Testing, commissioning of 10 Mtr Bajaj make high mast Systems with all accessories except LED Fittings including following activity complete as required. A. Construction of RCC foundation with 1:2:4 concrete for the high mast based on OEM Design at site with all materials and labour as required. B. Supply of foundation bolts manufactured from special steel along with nuts, washers, anchor plates and templates etc. purchased from OEM C. Supply and laying of power supply trailing cable of ERP insulated PCP sheathed 5CX2.5Sqmm including providing necessary connectors at both end etc. D. Servicing of existing Integral motor powered winch for lowering and raising operation of lantern carriage at inside the base compartment along with mechanical tripping facility and manual handle etc. E. Erection of the 10Meter High Mast with the help of suitable equipments and with all materials and labour etc. as required. ALL AS ABOVE 33 (A) To 33 (E) | 2.00 | Jobs | 100.00 | 65000.00 | 130000.00 | 35000.00 | 70000.00 | 65000.00 | 130000.00 | 120000.00 | 240000.00 | 114500.00 | 229000.00 | 70000.00 | jaydeep agency corporation
34.00 | Dismantling of existing 6M Height GI Poles including control box, light fitting and cable terminals from control box, loading, shifting, unloading, and handing over to AAI warehouse and demolishing of projected PCC/RCC existing foundation and leveling the same with PCC and disposal of material as per direction of Engineer - in - charge. | 75.00 | Jobs | 100.00 | 200.00 | 15000.00 | 500.00 | 37500.00 | 2500.00 | 187500.00 | 1100.00 | 82500.00 | 3500.00 | 262500.00 | 15000.00 | RVD INFRA SOLUTION PVT.LTD.
35.00 | Dismantling, loading & unloading, re-erection, testing and commissioning of 6 Mtr. height octagonal GI Poles with solar operated LED Light fitting with all accessories. including providing necessary foundation as per the direction of Engineering-In-Charge, providing and fixing J Bolts for foundation, painting the foundation etc., as required. | 6.00 | Jobs | 100.00 | 4200.00 | 25200.00 | 5000.00 | 30000.00 | 5000.00 | 30000.00 | 4000.00 | 24000.00 | 12500.00 | 75000.00 | 24000.00 | SHARMA TRADE AGENCY
| Total in Figures |  |  |  |  | 2728568.00 |  | 3490400.00 |  | 3349909.00 |  | 3497760.00 |  | 3770450.00
Lowest Amount Quoted BY: RVD INFRA SOLUTION PVT.LTD.(2728568.00)

## BOQ Summary
BOQ Summary Details Tender Title: Improvement of Illumination of Apron Area at Imphal Airport. Tender ID: 2021_AAI_80523_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | RVD INFRA SOLUTION PVT.LTD. | 2728568.00 | L1
| 2 | SAHA COMMERCIAL CONSTRUCTION | 3349909.00 | L2
| 3 | jaydeep agency corporation | 3490400.00 | L3
| 4 | SHARMA TRADE AGENCY | 3497760.00 | L4
| 5 | D.D.METAL CORPORATION | 3770450.00 | L5