## BoQ1
Government eProcurement System Created By: PADMA P Created Date/Time: 17-Aug-2021 12:00 PM Tender Title: Internal Modification Work of ITB DTB First Floor at Calicut International Airport SH Air conditioning and related Works Tender ID: 2021_AAI_83490_1
Tender Inviting Authority: Asst. General Manager (E-E) - II
Name of Work:Internal Modification Work of ITB / DTB First Floor at Calicut International Airport. SH : Airconditioning and related Works
Ref No: AAI/CL/Engg(E)/NIT -08/21-22/
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Supertech Engineers(GSTN-07AAMPS2459M1ZZ) |  | VOLKS ENERGIE PVT LTD(GSTN-07AADCV9396C1ZZ) |  | Voltas Limited(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying, installing, testing and commissioning of double skin construction AIR HANDLING UNIT of 14000CFM made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with polyurethane foam (PUF) insulation factory injected between them by injection moulding machine. AHUs shall be provided with Lockable push button OFF near AHU. AHU shall be complete with following: a. Supply air centrifugal Backward / forward curved fan for all AHU's with efficiency >75% suitable for static pressure of not less than 40mmwg and Fan outlet velocity not exceeding 10 mps. b. VFD shall be designed for dedicated HVAC applications for supply air fan with built-in PID controller, control panel (keypad & display) , suitable IP enclosure for use on standard. Each VFD panel to be provided with digital display showing electrical parameters like voltage, current, power consumption and shall be independent mounting type.The VFD should have following I/O points AI- 5 , AO- 4 , DI- 6, DO -2 , Vendor configure & programme VFD based on above points. Each VFD Panel shall be provided with a suitable capacity incomer 4 pole MCCB & Terminals for cable Termination etc as required. This starter Panel shall be provided with 2 nos 16 A DP MCB & 1No. 32 - 50 A TPN MCB for VFD etc complete as required for functionig of VFD for AHU. c.Pre filter ( MERV 8 - filter section with 50mm thick metal viscous/ washable synthetic type air prefilters ) in supply air stream. d.Cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) , cooling coil of 6 row deep e.Squirrel cage induction motors suitable for 415 ± 10% volts, 50 Hz, AC supply & high efficiency IE3. f.Fan belt drive package with suitable belt and pulleys g.Vibration isolators. h.Mixing Chamber with return air and fresh air dampers of suitable capacity. i. AHU shall be provided with SS-304 end plates for coil , 150 mm dia. dial type pressure gauges (2 nos.)and industrial type thermometers (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required | 1.00 | Job |  | 380000.00 | 380000.00 | 650000.00 | 650000.00 | 594280.00 | 594280.00 | 380000.00 | Supertech Engineers
2.00 | Supplying, installing, testing and commissioning of horizontal FAN COIL UNITS, blow through type, each complete with 3 rows deep chilled water coil, one or more 3 speed centrifugal fans, cleanable metalic filters, main condensate drain pans, casing, coil piping connections, through copper pipes, condensate drain connections, wiring, control wiring in conduit upto thermostat boxes. All fan coil units shall be suitable for 230 + 6% volts, 50 cycles, single phase power supply. Fan Coil Units shall be of 3TR and 1200CFM refrigeration capacities | 6.00 | Job |  | 36500.00 | 219000.00 | 40000.00 | 240000.00 | 44751.00 | 268506.00 | 219000.00 | Supertech Engineers
3.00 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside / outside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystrene moulded pipe section of density 20 kg/cu.m after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessain and finally applying 0.63mm aluminium sheet cladding complete with type3 , grade 1 roofing feltstrip(as per IS:1322 as amended up to date ) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. 100mm dia.(50mm thick insulation) pipe M.S. 'C' class as per IS : 1239 | 150.00 | Meter |  | 1950.00 | 292500.00 | 1900.00 | 285000.00 | 2890.00 | 433500.00 | 285000.00 | VOLKS ENERGIE PVT LTD
4.00 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside / outside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with fire retardant quality expanded polystrene moulded pipe section of density 20 kg/cu.m after a thick coat of cold setting adhesive (CPRX compound) wrapping with 500g polythene faced hessain and finally applying 0.63mm aluminium sheet cladding complete with type3 , grade 1 roofing feltstrip(as per IS:1322 as amended up to date ) at joints repairing of damage to building etc. as per specifications and as required complete in all respect. 32mm dia.(50mm thick insulation) pipe M.S. 'C' class as per IS : 1239 | 40.00 | Meter |  | 1050.00 | 42000.00 | 800.00 | 32000.00 | 1302.00 | 52080.00 | 32000.00 | VOLKS ENERGIE PVT LTD
5.00 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water piping duly insulated to the same specifications as the connected piping and adequately supported as per specifications. BUTTERFLY VALVE (MANUAL) with C I body SS Disc, Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water circulation as specified 100mm dia | 8.00 | Each |  | 6500.00 | 52000.00 | 4000.00 | 32000.00 | 5586.00 | 44688.00 | 32000.00 | VOLKS ENERGIE PVT LTD
6.00 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water piping duly insulated to the same specifications as the connected piping and adequately supported as per specifications. BUTTERFLY VALVE (MANUAL) with C I body SS Disc, Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water circulation as specified 40mm dia | 12.00 | Job |  | 4500.00 | 54000.00 | 2000.00 | 24000.00 | 3349.00 | 40188.00 | 24000.00 | VOLKS ENERGIE PVT LTD
7.00 | Y - STRAINER of Ductile CI Body flanged ends with stainless steel strainer for chilled / hot water circulation including insulation as specified. 100 mm dia | 2.00 | Each |  | 14500.00 | 29000.00 | 6000.00 | 12000.00 | 10785.00 | 21570.00 | 12000.00 | VOLKS ENERGIE PVT LTD
8.00 | Supply, installation, testing and commissioning of TWO WAY PRESSURE INDEPENDENT DYNAMIC BALANCING CUM CONTROL VALVE suitable for 100mm dia pipelines provided with spring return function & fitted with modulating actuators in chilled water lines at air handling unit. The actuator shall have required shut off capability of minimum 4 bar rating. The valves & actuators for AHU’s shall be provided with thermostat for measuring the return air temperature and operating the actuator as an independent system. Further the valve shall also be compatible with Building Automation System (Siemens Desigo CC) | 1.00 | Each |  | 85000.00 | 85000.00 | 90000.00 | 90000.00 | 113024.00 | 113024.00 | 85000.00 | Supertech Engineers
9.00 | Supply and laying of 40 mm PVC pipe for drain line with required supports etc complete as required | 20.00 | Meter |  | 350.00 | 7000.00 | 295.00 | 5900.00 | 467.00 | 9340.00 | 5900.00 | VOLKS ENERGIE PVT LTD
10.00 | Supplying, laying, fixing, testing and commissioning of 19mm thick closed cell elastrometric nitrile rubber of class 'O' applied by suitable adhesive, as per specifications and as required complete in all respect. | 5.00 | Sqm |  | 950.00 | 4750.00 | 690.00 | 3450.00 | 614.00 | 3070.00 | 3070.00 | Voltas Limited
11.00 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. a) Thickness 1.00 mm sheet | 20.00 | Sqm |  | 1400.00 | 28000.00 | 1092.00 | 21840.00 | 1161.00 | 23220.00 | 21840.00 | VOLKS ENERGIE PVT LTD
12.00 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. b)Thickness 0.80 mm sheet | 300.00 | Sqm |  | 1290.00 | 387000.00 | 943.00 | 282900.00 | 956.00 | 286800.00 | 282900.00 | VOLKS ENERGIE PVT LTD
13.00 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. c) Thickness 0.63 mm sheet | 80.00 | Sqm |  | 1150.00 | 92000.00 | 795.00 | 63600.00 | 836.00 | 66880.00 | 63600.00 | VOLKS ENERGIE PVT LTD
14.00 | Supplying and fixing of 25mm thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber (Class "O") insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50 mm wide and 3mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required. | 400.00 | Sqm |  | 1050.00 | 420000.00 | 1210.00 | 484000.00 | 693.00 | 277200.00 | 277200.00 | Voltas Limited
15.00 | Supply and laying of 10 mm closed cell nitrile rubber acoustic insulation | 320.00 | Sqm |  | 390.00 | 124800.00 | 600.00 | 192000.00 | 740.00 | 236800.00 | 124800.00 | Supertech Engineers
16.00 | Supply and fixing of canvas connections | 1.00 | Each |  | 5000.00 | 5000.00 | 10000.00 | 10000.00 | 3614.00 | 3614.00 | 3614.00 | Voltas Limited
17.00 | Supplying & fixing of powder coated extruded aluminium Supply Air Grills with aluminium volume control dampers as per specifications. | 10.00 | Sqm |  | 11500.00 | 115000.00 | 4000.00 | 40000.00 | 10978.00 | 109780.00 | 40000.00 | VOLKS ENERGIE PVT LTD
18.00 | Supplying & fixing of powder coated extruded aluminium Return Air Grills with louvers but without volume control dampers complete as required. | 10.00 | Sqm |  | 9500.00 | 95000.00 | 3000.00 | 30000.00 | 6544.00 | 65440.00 | 30000.00 | VOLKS ENERGIE PVT LTD
19.00 | Supply, installation, testing and commissioning of GI volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc, as per specifications. | 10.00 | Sqm |  | 9000.00 | 90000.00 | 4000.00 | 40000.00 | 8374.00 | 83740.00 | 40000.00 | VOLKS ENERGIE PVT LTD
20.00 | Supplying, Fixing,testing and commissioning of fire dampers in supply air duct/main branch and return air path as and where required of required sizes i/c control wiring,the damper shall be motorized and spring return so as to close the damper in the event of power failure automatically and open the same in case of power being restored. The spring return action shall be inbuilt mechanism and not externally mounted. The damper shall also be closed in the event of fire signal complete as required and as per specifications a) Fire damper | 2.00 | Sqm |  | 9500.00 | 19000.00 | 5000.00 | 10000.00 | 12156.00 | 24312.00 | 10000.00 | VOLKS ENERGIE PVT LTD
21.00 | Supplying, Fixing,testing and commissioning of fire dampers in supply air duct/main branch and return air path as and where required of required sizes i/c control wiring,the damper shall be motorized and spring return so as to close the damper in the event of power failure automatically and open the same in case of power being restored. The spring return action shall be inbuilt mechanism and not externally mounted. The damper shall also be closed in the event of fire signal complete as required and as per specifications. b)Actuator | 1.00 | Each |  | 12000.00 | 12000.00 | 8500.00 | 8500.00 | 13120.00 | 13120.00 | 8500.00 | VOLKS ENERGIE PVT LTD
22.00 | SITC of UVGI lamps system suitable for continuous operation having UV-C band having wave length of 254+/-1nm and irradiation intensity of average 4016microwatts/sq.cm for germicidal irradiation of the entire AHU cooling coil face area along with all supporting structures, power and control panel, cabling ,earthing ,safety provisions etc as per the detailed technical specifications for AHU details specified here under complete as required. 14000 CFM | 1.00 | Job |  | 120000.00 | 120000.00 | 125000.00 | 125000.00 | 186746.00 | 186746.00 | 120000.00 | Supertech Engineers
23.00 | Supply, Installation, Testing and Commissioning of Stand alone Intelligent 32 bit Microprocessor DDC Controllers (PXC12.D or equivalent) as per the specifications for IO points. The above shall be housed in a vandal proof, lockable & secure MS powder coated Cabinets to be supplied along with the Controllers. | 1.00 | Job |  | 45000.00 | 45000.00 | 46000.00 | 46000.00 | 56546.00 | 56546.00 | 45000.00 | Supertech Engineers
24.00 | Integration of the DDC controller including sensors into the existing BMS system (Make : Siemens Model : Desigo CC) | 1.00 | Job |  | 65000.00 | 65000.00 | 70000.00 | 70000.00 | 14307.00 | 14307.00 | 14307.00 | Voltas Limited
25.00 | Supply, Installation, Testing and Commissioning of Differential pressure switches across the blowers for indicating blower status. Pressure differential – 10mmWG – 125 mmWG. The switch shall be with connecting tube and metal bends for connections to the duct. The housing shall be IP 54 rated. The contact shall be SPDT type with 230 VAC, 1 A rating | 1.00 | Job |  | 8300.00 | 8300.00 | 1950.00 | 1950.00 | 4837.00 | 4837.00 | 1950.00 | VOLKS ENERGIE PVT LTD
26.00 | Supply, Installation, Testing and Commissioning of Differential pressure switches across the Air Handling Unit filters, for indicating the filter status. Pressure differential – 2 mmWG to 15 mm WG. The switch shall be with connecting tube and metal bends for connections to the duct. The housing shall be IP 54 rated. The contact shall be SPDT type with 230 VAC, 1 A rating as per specification. | 1.00 | Job |  | 8300.00 | 8300.00 | 1950.00 | 1950.00 | 4837.00 | 4837.00 | 1950.00 | VOLKS ENERGIE PVT LTD
27.00 | Supply, Installation, Testing and Commissioning of Duct Temperature Sensor shall be with rigid stem and of averaging type. These shall be suitable for duct installation (Range - 0-100o F) and accuracy shall be ± 0.36 degrees F. | 1.00 | Job |  | 8500.00 | 8500.00 | 2450.00 | 2450.00 | 4927.00 | 4927.00 | 2450.00 | VOLKS ENERGIE PVT LTD
28.00 | SITC of 2.0 Ton split type 5 star AC (EER 3.35 min) consisting of single room unit (evaporator unit) comprising copper coil with cordless remote control, suitable stabilizer unit and one number outdoor condensing unit comprising of sealed suitable type compressor and Copper coil condenser suitable for operation on 230V, 50Hz. AC supply and non CFC refrigerant like R-410A or equivalent capable of performing (a) cooling (b) de-humidifying (c) Air-Circulating (d) filtering including fixing the outdoor condenser unit on a raised suitable pedestals duly painted/Metal Stand as per site requirement (Pedestals/Metal Stand included in the scope) and fixing of Evaporator unit including providing and making inter connections between evaporator unit and condensing unit up to a length of 5 mtrs. comprising of the following including first charge of refrigerant, complete as required. a) Suitable drain pipe of PVC or as per OEM specification for length upto 10 Metre b) Suitable insulated copper pipe for liquid line or as per OEM specification for length upto 5 Metre c) Suitable copper pipe for suction or as per OEM specification for length upto 5 Metre d) Suitable FR insulated, PVC sheathed unarmoured multi strand copper cable or as per OEM specification for length upto 5 Metre e) Supply and Fixing of Heavy duty Rigid type PVC pipe / PVC Trunking of suitable size for covering in the liquid line, suction line and multi strand copper cable or as per OEM specification for length upto 5 Metre | 3.00 | Each |  | 52500.00 | 157500.00 | 50000.00 | 150000.00 | 47590.00 | 142770.00 | 142770.00 | Voltas Limited
29.00 | Supply and fixing of following for interconnections between evaporator unit and condensing unit mentioned in item No 28 (extra length if required) complete as required a)Suitable drain pipe for heavy duty PVC pipe or as per OEM specification for the item No 28 b) Suitable insulated copper pipe for liquid line or as per OEM specification for the item No 28 c) Suitable insulated copper pipe for suction or as per OEM specification for the item No 28 d) Suitable FR insulated, PVC sheathed unarmored multi strand copper cable or as per OEM specification for the item No 28 e) Supply and Fixing of Heavy duty Rigid type PVC Pipe/Plastic Trunking of suitable size for covering in the refrigerant drain line, liquid line, suction line and multi strand copper cable as required for the item No 28 | 30.00 | Meter |  | 1550.00 | 46500.00 | 800.00 | 24000.00 | 1566.00 | 46980.00 | 24000.00 | VOLKS ENERGIE PVT LTD
| Total in Figures |  |  |  |  | 3012150.00 |  | 2978540.00 |  | 3233102.00
Lowest Amount Quoted BY: VOLKS ENERGIE PVT LTD(2978540.00)

## BOQ Summary
BOQ Summary Details Tender Title: Internal Modification Work of ITB DTB First Floor at Calicut International Airport SH Air conditioning and related Works Tender ID: 2021_AAI_83490_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | VOLKS ENERGIE PVT LTD | 2978540.00 | L1
| 2 | Supertech Engineers | 3012150.00 | L2
| 3 | Voltas Limited | 3233102.00 | L3