## BoQ1
Government eProcurement System Created By: SABYASACHI MUKHERJEE Created Date/Time: 15-Nov-2021 04:45 PM Tender Title: SITC of 75 KLD Sewage Treatment Plant (STP) based on MBR Treatment Water Treatment Plant (WTP) and Submersible Pump at Kolkata Airport. Tender ID: 2021_AAI_84760_1
Tender Inviting Authority: Airports Authority of India
Name of Work: Construction of 03 Hangers for C category Aircrafts connecting apron and taxi link ( Narayanpur side) at NSCBI Airport Kolkata. SH: SITC of 75 KLD Sewage Treatment Plant (STP) based on MBR Treatment, Water Treatment Plant (WTP) & Submersible Pump at Kolkata Airport.
Contract No: 2021_AAI_84760_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SAWEN CONSULTANCY SERVICES PVT. LTD.(GSTN-09AAQCS9226F1ZU) |  | UY TRIENVIRO PVT. LTD.(GSTN-09AADCC7268G1ZF) |  | POLLUCON TECHNOLOGIES LIMITED(GSTN-09AACCP1008J1ZM) |  | HITECH SWEET WATER TECH PVT LTD(GSTN-07AAACH7432C1ZZ) |  | Trans Organics (India) Pvt. Ltd(GSTN-19AACCT1827B1ZN) |  | MECO TECHNOLOGIES PVT LTD(GSTN-22AAICM0881G1ZN) |  | ENSYS TECHNOLOGIES (I) PVT LTD(GSTN-33AAACE2532J1Z1) |  | ENHANCE ECOTECH SOLUTION PVT LTD(GSTN-06AADCE9126D1ZW) |  | Sainath Envirotech(GSTN-33ALGPK3290B1ZJ) |  | HITECH ENVIRO ENGINEERS AND CONSULTANTS PVT LTD(GSTN-09AADCH3746E1ZN) |  | Rysa Infratech Private Limited(GSTN-NA) |  | QUALICOM SOLUTIONS PRIVATE LIMITED(GSTN-NA) |  | LANDMARK AQUATEC PRIVATE LIMITED(GSTN-NA) |  | B S ENVIRO N INFRACON PVT LTD(GSTN-NA) |  | WTE INFRA PROJECTS PVT LTD(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I PUMP ROOM
1.01 | Design, Supplying, installing, testing & commissioning of on Membrane Bio Reactor (MBR) Sewage Treatment Plant of 75 KLD in one module of 75 kld capacity (excluding Civil construction work) for the following duty Sewage treatment plant shall include the following items Screen chambers with SS Screen as per the technical specification. Equalization Tank in RCC Aerobic tank in MSFRP (Inside coating) Anoxic tank in MSFRP (Inside coating) MBR TANK in MSFRP (Inside Coating) Sludge Holding tank in MSFRP ( Inside Coating) Air Blowers (Seperate sets for MBR & Aeration, EQT & SHT)) Submerged MBR Membranes Recirculation pumps, backpulse pump, permeate pump etc. Chemical Cleaning System Air Compressors if necessary CIP System Electrical Panel, Cabling (Power & Control), Earthing Clear Water tank and Soft Water tank in MSFRP (Inside Coating)
1.02 | Quoted rate should include Approval from pollution board at initial & various other stages of works including preparation of report/ drawings as per pollution board requirement, arrangement of raw sewage for testing & commissioning. Contractor shall include the cost of all chemicals (consumed during testing & commissioning and the cost of such items of works which are not explicitly mentioned above, but are mendatory to have pollution board approval. INLET EFFLUENT CHARACTERSTICS PH : 6.5 - 8.5 BOD 5 : 350 mg/l S. Solids : 300 mg/l COD : 600 mg/l Oil & grease : 50 mg/l N-Total : 50 PPM Effluent discharge standard after treatment: Conforming to requirement approved standards PH : 6.5 - 8.5 BOD 5 : < 10 mg/l S. Solids : < 5 mg/l COD : < 20 mg/l Oil & grease : Below detectable Limit. NH4-N : < 5 PPM N-Total : < 10 PPM Turbidity : < 5 NTU Note:-Contractor shall ensure submission of detailed GA drawings (Plan & Section), P&I diagram, schematic diagram for the above said component and additional component if so required for the complete working of the STP for the full capacity.
1.03 | (i) Supply, installation, testing & commissioning MSFRP Tanks as mentioned above of 5 mm thick MS plate & 2 mm thick FRP Coating (Inside) | 1.00 | Job |  | 3700000.00 | 3700000.00 | 1963000.00 | 1963000.00 | 3500000.00 | 3500000.00 | 2300000.00 | 2300000.00 | 6500000.00 | 6500000.00 | 1500000.00 | 1500000.00 | 4035830.00 | 4035830.00 | 1102137.00 | 1102137.00 | 3000000.00 | 3000000.00 | 2000000.00 | 2000000.00 | 1700000.00 | 1700000.00 | 1328761.00 | 1328761.00 | 500000.00 | 500000.00 | 2100000.00 | 2100000.00 | 6000000.00 | 6000000.00 | 500000.00 | LANDMARK AQUATEC PRIVATE LIMITED
2.00 | Supply, installation, testing & commissioning of Stainless Steel Perforated, Corrugated Bar Screen with suitable lifting arrangement of following mesh sizes:
2.01 | (i) Coarse Screen - 10 mm mesh size | 1.00 | Job |  | 12000.00 | 12000.00 | 45000.00 | 45000.00 | 40000.00 | 40000.00 | 10000.00 | 10000.00 | 15000.00 | 15000.00 | 150000.00 | 150000.00 | 28750.00 | 28750.00 | 18229.00 | 18229.00 | 100000.00 | 100000.00 | 15000.00 | 15000.00 | 10000.00 | 10000.00 | 14667.00 | 14667.00 | 10000.00 | 10000.00 | 11000.00 | 11000.00 | 500000.00 | 500000.00 | 10000.00 | LANDMARK AQUATEC PRIVATE LIMITED, HITECH SWEET WATER TECH PVT LTD, Rysa Infratech Private Limited
2.02 | (ii) Screen - 5 mm punched hole | 1.00 | Job |  | 12000.00 | 12000.00 | 33000.00 | 33000.00 | 40000.00 | 40000.00 | 15000.00 | 15000.00 | 15000.00 | 15000.00 | 60000.00 | 60000.00 | 34650.00 | 34650.00 | 13021.00 | 13021.00 | 100000.00 | 100000.00 | 20000.00 | 20000.00 | 12000.00 | 12000.00 | 14667.00 | 14667.00 | 8000.00 | 8000.00 | 13000.00 | 13000.00 | 500000.00 | 500000.00 | 8000.00 | LANDMARK AQUATEC PRIVATE LIMITED
2.03 | (iii) Automatic Fine Screen (Rotary Drum Type) with Self Cleaning Backpulse arrangement - MOC: SS 304, Flow Rate: As per Vendor , Provision for Overflow & Drain. With Greated Motor - 15 to 20 RPM & required torque for continuous operation. | 1.00 | Job |  | 75000.00 | 75000.00 | 780000.00 | 780000.00 | 400000.00 | 400000.00 | 110000.00 | 110000.00 | 650000.00 | 650000.00 | 800000.00 | 800000.00 | 397500.00 | 397500.00 | 156249.00 | 156249.00 | 700000.00 | 700000.00 | 450000.00 | 450000.00 | 230000.00 | 230000.00 | 540000.00 | 540000.00 | 250000.00 | 250000.00 | 260000.00 | 260000.00 | 500000.00 | 500000.00 | 75000.00 | SAWEN CONSULTANCY SERVICES PVT. LTD.
3.00 | Supply,Installation,Testing and Commissioning of automatic belt type oil skimmer SS for grease trap of suitable size of minimum1200mm liquid depth in brick work of class 75 with cement mortar (1:6), inside plastering 16 mm thick with cement mortar 1:3 with floating coat of neat cement and rough plaster on outside. Including SS bucket to collect the grease. (suitable of 75 KLD flow) | 1.00 | No |  | 60000.00 | 60000.00 | 78000.00 | 78000.00 | 100000.00 | 100000.00 | 55000.00 | 55000.00 | 450000.00 | 450000.00 | 230000.00 | 230000.00 | 215420.00 | 215420.00 | 41667.00 | 41667.00 | 100000.00 | 100000.00 | 110000.00 | 110000.00 | 30000.00 | 30000.00 | 62667.00 | 62667.00 | 65000.00 | 65000.00 | 78000.00 | 78000.00 | 100000.00 | 100000.00 | 30000.00 | Rysa Infratech Private Limited
4.00 | Supply,Installation,Testing and Commissioning of MS hot dip galvanized puddle flanges in accordance to BS:10 table D as required to be provided (in the structural slab and wall) of various diameters. Puddle flanges shall be provided for all the structural component of the STP. For the installation of the puddle flanges vendor to depute the engineer to the same at the required levels & position. | 1.00 | Lot |  | 50000.00 | 50000.00 | 65000.00 | 65000.00 | 20000.00 | 20000.00 | 28000.00 | 28000.00 | 35000.00 | 35000.00 | 250000.00 | 250000.00 | 32210.00 | 32210.00 | 26042.00 | 26042.00 | 100000.00 | 100000.00 | 100000.00 | 100000.00 | 10000.00 | 10000.00 | 40533.00 | 40533.00 | 25000.00 | 25000.00 | 58000.00 | 58000.00 | 500000.00 | 500000.00 | 10000.00 | Rysa Infratech Private Limited
5.00 | Supply,Installation,Testing and Commissioning of plastic manhole step / foot rest (@ 300 mm c/c) with polypropelene compound injection molded around 16 mm dia (Fe-415) steel reinforcing bar. Provision of the foot rest is envisaged in all the tanks/ components of the STP for the purpose of accessability. The installation of the foot rest shall be done by the civil contractor as per civil GA drawing | 1.00 | Lot |  | 30000.00 | 30000.00 | 78000.00 | 78000.00 | 15000.00 | 15000.00 | 20000.00 | 20000.00 | 12000.00 | 12000.00 | 230000.00 | 230000.00 | 19850.00 | 19850.00 | 15625.00 | 15625.00 | 50000.00 | 50000.00 | 40000.00 | 40000.00 | 10000.00 | 10000.00 | 133333.00 | 133333.00 | 30000.00 | 30000.00 | 39000.00 | 39000.00 | 500000.00 | 500000.00 | 10000.00 | Rysa Infratech Private Limited
6.00 | Supply, installation, testing & commissioning of double seal CI medium duty rectangular manhole cover with frame for the feasibility of access in the tank with locking arrangement. Size : 600 x 900x 10 mm thick (Approximate 45 Kg weight) | 1.00 | Lot |  | 150000.00 | 150000.00 | 58500.00 | 58500.00 | 10000.00 | 10000.00 | 20000.00 | 20000.00 | 7000.00 | 7000.00 | 120000.00 | 120000.00 | 23450.00 | 23450.00 | 20834.00 | 20834.00 | 50000.00 | 50000.00 | 100000.00 | 100000.00 | 10000.00 | 10000.00 | 18000.00 | 18000.00 | 40000.00 | 40000.00 | 26000.00 | 26000.00 | 500000.00 | 500000.00 | 7000.00 | Trans Organics (India) Pvt. Ltd
7.00 | Supply, installation, testing & commissioning of non clogging type pumps having CI casing & SS impeller complete with all accessories, motor of required capacity including pressure gauge on delivery line with isolation cock, isolation valve, check valve, flow meter, level switch, level controller (with wiring) to control the level of sump automatically. Pumps shall have following duty Submersible Sewage Pumps for transfer of Effluent from EQT to Anoxic Tank (1 working + 1 Standby) Flow rate (each) - 3.75 cubic meter /Hr Head (Mtr) - 15 m (Solid handling size for this pump shall be 30 to 50 mm). Provision of guide ropes to guide submersible pump from upper level to operational level in sump basin with channels / angle section of MSEP shall be made by the STP contractor | 2.00 | No |  | 65000.00 | 130000.00 | 65000.00 | 130000.00 | 120000.00 | 240000.00 | 25000.00 | 50000.00 | 85000.00 | 170000.00 | 300000.00 | 600000.00 | 173650.00 | 347300.00 | 23438.00 | 46876.00 | 50000.00 | 100000.00 | 80000.00 | 160000.00 | 45000.00 | 90000.00 | 76000.00 | 152000.00 | 20000.00 | 40000.00 | 57500.00 | 115000.00 | 200000.00 | 400000.00 | 40000.00 | LANDMARK AQUATEC PRIVATE LIMITED
7.01 | Submersible Agitator / Mixer for Anoxic Tank with suitable RPM in SS / PP MOC each suitable of one module of 75 KLD. | 1.00 | No |  | 45000.00 | 45000.00 | 195000.00 | 195000.00 | 200000.00 | 200000.00 | 20000.00 | 20000.00 | 75000.00 | 75000.00 | 270000.00 | 270000.00 | 132460.00 | 132460.00 | 40365.00 | 40365.00 | 300000.00 | 300000.00 | 115000.00 | 115000.00 | 80000.00 | 80000.00 | 120000.00 | 120000.00 | 25000.00 | 25000.00 | 39000.00 | 39000.00 | 200000.00 | 200000.00 | 20000.00 | HITECH SWEET WATER TECH PVT LTD
8.00 | Air diffusion system shall include the following Twin type rotary air blowers capable of delivering required amount of free air at required pressure driven through “V” belt or directly coupled through flexible coupling to a TEFC motor of suitable HP Suitable for 415 ± 10% volts, 3 phase, 50 cycles A/C supply. The cost shall be inclusive of pressure safety valves, pressure guage with isolation valve, discharge check valves, discharge isolation valves, drain valves and all other associated piping, valves complete with motor, base-plate, inlet filter, intake silencer and off-load starting system outlet silencer,anti-vibration damper, flexible coupling, filter restriction indicator, non-return valve, pressure relief valve, V-belt system or direct drive coupling. The casing rotor shall be of cast iron construction. Bearings and gears shall be grease lubricated. Motor speed shall be not less than 1500 rpm.The size and performance of the air blower shall be so selected that it can provide a minimum air flow rate 0.4 l /sec / diffuser to 1l/sec/diffuser maximum, and to maintain a minimum of 2.0mg/liters dissolved oxygen in the aeration tanks in operation.The air blowers shall be of following capacities.
8.01 | (i) For MBR (1 Working + 1 Standby) Capacity : As per Membrane Manufacturer | 2.00 | No |  | 90000.00 | 180000.00 | 97500.00 | 195000.00 | 250000.00 | 500000.00 | 50000.00 | 100000.00 | 325000.00 | 650000.00 | 480000.00 | 960000.00 | 257650.00 | 515300.00 | 58594.00 | 117188.00 | 100000.00 | 200000.00 | 120000.00 | 240000.00 | 100000.00 | 200000.00 | 106893.00 | 213786.00 | 60000.00 | 120000.00 | 98000.00 | 196000.00 | 400000.00 | 800000.00 | 100000.00 | HITECH SWEET WATER TECH PVT LTD
8.02 | (ii) Root blower for Equalisation tank, Aeration tank & Sludge holding tank ( 1 working +1 stand by) Capacity : 90 cubic meter/hr @ 5000 mm WC ( Minimum) | 2.00 | No |  | 90000.00 | 180000.00 | 130000.00 | 260000.00 | 200000.00 | 400000.00 | 40000.00 | 80000.00 | 310000.00 | 620000.00 | 480000.00 | 960000.00 | 278740.00 | 557480.00 | 58594.00 | 117188.00 | 200000.00 | 400000.00 | 150000.00 | 300000.00 | 100000.00 | 200000.00 | 100227.00 | 200454.00 | 60000.00 | 120000.00 | 98000.00 | 196000.00 | 400000.00 | 800000.00 | 80000.00 | HITECH SWEET WATER TECH PVT LTD
9.00 | Air diffusers for Equalization, Sludge holding and aeration Tank Air diffusers shall be made to provide a uniform distribution of fine bubble air release performance in the system. The air diffuser shall be either made of elastomic rubbervmembrane or composed of crystalline fused aluminium oxide with a suitable ceramic bonding material. Diffuser shall be of self-cleaning, non-clog disc or dome-shaped type. Oxygen transfer efficiency shall not be less than 20% at 3.5m submergence in clear water. Alternatives may be offered for consideration. Diffuser hold down assemblies shall consist of a retainer bolt, a matching washer and gasket. Sealing gasket shall be composed of solid neoprene rubber and shall be conform to ASTM D-2000 and shall be suitable for withstanding the effects of wastewater high temperature up to 120 degree C.The Contractor shall submit calculation to justify the diffuser selection and air requirement during the detailed design.
9.01 | (i) Diffuser complete with hold down assemblies for equity tank | 1.00 | Lot |  | 35000.00 | 35000.00 | 13000.00 | 13000.00 | 150000.00 | 150000.00 | 12000.00 | 12000.00 | 150000.00 | 150000.00 | 300000.00 | 300000.00 | 87500.00 | 87500.00 | 5209.00 | 5209.00 | 100000.00 | 100000.00 | 85000.00 | 85000.00 | 20000.00 | 20000.00 | 5734.00 | 5734.00 | 8000.00 | 8000.00 | 2600.00 | 2600.00 | 100000.00 | 100000.00 | 2600.00 | B S ENVIRO N INFRACON PVT LTD
9.02 | (ii) Diffuser complete with hold down assemblies for sludge holding tank | 1.00 | Lot |  | 35000.00 | 35000.00 | 13000.00 | 13000.00 | 100000.00 | 100000.00 | 5500.00 | 5500.00 | 50000.00 | 50000.00 | 210000.00 | 210000.00 | 74620.00 | 74620.00 | 5209.00 | 5209.00 | 100000.00 | 100000.00 | 40000.00 | 40000.00 | 60000.00 | 60000.00 | 5734.00 | 5734.00 | 8000.00 | 8000.00 | 2600.00 | 2600.00 | 100000.00 | 100000.00 | 2600.00 | B S ENVIRO N INFRACON PVT LTD
9.03 | (iii) Diffuser complete with hold down assemblies for aeration tank | 1.00 | Lot |  | 60000.00 | 60000.00 | 13000.00 | 13000.00 | 200000.00 | 200000.00 | 15000.00 | 15000.00 | 250000.00 | 250000.00 | 280000.00 | 280000.00 | 134550.00 | 134550.00 | 26042.00 | 26042.00 | 300000.00 | 300000.00 | 150000.00 | 150000.00 | 40000.00 | 40000.00 | 19333.00 | 19333.00 | 5000.00 | 5000.00 | 24000.00 | 24000.00 | 100000.00 | 100000.00 | 5000.00 | LANDMARK AQUATEC PRIVATE LIMITED
10.00 | Air piping shall comprise of pipes droppers/ laterals with MS epoxy (non submerged) / SS 304 (submerged) Header complete with all fittings such as tees, crosses, plugs, sockets, elbows, reducers, supports & clamps, puddle flanges etc cutting chases & making good. Contactor to submit detailed P & I indicating their proposal. | 1.00 | Lot |  | 175000.00 | 175000.00 | 156000.00 | 156000.00 | 300000.00 | 300000.00 | 50000.00 | 50000.00 | 150000.00 | 150000.00 | 210000.00 | 210000.00 | 287650.00 | 287650.00 | 65104.00 | 65104.00 | 500000.00 | 500000.00 | 250000.00 | 250000.00 | 12000.00 | 12000.00 | 66667.00 | 66667.00 | 10000.00 | 10000.00 | 75000.00 | 75000.00 | 500000.00 | 500000.00 | 10000.00 | LANDMARK AQUATEC PRIVATE LIMITED
11.00 | Providing and fixing all piping (as described below) and isolation control valves for making the system complete.All pump should have strainer,suction valve ,discharge valve and NRV. SS 304 : Submerged air piping MS Epoxy : Air piping & pumped effluent riser (non submerged) PVC piping : Pumped effluent (submerged) & tank overflow pipe line GI (Heavy) : Interconnecting pipe line after delivery header of pump/ filter | 1.00 | Job |  | 125000.00 | 125000.00 | 130000.00 | 130000.00 | 200000.00 | 200000.00 | 50000.00 | 50000.00 | 150000.00 | 150000.00 | 1200000.00 | 1200000.00 | 214650.00 | 214650.00 | 260414.00 | 260414.00 | 500000.00 | 500000.00 | 210000.00 | 210000.00 | 50000.00 | 50000.00 | 93333.00 | 93333.00 | 50000.00 | 50000.00 | 205000.00 | 205000.00 | 200000.00 | 200000.00 | 50000.00 | LANDMARK AQUATEC PRIVATE LIMITED, HITECH SWEET WATER TECH PVT LTD, Rysa Infratech Private Limited
12.00 | Supplying, installing, testing & commissioning of semiautomatic hydraulic filter press along with screw pump (1 working +1 stand by), pressure gauge with isolation cock, Isolation valve. Capacity : 1 m3 / hr. Discharge Head : 60 m RPM : 1500 | 1.00 | No |  | 100000.00 | 100000.00 | 130000.00 | 130000.00 | 550000.00 | 550000.00 | 65000.00 | 65000.00 | 550000.00 | 550000.00 | 610000.00 | 610000.00 | 321650.00 | 321650.00 | 156249.00 | 156249.00 | 400000.00 | 400000.00 | 330000.00 | 330000.00 | 340000.00 | 340000.00 | 319333.00 | 319333.00 | 70000.00 | 70000.00 | 260000.00 | 260000.00 | 300000.00 | 300000.00 | 65000.00 | HITECH SWEET WATER TECH PVT LTD
13.00 | Supply, installation, testing & commissioning of sludge re circulation pump. Each shall be of non-submersible type centrifugal pump with suction grid and automatic discharge connection. Pump casing and impeller shall be of cast iron material. Shaft shall be of CS material.( 1 working +1 standby) Capacity : 20 cubic meter/hr @ 10 mtr (1 working + 1 standby) | 2.00 | No |  | 35000.00 | 70000.00 | 65000.00 | 130000.00 | 120000.00 | 240000.00 | 20000.00 | 40000.00 | 85000.00 | 170000.00 | 200000.00 | 400000.00 | 98960.00 | 197920.00 | 22787.00 | 45574.00 | 50000.00 | 100000.00 | 65000.00 | 130000.00 | 39000.00 | 78000.00 | 42340.00 | 84680.00 | 30000.00 | 60000.00 | 73000.00 | 146000.00 | 75000.00 | 150000.00 | 40000.00 | HITECH SWEET WATER TECH PVT LTD
14.00 | Supply, installation, testing & commissioning of Chemical Cleaning system comprising Chemical Cleaning tank filled with Sodium Hypochlorite solution in required proportion and centrifugal pump. The system shall be comprising of following in addition to isolation valves, check valves, level switches and and other associated piping, valves and items as per approved P&I. Tank Capacity : As per Membrane Manufacturer Pump capacity : As per Membrane Manufacturer Head : As per Membrane Manufacturer | 1.00 | Set |  | 55000.00 | 55000.00 | 130000.00 | 130000.00 | 100000.00 | 100000.00 | 14000.00 | 14000.00 | 550000.00 | 550000.00 | 170000.00 | 170000.00 | 378550.00 | 378550.00 | 32552.00 | 32552.00 | 300000.00 | 300000.00 | 40000.00 | 40000.00 | 19000.00 | 19000.00 | 46933.00 | 46933.00 | 5000.00 | 5000.00 | 45000.00 | 45000.00 | 50000.00 | 50000.00 | 5000.00 | LANDMARK AQUATEC PRIVATE LIMITED
15.00 | Supply, installation, testing and comissioning of membrane modules consisting of hollow fibre membranes housed in SS 304 housing with SS 304 permeate water manifold and aeration diffuser system capable of delivering the required flow of 75 KLD of effluent through the module. The cost shall be inclusive of cyclic air valve, level transmitter of membrane tank, isolation valves, pressure transmitter and other associated piping, valves and items as per approved P&I. The flux shall be max 25 LMH Membranes shall be physically strong enough to withstand the operating conditions associated with continuous operation in an aerated tank of mixed liquor at concentrations of up to 10,000 mg/L. If required, membranes shall be capable of regular backwashing with and without cleaning chemicals to minimize pore fouling. Max 25 LMH flux shall be considered to arrive at total membrane area required to treat specified waste water quantity. The minimum membrane warranty for life of membranes should be for minimum 5 years The membrane rack / cassette shall include connection points for agitation air and permeate water. All metallic components of each membrane rack/cassette shall be manufactured from stainless steel with a minimum grade of at least Type SS 316. It shall be possible to isolate and remove each membrane rack / cassette from the manifold header pipework while the system is in operation. Permeate System: All the racks/cassettes in each membrane tank shall be connected to a common header which discharges the permeate by pumping. Back pulse pumps, if required, shall also be provided. Clean-In-Place System: The membranes shall be cleaned “in-place” without removal from the membrane tank. The system shall consist of a chemical feed pump (if required) and storage tank (if required) and include all interior piping, valving, and in-tank piping and supports. Maintenance Cleaning: The “maintenance clean” system must be fully automated. This type of cleaning shall not be performed more than once a week and shall not require each MBR tank to be taken out of service for more than 30 minutes. Recovery Cleaning (if required): The “recovery clean” system shall be either fully automated or partially automated with only limited operator’s attention needed. This type of cleaning shall not be performed more than two times a year. Neutralization system, if required, must be included to handle the soak solution after the cleaning process. The cleaning period shall not require each MBR tank to be taken out of service for more than 12 hours. | 1.00 | Set |  | 1000000.00 | 1000000.00 | 1300000.00 | 1300000.00 | 1800000.00 | 1800000.00 | 1150000.00 | 1150000.00 | 1500000.00 | 1500000.00 | 1210000.00 | 1210000.00 | 2798640.00 | 2798640.00 | 1041656.00 | 1041656.00 | 1500000.00 | 1500000.00 | 1000000.00 | 1000000.00 | 2350000.00 | 2350000.00 | 1798827.00 | 1798827.00 | 400000.00 | 400000.00 | 1350000.00 | 1350000.00 | 2700000.00 | 2700000.00 | 400000.00 | LANDMARK AQUATEC PRIVATE LIMITED
16.00 | Supply, installation, testing & commissioning of Chemical Cleaning system comprising Chemical Cleaning tank filled with Citric Acid solution in required proportion and centrifugal pump. The system shall be comprising of following in addition to isolation valves, check valves, level switches and and other associated piping, valves and items as per approved P&I. Tank Capacity : As per Membrane Manufacturer Pump capacity : As per Membrane Manufacturer Head : As per Membrane Manufacturer | 1.00 | Set |  | 250000.00 | 250000.00 | 130000.00 | 130000.00 | 100000.00 | 100000.00 | 14000.00 | 14000.00 | 125000.00 | 125000.00 | 130000.00 | 130000.00 | 378550.00 | 378550.00 | 32552.00 | 32552.00 | 300000.00 | 300000.00 | 65000.00 | 65000.00 | 19000.00 | 19000.00 | 46933.00 | 46933.00 | 5000.00 | 5000.00 | 45000.00 | 45000.00 | 50000.00 | 50000.00 | 5000.00 | LANDMARK AQUATEC PRIVATE LIMITED
17.00 | Supply, installation, testing & commissioning of the PLC based compartmentalized control panel of 14 gauge CRCA sheet steel, powder coated with interlocking arrangement with supply pumps, suction pumps, chemical cleaning tank, modulating or shut-off valves including necessary wiring, RS 485 communication port, magnetic switches & sensors complete to make the system functional with following interlocking Suction pump stop Suction pump`s head loss greater then set suction head Supply pump stop Suction pump stop & Chemical cleaning pump start Suction pump`s head loss greater then set suction head Suction pump`s suction header valve stop Suction pump`s head loss greater then set suction head Chemical pumps delivery valve open in suction pump`s suction header | 1.00 | Lot |  | 500000.00 | 500000.00 | 195000.00 | 195000.00 | 350000.00 | 350000.00 | 150000.00 | 150000.00 | 450000.00 | 450000.00 | 1180000.00 | 1180000.00 | 1098740.00 | 1098740.00 | 130207.00 | 130207.00 | 400000.00 | 400000.00 | 610000.00 | 610000.00 | 70000.00 | 70000.00 | 166000.00 | 166000.00 | 100000.00 | 100000.00 | 195000.00 | 195000.00 | 1800000.00 | 1800000.00 | 70000.00 | Rysa Infratech Private Limited
18.00 | Supplying, installing, testing & commissioning of (Permeate / Backpulse Pumps) Horizontal centrifugal non clog water pumps with CI Head & Base, bronze Impeller with VFD drive along with motor, pressure gauge with isolation cock, Isolation valve, NRV on delivery line. Isolation valve, stainer (with by-pass) at suction. Mechanical seal, suitable vibration elimination pads of approved design, drain pipe with valve (25 dia) for the pump. The pump shall be suitable for 415±10% volts 3 phase AC supply. (1 working + 1 standby) Capacity : As per Membrane Manufacturer Discharge Head : As per Membrane Manufacturer RPM : As per Membrane Manufacturer | 2.00 | No |  | 150000.00 | 300000.00 | 78000.00 | 156000.00 | 100000.00 | 200000.00 | 13000.00 | 26000.00 | 75000.00 | 150000.00 | 210000.00 | 420000.00 | 211430.00 | 422860.00 | 19532.00 | 39064.00 | 50000.00 | 100000.00 | 115000.00 | 230000.00 | 60000.00 | 120000.00 | 48527.00 | 97054.00 | 35000.00 | 70000.00 | 55000.00 | 110000.00 | 100000.00 | 200000.00 | 26000.00 | HITECH SWEET WATER TECH PVT LTD
19.00 | Supplying, installing, testing & commissioning of Process Instruments, MBR Accessories, Solneoid Valves for Automation & Membrane Ejector as per details below common for entire system Note: The cost shall be inclusive of following instrumentation: Permeate isolation valves Drain valves Backpulse isolation valves Permeate discharge isolation valves Permeate Flow meter Turbidity meter (controller + sensor) (Offline) Permeate pump ejector Solenoid valve on line pH meter digital type Permeate suction pressure guage Permeate suction Isolation valve Other associated piping, valves and items as per approved P&I. | 1.00 | Lot |  | 75000.00 | 75000.00 | 780000.00 | 780000.00 | 250000.00 | 250000.00 | 155000.00 | 155000.00 | 125000.00 | 125000.00 | 210000.00 | 210000.00 | 1087320.00 | 1087320.00 | 195311.00 | 195311.00 | 300000.00 | 300000.00 | 180000.00 | 180000.00 | 40000.00 | 40000.00 | 117333.00 | 117333.00 | 110000.00 | 110000.00 | 275000.00 | 275000.00 | 800000.00 | 800000.00 | 40000.00 | Rysa Infratech Private Limited
20.00 | Providing & fixing level controllers for water pumps to start / stop the pump at set level. Including wiring, cabling from pump to panel & all other accessories as required to operate the system automatically. (Quantity as per vendor design). | 1.00 | Lot |  | 25000.00 | 25000.00 | 130000.00 | 130000.00 | 150000.00 | 150000.00 | 35000.00 | 35000.00 | 125000.00 | 125000.00 | 150000.00 | 150000.00 | 214320.00 | 214320.00 | 84635.00 | 84635.00 | 100000.00 | 100000.00 | 50000.00 | 50000.00 | 8000.00 | 8000.00 | 24000.00 | 24000.00 | 8000.00 | 8000.00 | 23000.00 | 23000.00 | 20000.00 | 20000.00 | 8000.00 | LANDMARK AQUATEC PRIVATE LIMITED, Rysa Infratech Private Limited
21.00 | Providing & fixing on line Electro magnetic type flow meter cum Totaliser for Monitoring the total flow, Flow rate. etc. Including electrical wiring from panel to flow meter. Complete with all type of Plumbing & Electrical connections, accessories, wiring, conduits & supports complete with all respect. The signal from read out shall be 4-20 m.amps to be received on BAS.To be installed at input sewage and Outlet product water of MBR (1 for each module)
21.01 | (i) 40 mm dia | 1.00 | No |  | 45000.00 | 45000.00 | 78000.00 | 78000.00 | 80000.00 | 80000.00 | 65000.00 | 65000.00 | 100000.00 | 100000.00 | 170000.00 | 170000.00 | 218950.00 | 218950.00 | 46875.00 | 46875.00 | 200000.00 | 200000.00 | 60000.00 | 60000.00 | 35000.00 | 35000.00 | 22667.00 | 22667.00 | 28000.00 | 28000.00 | 58000.00 | 58000.00 | 100000.00 | 100000.00 | 22667.00 | QUALICOM SOLUTIONS PRIVATE LIMITED
22.00 | ELECTRICAL INSTALLATION FOR SEWAGE TREATMENT PLANT Design, fabrication, assembling, wiring, supply, installation, testing and commissioning of compartmentized motor control centre shall be fabricated out of 14 gauge CRCA sheet steel in form in 3b formation with reinforcement of suitable size angle iron, channel ‘T’ sections irons and/or flats wherever necessary. Cable gland plates shall be provided on top as well as at the bottom of the panels. Panels shall be treated with all anticorrosive process before painting as per specifications with 2 coats of red oxide primer and final approved shade of powder coated paint. 2 Nos. earthing terminals shall be provided for 3 phase, 4 wire, 50 Hz supply system. Lifting hooks shall also be provided in case of large panels. Approval shall be taken for each panel before fabrication. Cadmium Plated hardware shall be used in fabrication of panels. Quoted rates shall inclusive of cables, cable trays, control cabling, earthing (in accordance to specification) with earthing from panel to each motor / equipment. Incomer 1 Nos. 200 Amp four pole Moulded Case Circuit Breaker (Ics = Icu = 25 KA) with built in thermal based release unit with adjustable setting. BUSBARS 300 Amp TPN busbars (25 KA) of high conductivity electrolytic quality aluminium alloy with heat shrinkable insulation sleeves. INSTRUMENTS 1 Set of digital multifunction meter for 3 phase, 4 wire operation to measure V, A, Hz, W, PF, Wh, THD with RS 485 facility. Acc. class: 1 as per specification. 1 Set of ON, OFF, Trip indicating lamps, LED type, shall be protected by 2 amp SP MCB. 1 Set of LED Phase indicating lamps RYB, shall be protected by 2 amp SP MCB 1 Set of 200/5A, Class 1, 10VA, Cast Resin CT for metering.
22.01 | Outgoings a) 1 Nos TP MCCB for 0.75 kW direct on line starter and outgoing feeders for Semi-Automatic Bar Screen. Each compartment shall contain auto/manual selector switch and indicating lamp with ‘ON/OFF/TRIP’ status of motor. b)1 Nos Single Phase direct on line starter and outgoing feeders for Oil Skimmer c) 2 Nos TP MCCB for 0.75 kW direct on line starter and outgoing feeders for Sewage Transfer Pumps. Each compartment shall contain auto/manual selector switch and indicating lamp with ‘ON/OFF/TRIP’ status of motor. d) 2 Nos TP MCCB for 0.75 kW direct on line starter and outgoing feeders for Plant Room Sump Pumps. Each compartment shall contain auto/manual selector switch and indicating lamp with ‘ON/OFF/TRIP’ status of motor. e) 2 Nos TP MCCB for 0.75 kW direct on line starter and outgoing feeders for Submersible Agitator for Anoxic Tank. Each compartment shall contain auto/manual selector switch and indicating lamp with ‘ON/OFF/TRIP’ status of motor. f) 3 Nos TP MCCB for 3.7 kW direct on line starter and outgoing feeders for Air Blowers for MBR Tank. Each compartment shall contain auto/manual selector switch and indicating lamp with ‘ON/OFF/TRIP’ status of motor. g) 2 Nos TP MCCB for 3.7 kW direct on line starter and outgoing feeders for Air Blowers for Aeration, EQT and SHT. Each compartment shall contain auto/manual selector switch, timer-based auto changeover and indicating lamp with ‘ON/OFF/TRIP’ status of motor. h) 2 Nos TP MCCB for 0.75 kW direct on line starter and outgoing feeders for Filter Press Feed Pumps. Each compartment shall contain auto/manual selector switch and indicating lamp with ‘ON/OFF/TRIP’ status of motor. i) 1 Nos TP MCCB for 1.5 kW direct on line starter and outgoing feeders for Filter Press. Each compartment shall contain auto/manual selector switch and indicating lamp with ‘ON/OFF/TRIP’ status of motor. j) 1 Nos TP MCCB for 1.5 kW direct on line starter and outgoing feeders for Sludge Recirculation Pumps. Each compartment shall contain auto/manual selector switch and indicating lamp with ‘ON/OFF/TRIP’ status of motor. k) 2 Nos TP MCCB for 1.5 kW direct on line starter and outgoing feeders for Permeate Pumps. Each compartment shall contain auto/manual selector switch and indicating lamp with ‘ON/OFF/TRIP’ status of motor. l) Single Phase Feeders for Dosing Pumps m) Space for Level controllers and Instruments
22.02 | Note: All MCCB's to be suitable for motor duty and shall be of 25 KA breaking capacity. Provision shall be made for providing potential free contacts to all pumps starters for connection to building automation system. All motor starter shall be provided with Automatic level controller. Overflow alarm must be provided at the plant room Electrical panel must have the Auto announciator to indicate the system failure if any All Swithgear Ratings are indicative & shall need to be selected based on actual equipment ratings Motors 7.5 HP above should have Star delta starter Permeate Pump should have DOL starter | 1.00 | Nos |  | 250000.00 | 250000.00 | 390000.00 | 390000.00 | 720000.00 | 720000.00 | 25000.00 | 25000.00 | 350000.00 | 350000.00 | 550000.00 | 550000.00 | 976320.00 | 976320.00 | 208000.00 | 208000.00 | 500000.00 | 500000.00 | 250000.00 | 250000.00 | 150000.00 | 150000.00 | 546667.00 | 546667.00 | 170000.00 | 170000.00 | 450000.00 | 450000.00 | 1500000.00 | 1500000.00 | 25000.00 | HITECH SWEET WATER TECH PVT LTD
23.00 | SH-II WATER TREATMENT PLANT
23.01 | Supply, installation, testing & commissioning of water filteration plant (20 m3/h) comprising of the following including all necessary inter connecting piping, control valves, electrical cables, control cables, other accessories etc. as directed and required at site to complete the work.
23.02 | FILTER FEED PUMPS
23.03 | Supply, installation, testing and commissioning of single stage, horizontal, centrifugal, 2 pole, 50 HZ, AC, monoblock pumps (as per IS : 9079) incorporating C.I. casing and frame, stainless steel shaft, SS impeller, TEFC induction motor directly coupled to the pump, IP44 protection, class B insulated, C.I. body, hydraulically and dynamically balanced to give vibration free operation, with mechanical seal arrangement, fixed on a base plate with suitable vibration eleminator pads complete with PCC foundation, bolts grouted in CC blocks of 1:2:4, suitably rated DOL / star-delta starter fixed inside main electrical panel complete with level controller, necessary wiring, pressure gauge on the delivery side and strainer on suction side, including non-return valve and isolating valves on suction and delivery sides as required, including suction and delivery headers complete in all respects.
23.04 | Filter Feed Pumps - 2 nos (1W+1S), having discharge : 20.0 m3/hr (each) at 30 meter head | 2.00 | Nos |  | 125000.00 | 250000.00 | 39000.00 | 78000.00 | 100000.00 | 200000.00 | 25000.00 | 50000.00 | 75000.00 | 150000.00 | 180000.00 | 360000.00 | 159560.00 | 319120.00 | 42318.00 | 84636.00 | 75000.00 | 150000.00 | 65000.00 | 130000.00 | 42000.00 | 84000.00 | 48827.00 | 97654.00 | 90000.00 | 180000.00 | 84000.00 | 168000.00 | 200000.00 | 400000.00 | 50000.00 | HITECH SWEET WATER TECH PVT LTD
24.00 | OXIDATION CHAMBER
24.01 | Supply, installation , testing and commissioning of vertical floor mounted MSEP Oxidation Chamber of suitable size, provided with an inlet distributor, complete with frontal piping & butterfly valves, back wash system & filter media etc. complete with standard fittings like manhole cover, pressure gauge at inlet & outlet, sampling cock, rinse drain valve, air vent valve with piping, bolts, nuts & rubber gaskets.
24.02 | Flow rate = 20.0 M3/hr Vessel Dia = 800 mm HOS = Min. 600 mm Filteration rate = 50 M3/M2/Hr Shell/ Dish thickness = 5 / 6 mm MOC: MSEP | 1.00 | No |  | 200000.00 | 200000.00 | 260000.00 | 260000.00 | 150000.00 | 150000.00 | 100000.00 | 100000.00 | 125000.00 | 125000.00 | 170000.00 | 170000.00 | 212850.00 | 212850.00 | 110676.00 | 110676.00 | 200000.00 | 200000.00 | 210000.00 | 210000.00 | 120000.00 | 120000.00 | 75221.00 | 75221.00 | 425000.00 | 425000.00 | 208000.00 | 208000.00 | 200000.00 | 200000.00 | 75221.00 | QUALICOM SOLUTIONS PRIVATE LIMITED
25.00 | MULTI GRADE FILTER
25.01 | Supply, installation , testing and commissioning of vertical floor mounted MSEP Multi Grade filter of suitable size, provided with an inlet distributor, complete with frontal piping & butterfly valves, back wash system & filter media etc. complete with standard fittings like manhole cover, pressure gauge at inlet & outlet, sampling cock, rinse drain valve, air vent valve with piping, bolts, nuts & rubber gaskets.
25.02 | Flow rate = 20.0 M3/hr Vessel Dia = 1200 mm HOS = Min. 1800 mm Filteration rate = 20 M3/M2/Hr Shell/ Dish thickness = 5 / 6 mm MOC: MSEP | 1.00 | No |  | 225000.00 | 225000.00 | 260000.00 | 260000.00 | 400000.00 | 400000.00 | 175000.00 | 175000.00 | 195000.00 | 195000.00 | 280000.00 | 280000.00 | 368950.00 | 368950.00 | 142000.00 | 142000.00 | 250000.00 | 250000.00 | 135000.00 | 135000.00 | 200000.00 | 200000.00 | 207491.00 | 207491.00 | 330000.00 | 330000.00 | 189000.00 | 189000.00 | 300000.00 | 300000.00 | 135000.00 | HITECH ENVIRO ENGINEERS AND CONSULTANTS PVT LTD
26.00 | Activated Carbon Filter Supply, installation & testing and commissioning of vertical floor mounted MSEP Activated Carbon filter of suitable size, provided with an inlet distributor, complete with frontal piping & butterfly valves, back wash system & filter media etc. complete with standard fittings like manhole cover, pressure gauge at inlet & outlet, sampling cock, rinse drain valve, air vent valve with piping, bolts, nuts & rubber gaskets.
26.01 | Flow rate = 20.0 M3/hr Vessel Dia = 1300 mm HOS = Min. 1800 mm Filteration rate = 15 M3/M2/Hr Shell/ Dish thickness = 5 / 6 mm MOC: MSEP | 1.00 | No |  | 250000.00 | 250000.00 | 286000.00 | 286000.00 | 430000.00 | 430000.00 | 200000.00 | 200000.00 | 245000.00 | 245000.00 | 340000.00 | 340000.00 | 402650.00 | 402650.00 | 167000.00 | 167000.00 | 350000.00 | 350000.00 | 180000.00 | 180000.00 | 250000.00 | 250000.00 | 226100.00 | 226100.00 | 380000.00 | 380000.00 | 254000.00 | 254000.00 | 300000.00 | 300000.00 | 167000.00 | ENHANCE ECOTECH SOLUTION PVT LTD
27.00 | SOFTENER Supply, installation & testing and commissioning of vertical floor mounted MSEP Softener of suitable size, provided with an inlet distributor, complete with frontal piping & butterfly valves, regeneration system with ejector & resin etc. complete with standard fittings like manhole cover, pressure gauge at inlet & outlet, sampling cock, rinse drain valve, air vent valve with piping, bolts, nuts & rubber gaskets.
27.01 | Flow rate = 20.0 M3/hr Vessel Dia = 1300 mm HOS = Min. 2500 mm Resin Volume = 1400 L Shell/ Dish thickness = 5 / 6 mm OBR=200 m3 MOC: MSEP | 1.00 | No |  | 325000.00 | 325000.00 | 780000.00 | 780000.00 | 600000.00 | 600000.00 | 400000.00 | 400000.00 | 395000.00 | 395000.00 | 370000.00 | 370000.00 | 432680.00 | 432680.00 | 350000.00 | 350000.00 | 400000.00 | 400000.00 | 350000.00 | 350000.00 | 500000.00 | 500000.00 | 452863.00 | 452863.00 | 825000.00 | 825000.00 | 390000.00 | 390000.00 | 1000000.00 | 1000000.00 | 325000.00 | SAWEN CONSULTANCY SERVICES PVT. LTD.
28.00 | Providing & fixing on line Electro magnetic type flow meter cum Totaliser for Monitoring the total flow, Flow rate. etc. Including electrical wiring from panel to flow meter. Complete with all type of Plumbing & Electrical connections, accessories, wiring, conduits & supports complete with all respect, capable of trasmitting 4-20mA output. To be installed at outlet of softening unit. | 1.00 | No |  | 65000.00 | 65000.00 | 78000.00 | 78000.00 | 80000.00 | 80000.00 | 65000.00 | 65000.00 | 100000.00 | 100000.00 | 170000.00 | 170000.00 | 146980.00 | 146980.00 | 46875.00 | 46875.00 | 200000.00 | 200000.00 | 115000.00 | 115000.00 | 35000.00 | 35000.00 | 68021.00 | 68021.00 | 125000.00 | 125000.00 | 78000.00 | 78000.00 | 200000.00 | 200000.00 | 35000.00 | Rysa Infratech Private Limited
29.00 | CLORINE DOSING SYSTEM:
29.01 | Supply, installation, testing & commissioning of Chlorine dosing system consisting of one HDPE tank of 200 litres capacity with a positive displacement diaphragm dosing pump having variable flow rate of (0‐6 LPH). The motor shall be suitable for operation at 240 V / single phase 50 Hertz AC supply. The pump shall be supplied complete with necessary polypropylene piping, valves, strainers & injection fittings for complete automatic dosing. | 1.00 | Set |  | 45000.00 | 45000.00 | 15600.00 | 15600.00 | 100000.00 | 100000.00 | 15000.00 | 15000.00 | 25000.00 | 25000.00 | 120000.00 | 120000.00 | 116540.00 | 116540.00 | 22136.00 | 22136.00 | 100000.00 | 100000.00 | 65000.00 | 65000.00 | 25000.00 | 25000.00 | 13333.00 | 13333.00 | 35000.00 | 35000.00 | 18000.00 | 18000.00 | 500000.00 | 500000.00 | 13333.00 | QUALICOM SOLUTIONS PRIVATE LIMITED
30.00 | MAIN DISTRIBUTION BOARD (WATER TREATMENT PLANT) Design, fabrication, assembling, wiring, supply, installation, testing and commissioning of compartmentized motor control centre shall be fabricated out of 14 gauge CRCA sheet steel in form in 3b formation with reinforcement of suitable size angle iron, channel ‘T’ sections irons and/or flats wherever necessary. Cable gland plates shall be provided on top as well as at the bottom of the panels. Panels shall be treated with all anticorrosive process before painting as per specifications with 2 coats of red oxide primer and final approved shade of powder coated paint. 2 Nos. earthing terminals shall be provided for 3 phase, 4 wire, 50 Hz supply system. Lifting hooks shall also be provided in case of large panels. Approval shall be taken for each panel before fabrication. Cadmium Plated hardware shall be used in fabrication of panels. Quoted rates shall inclusive of cables (except submersible pump feeder cable), cable trays, control cabling, earthing (in accordance to specification) with earthing from panel to each motor / equipment.
30.01 | Incomer "2 Nos. 200 Amp four pole Moulded Case Circuit Breaker (Ics = Icu = 25 KA) with built in thermal based release unit with adjustable setting. " BUSBARS 300 Amp TPN busbars (25 KA)of high conductivity electrolytic quality aluminium alloy with heat shrinkable insulation sleeves. BUS COUPLER 1 No. 200 A, FP, MCCB without protection release. INSTRUMENTS 1 Set of digital multifunction meter for 3 phase, 4 wire operation to measure V, A, Hz, W, PF, Wh, THD with RS 485 facility. Acc. class: 1 as per specification. 1 Set of ON, OFF, Trip indicating lamps, LED type , shall be protected by 2 amp SP MCB . 1 Set of LED Phase indicating lamps RYB, shall be protected by 2 amp SP MCB 1 Set of 200/5A, Class 1, 10VA, Cast Resin CT for metering. Outgoings a) 2 Nos TP MCCB for 3.7 kW direct on line starter and out going feeders for Filter Feed Pump. Each compartment shall contain auto/manual selector switch and indicating lamp with ‘ON/OFF/TRIP’ status of motor.status of motor. b) 2 nos of 4 Pole MCCB (100 Amps) for Submersible Pumpset Panels c) Single Phase Feeders for Dosing Pumps Note: All MCCB's to be suitable for motor duty and shall be of 25 KA breaking capacity & Ics= Icu = 100% ) | 1.00 | No |  | 350000.00 | 350000.00 | 260000.00 | 260000.00 | 300000.00 | 300000.00 | 45000.00 | 45000.00 | 125000.00 | 125000.00 | 370000.00 | 370000.00 | 516870.00 | 516870.00 | 104166.00 | 104166.00 | 300000.00 | 300000.00 | 350000.00 | 350000.00 | 70000.00 | 70000.00 | 76667.00 | 76667.00 | 480000.00 | 480000.00 | 175000.00 | 175000.00 | 1000000.00 | 1000000.00 | 45000.00 | HITECH SWEET WATER TECH PVT LTD
31.00 | BOREWELL SUBMERSIBLE PUMP "Supply, installation, testing and commissioning of Multistage vertical submersible pump motor set of CI Body, Stainless steel shaft and impeller , suitable for operation on 3 phase 415 volts + 10% - 15 %, 50 HZ A.C supply, speed 2900 RPM, including supply & laying of copper flat cable of 2 nos 3 core x 6 Sq. m. size upto 45 Mtr length including lowering with U clamp , C class GI pipe of 100 mm NB with necessary sockets & bends etc upto 40 Mtr, 10 mm double steel wire rope upto 80 mtr., well cover (12"" x 8""), NRV and gate valve, supporting clamps, flanges, pressure gauge etc.as per following specifications: Discharge: 600 LPM minimum Head : 45 M minimum. HP : 20 HP" | 2.00 | Set |  | 300000.00 | 600000.00 | 78000.00 | 156000.00 | 100000.00 | 200000.00 | 35000.00 | 70000.00 | 85000.00 | 170000.00 | 280000.00 | 560000.00 | 211420.00 | 422840.00 | 216144.00 | 432288.00 | 200000.00 | 400000.00 | 125000.00 | 250000.00 | 130000.00 | 260000.00 | 116299.00 | 232598.00 | 195000.00 | 390000.00 | 210000.00 | 420000.00 | 150000.00 | 300000.00 | 70000.00 | HITECH SWEET WATER TECH PVT LTD
32.00 | Design, Fabrication, supply, installation, Testing and commissioning of Floor Mounted outdoor type, suitable size control panel cum feeder pillar made of CRCA sheet steel of 2 mm thick for frame work and covers i/c cleaning and finishing complete with powder coating in approved shade, having 150 amps capacity TPN aluminium busbars, bottom base of MS channel and Legs, have a common GI earth bar with 2 nos earth stud, internal connection by suitable aluminium strip/bar or aluminium cable as per specification and control wiring with 2.5 Sq.mm PVC insulated copper conductor cable i/c providing the following switch gears and same should be fixed 2 ft. height (from ground level) on brick foundation i/c outgoing and incoming electrical connection etc as required.
32.01 | 100 amps, 4 pole, 25 KA MCCB ( Ics = Icu = 100 %) incoming with extended rotary handle 20 HP rating Star-Delta starter Single phasing preventer Time switch with suitable power contactor Thermal Over Load relay Voltmeter and ammeter with necessary CTs and selector switches, LED type indication Lamps for incoming | 2.00 | Nos |  | 150000.00 | 300000.00 | 195000.00 | 390000.00 | 100000.00 | 200000.00 | 40000.00 | 80000.00 | 35000.00 | 70000.00 | 120000.00 | 240000.00 | 203460.00 | 406920.00 | 104166.00 | 208332.00 | 300000.00 | 600000.00 | 60000.00 | 120000.00 | 25000.00 | 50000.00 | 31667.00 | 63334.00 | 320000.00 | 640000.00 | 45000.00 | 90000.00 | 80000.00 | 160000.00 | 50000.00 | Rysa Infratech Private Limited
33.00 | Supply of following size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor power cable conforming to IS 7098 (Part 1) amended upto date.
33.01 | 3.5 core X 50 Sq.mm | 200.00 | Mtr |  | 1200.00 | 240000.00 | 200.00 | 40000.00 | 300.00 | 60000.00 | 900.00 | 180000.00 | 200.00 | 40000.00 | 700.00 | 140000.00 | 590.00 | 118000.00 | 625.00 | 125000.00 | 1000.00 | 200000.00 | 560.00 | 112000.00 | 220.00 | 44000.00 | 450.00 | 90000.00 | 269.00 | 53800.00 | 375.00 | 75000.00 | 5000.00 | 1000000.00 | 40000.00 | UY TRIENVIRO PVT. LTD., Trans Organics (India) Pvt. Ltd
34.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc. as required.
34.01 | 3.5 core X 50 Sq.mm | 150.00 | Mtr |  | 1200.00 | 180000.00 | 200.00 | 30000.00 | 250.00 | 37500.00 | 900.00 | 135000.00 | 200.00 | 30000.00 | 700.00 | 105000.00 | 475.00 | 71250.00 | 261.00 | 39150.00 | 300.00 | 45000.00 | 250.00 | 37500.00 | 25.00 | 3750.00 | 166.00 | 24900.00 | 170.00 | 25500.00 | 375.00 | 56250.00 | 5000.00 | 750000.00 | 3750.00 | Rysa Infratech Private Limited
35.00 | Laying and fixing of one number PVC insulated PVC sheathed / XLPE power cable of 1.1 KV grade of following sizes on wall/ surface/ cable tray as required.
35.01 | 3.5 core X 50 Sq.mm | 50.00 | Mtr |  | 1500.00 | 75000.00 | 200.00 | 10000.00 | 400.00 | 20000.00 | 900.00 | 45000.00 | 200.00 | 10000.00 | 700.00 | 35000.00 | 100.00 | 5000.00 | 129.00 | 6450.00 | 500.00 | 25000.00 | 250.00 | 12500.00 | 30.00 | 1500.00 | 144.00 | 7200.00 | 152.00 | 7600.00 | 375.00 | 18750.00 | 5000.00 | 250000.00 | 1500.00 | Rysa Infratech Private Limited
36.00 | Supplying and making cable end termination with brass compression gland and aluminium lugs for following size of PVC insulated PVC sheathed/ XLPE aluminium conductor cable of 1.1 kV grade as required.
36.01 | 3.5 core X 50 Sq.mm | 4.00 | Sets |  | 20000.00 | 80000.00 | 10000.00 | 40000.00 | 300.00 | 1200.00 | 4625.00 | 18500.00 | 25000.00 | 100000.00 | 100000.00 | 400000.00 | 1050.00 | 4200.00 | 326.00 | 1304.00 | 20000.00 | 80000.00 | 1000.00 | 4000.00 | 100.00 | 400.00 | 867.00 | 3468.00 | 24750.00 | 99000.00 | 2600.00 | 10400.00 | 5000.00 | 20000.00 | 400.00 | Rysa Infratech Private Limited
37.00 | Earthing with GI earth pipe 4.5 mtr Long, 40mm dia i/c all accessories and providing masonary enclosure with cover plate, having locking arrangement and watering pipe etc. with charcoal/coke and salt as required. | 4.00 | Nos |  | 13000.00 | 52000.00 | 10000.00 | 40000.00 | 2500.00 | 10000.00 | 39000.00 | 156000.00 | 25000.00 | 100000.00 | 170000.00 | 680000.00 | 16850.00 | 67400.00 | 5209.00 | 20836.00 | 50000.00 | 200000.00 | 25000.00 | 100000.00 | 7000.00 | 28000.00 | 3639.00 | 14556.00 | 31000.00 | 124000.00 | 6500.00 | 26000.00 | 50000.00 | 200000.00 | 10000.00 | POLLUCON TECHNOLOGIES LIMITED
38.00 | Supply & laying 25 mm x 5mm size GI strip at 0.5 m below ground level as strip earth electrode, including connection/ termination with GI nut, bolt, spring, washer etc as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50 mm) | 20.00 | Mtr |  | 2000.00 | 40000.00 | 1140.00 | 22800.00 | 150.00 | 3000.00 | 3750.00 | 75000.00 | 500.00 | 10000.00 | 3500.00 | 70000.00 | 350.00 | 7000.00 | 183.00 | 3660.00 | 2000.00 | 40000.00 | 350.00 | 7000.00 | 100.00 | 2000.00 | 3872.00 | 77440.00 | 1400.00 | 28000.00 | 50.00 | 1000.00 | 5000.00 | 100000.00 | 1000.00 | B S ENVIRO N INFRACON PVT LTD
39.00 | Supply & laying 25 mm X 5 mm size GI strip on surface or in recess for connection etc as required. | 30.00 | Mtr |  | 2000.00 | 60000.00 | 1140.00 | 34200.00 | 120.00 | 3600.00 | 3700.00 | 111000.00 | 500.00 | 15000.00 | 3500.00 | 105000.00 | 250.00 | 7500.00 | 157.00 | 4710.00 | 2000.00 | 60000.00 | 350.00 | 10500.00 | 150.00 | 4500.00 | 5525.00 | 165750.00 | 370.00 | 11100.00 | 30.00 | 900.00 | 5000.00 | 150000.00 | 900.00 | B S ENVIRO N INFRACON PVT LTD
40.00 | SH-III Operation and Maintenance
41.00 | "Operation, upkeeing and carrying out day to day maintenance of all equipments, machinaries and accessories related to 75 KLD Sewage Treatment Plant, Water Treatment Plant & submersible pumps involving operation minor condition of the systems, ensuring serviceability / satisfactory working condition of the systems, maintenacne of records / documentation of the above works etc., as per the detailed specification, terms & conditions covered under this contract on all days including sundays & holidays of the month complete as required. The required minimum man power (One Technician cum Operator and One helper in each shift for round the clock operation ) to be deployed for each shift of 8 hrs for the equipments to be operated and upkeeped shall be as per special condition of contract. " (i) First Year ( During DLP ) (18.8813 % per year of total amount of SITC work of STP & WTP) - 1 Job (ii) Second Year ( Yearly 5% cumulative enhancement on First year Rate) - 1 Job (iii) Third Year ( Yearly 5% cumulative enhancement on Second year Rate) - 1 Job (iv) Fourth Year ( Yearly 5% cumulative enhancement on Third year Rate) - 1 Job (v) Fifth Year ( Yearly 5% cumulative enhancement on Fourth year Rate) - 1 Job (vi) Sixth Year ( Yearly 5% cumulative enhancement on Fifth year Rate) - 1 Job
42.00 | "Comprehensive Maintenance of 75 KLD Sewage Treatment Plant inclusive of all spares, chemicals & material & carrying out breakdown & the preventive maintenance as per OEM recommendations after Defect Liability Period." (i) First Year (5.9318 % per year of amount of SITC work of STP) - 1 Job (ii) Second Year ( Yearly 1.4931 % cumulative enhancement on First year Rate) - 1 Job (iii) Third Year ( Yearly 1.5403 % cumulative enhancement on Second year Rate) - 1 Job (iv) Fourth Year ( Yearly 1.5851% cumulative enhancement on Third year Rate) - 1 Job (v) Fifth Year ( Yearly 1.6778% cumulative enhancement on Fourth year Rate) - 1 Job
| Total in Figures |  |  |  |  | 11061000.00 |  | 10535100.00 |  | 13750300.00 |  | 6600000.00 |  | 16049000.00 |  | 18045000.00 |  | 18859740.00 |  | 5959293.00 |  | 14500000.00 |  | 9518500.00 |  | 7671150.00 |  | 8196692.00 |  | 6499000.00 |  | 8575500.00 |  | 26800000.00
Lowest Amount Quoted BY: ENHANCE ECOTECH SOLUTION PVT LTD(5959293.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of 75 KLD Sewage Treatment Plant (STP) based on MBR Treatment Water Treatment Plant (WTP) and Submersible Pump at Kolkata Airport. Tender ID: 2021_AAI_84760_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | ENHANCE ECOTECH SOLUTION PVT LTD | 5959293.00 | L1
| 2 | LANDMARK AQUATEC PRIVATE LIMITED | 6499000.00 | L2
| 3 | HITECH SWEET WATER TECH PVT LTD | 6600000.00 | L3
| 4 | Rysa Infratech Private Limited | 7671150.00 | L4
| 5 | QUALICOM SOLUTIONS PRIVATE LIMITED | 8196692.00 | L5
| 6 | B S ENVIRO N INFRACON PVT LTD | 8575500.00 | L6
| 7 | HITECH ENVIRO ENGINEERS AND CONSULTANTS PVT LTD | 9518500.00 | L7
| 8 | UY TRIENVIRO PVT. LTD. | 10535100.00 | L8
| 9 | SAWEN CONSULTANCY SERVICES PVT. LTD. | 11061000.00 | L9
| 10 | POLLUCON TECHNOLOGIES LIMITED | 13750300.00 | L10
| 11 | Sainath Envirotech | 14500000.00 | L11
| 12 | Trans Organics (India) Pvt. Ltd | 16049000.00 | L12
| 13 | MECO TECHNOLOGIES PVT LTD | 18045000.00 | L13
| 14 | ENSYS TECHNOLOGIES (I) PVT LTD | 18859740.00 | L14
| 15 | WTE INFRA PROJECTS PVT LTD | 26800000.00 | L15