## BoQ1
Government eProcurement System Created By: Dadan Singh Created Date/Time: 14-Sep-2021 12:17 PM Tender Title: Provision of lightning Arrestor for CCR Room / Power House building at R.B. Airport, Bhopal Tender ID: 2021_AAI_84913_1
Tender Inviting Authority: AGM(E-E), AAI, R.B. Airport, Bhopal
Name of Work: Provision of lightning Arrestor for CCR Room / Power House building at R.B. Airport, Bhopal.
Contract No: AAI/BPL/ENGG(E)/NIT-06/2021-22
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | BR Power Control and Automation Services(GSTN-06AREPS4024K1ZP) |  | Taral Electricals(GSTN-24ACMPR0280M1Z9) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5) |  | Manish Electricals(GSTN-22ABLPM9012E1ZY)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, fixing, testing and commissioning of single spike air terminals of following lengths and dia as required and as per site conditions. The air terminal shall be manufactured with copper coated steel. The terminal shall be provided with the integrated / attached threaded base support suitable for mounting the terminals as per site condition. The base support shall be minimum 3 mm thick and shall have inbuilt connector fitting for connection of lightning conductor in such a way that conductor contact area shall not be less than 40mm on all side of the conductor as per IS/IEC 62305. a) 1000 mm -10mm dia | 8.00 | Each |  | 2383.00 | 19064.00 | 1626.00 | 13008.00 | 375.00 | 3000.00 | 11000.00 | 88000.00 | 3000.00 | Awasthi Electric Works
2.00 | Providing and fixing 8 mm dia copper clad steel round conductor for air termination network at parapet wall. Including providing suitable parapet conductor holder, Tee, Straight & cross connector etc. on parapet wall, roof and vertical facade of masonry / glass / metalic work as per IS/IEC 62305. | 215.00 | Meter |  | 410.00 | 88150.00 | 599.00 | 128785.00 | 355.00 | 76325.00 | 100.00 | 21500.00 | 21500.00 | Manish Electricals
3.00 | Supply and fixing of copper Bridging cable of 16 sqmm including lugs to connect air termination rod with any metallic structure on the roof as per IS/IEC 62305. | 5.00 | Meter |  | 275.00 | 1375.00 | 1061.00 | 5305.00 | 585.00 | 2925.00 | 8000.00 | 40000.00 | 1375.00 | BR Power Control and Automation Services
4.00 | Providing and fixing 8 mm dia copper clad steel round conductor for Down conductors to be installed on vertical façade of masonry / glass / metalic work. Including providing connector holder etc and install at every 1 mtr. as per IS/IEC 62305. (For vertical run) | 65.00 | Meter |  | 424.00 | 27560.00 | 423.00 | 27495.00 | 415.00 | 26975.00 | 400.00 | 26000.00 | 26000.00 | Manish Electricals
5.00 | Supply, fixing, testing and commissioning of Lightning Strike counter for counting the number of lightning strikes without any power supply. The Counter should be mounted on the Down Conductor. The Lightning Counter should be IP65 rated enclosure suitable for external application as per IS/IEC 62305. | 2.00 | Each |  | 12773.00 | 25546.00 | 29892.00 | 59784.00 | 21900.00 | 43800.00 | 11800.00 | 23600.00 | 23600.00 | Manish Electricals
6.00 | Supply and fixing of Test Link to disconnect the down conductor from the earth termination network for regular checks of the earth termination resistance value. (with stainless steel enclosure) as per IS/IEC 62305. | 9.00 | Each |  | 2383.00 | 21447.00 | 3900.00 | 35100.00 | 1850.00 | 16650.00 | 2500.00 | 22500.00 | 16650.00 | Awasthi Electric Works
7.00 | Supply and fixing of Expansion piece of made of 8mm Copper clad steel (CCS) to maintain the flexibility to the conductor due to heat IS/IEC 62305. | 11.00 | Each |  | 691.00 | 7601.00 | 2015.00 | 22165.00 | 585.00 | 6435.00 | 900.00 | 9900.00 | 6435.00 | Awasthi Electric Works
8.00 | Providing and laying 10 mm dia. Copper clad steel (CCS) Conductor laid at 500mm below the ground, as required and as per specification and code of practice IS/IEC 62305. | 175.00 | Meter |  | 478.00 | 83650.00 | 273.00 | 47775.00 | 410.00 | 71750.00 | 400.00 | 70000.00 | 47775.00 | Taral Electricals
9.00 | Supply and fixing of Maintenance Free Earthing termination made of copper-bonded rod of 10 feet length, 14.2 mm dia. (Minimum copper bonding shall be 0.25mm) along with Rod-to-Conductor connectors, Carbon based Earth enhancement material 25 kg, PVC Pit Cover and other accessories as required and as per IEC 62561/IS:3043-2018 | 9.00 | Each |  | 12867.00 | 115803.00 | 8450.00 | 76050.00 | 10400.00 | 93600.00 | 13000.00 | 117000.00 | 76050.00 | Taral Electricals
| Total in Figures |  |  |  |  | 390196.00 |  | 415467.00 |  | 341460.00 |  | 418500.00
Lowest Amount Quoted BY: Awasthi Electric Works(341460.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of lightning Arrestor for CCR Room / Power House building at R.B. Airport, Bhopal Tender ID: 2021_AAI_84913_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Awasthi Electric Works | 341460.00 | L1
| 2 | BR Power Control and Automation Services | 390196.00 | L2
| 3 | Taral Electricals | 415467.00 | L3
| 4 | Manish Electricals | 418500.00 | L4