## BoQ1
Government eProcurement System Created By: UMESH KUMAR SINGH Created Date/Time: 06-Oct-2021 12:35 PM Tender Title: Replacement of DG Set of DVOR at Surat Airport Tender ID: 2021_AAI_85454_1
Tender Inviting Authority: SM (E-E), AAI, Surat Airport, Surat
Name of Work: Replacement of DG Set of DVOR at Surat Airport.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Mona Generator Services Pvt. Ltd.(GSTN-07AAFCM4263P1ZZ) |  | SHEKHAWATI BUILDCON PRIVATE LIMITRD(GSTN-08AAMCS0221J1ZE) |  | Taral Electricals(GSTN-24ACMPR0280M1Z9) |  | Manish Electricals(GSTN-22ABLPM9012E1ZY) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | DIESEL GENERATOR SETS
1.10 | SITC of minimum 40 KVA prime power D.G. Set with acoustic enclosure conforming to latest environment regulations for emmission and noise levels complete with Diesel Engine of suitable BHP (considering de-rating factor if any) at 1500 RPM, water cooled, (Radiator type), four stroke, electric start, turbo-charged & inter/after cooled conforming to BS: 5514 with all standard accessories, coupled with alternator of 40KVA rating prime power rated, brushless, self excited, self regulated and suitable for continuous operation, generation 415 V +/- 5% Volts at 0.8 PF (lag), 50Hz, 3 phase, 4 wire system generally conforming to BS: 2613 & IS: 4722. along with DG set command control panel complete as required. Both Engine and Alternator shall be mounted on common channel iron base frame, with complete fuel pipe line, antivibration mountings, residential type silencer , batteries & battery charger, minimum 95 ltr inbuild HSD tank (day tank) with level indicator, first fill of lubricating oil, filling of sufficient diesel for testing & commissioning, and all mandatory accessories, complete with neccessary civil work of making cement concrete foundation for placing the DG set, grouting, chipping, finishing with cement etc as recommended by OEM and as per site condition etc as required. The work shall be as per C.E.A/Electrical inspectorate standards. | 1.00 | Job |  | 603000.00 | 603000.00 | 391000.00 | 391000.00 | 559300.00 | 559300.00 | 688500.00 | 688500.00 | 639000.00 | 639000.00 | 391000.00 | SHEKHAWATI BUILDCON PRIVATE LIMITRD
2.00 | Insulated Exhaust Piping with aluminium cladding : Supply, installation, testing and commissioning of insulated MS exhaust pipe of 100mm dia with aluminium cladding of suitable length conforming to class - C as per relevant IS , i/c insulation of complete exhaust piping with mineral wool/rock wool of appropriate thickness and density, suitable for higher temperature with 24 SWG aluminium cladding (around the exhaust pipe) and fixing / supporting arrangement for piping, insulation & aliminium cladding etc. with all other required accessories such as bends, flanges, stainless steel flexible bellows . complete as required. | 8.00 | Mtr. |  | 9321.00 | 74568.00 | 2200.00 | 17600.00 | 4255.00 | 34040.00 | 1800.00 | 14400.00 | 6000.00 | 48000.00 | 14400.00 | Manish Electricals
3.00 | Supply of following sizes of XLPE insulated PVC sheathed, aluminium conductor, armoured, power cable of 1.1 KV grade conforming to IS 7098 (Part I), 1988 amended upto date.
3.10 | 3.5 x 70 Sqmm | 40.00 | Mtr |  | 330.00 | 13200.00 | 380.00 | 15200.00 | 336.00 | 13440.00 | 560.00 | 22400.00 | 395.00 | 15800.00 | 13200.00 | Mona Generator Services Pvt. Ltd.
4.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
4.10 | Above 35 sq. mm and upto 95 sq. mm | 30.00 | Mtr |  | 28.00 | 840.00 | 130.00 | 3900.00 | 92.00 | 2760.00 | 50.00 | 1500.00 | 100.00 | 3000.00 | 840.00 | Mona Generator Services Pvt. Ltd.
5.00 | Outdoor LT Feeder pillar Panel (PTTA)
5.10 | Supply, Installation, Testing and Commissioning of LT Feeder pillar Panel, cubicle type, made out of 2 mm thick CRCA sheet steel, totally enclosed, outdoor weather proof, protection free standing, floor mounting, dust and vermin proof, indoor, compartmentalized, powder coated painting, suitable for operation on 3 phase and neutral, 415V, 50Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper leads/ solid aluminium strips,MS stand including cement concrete foundation work, door locking arrangement, provision of bottom entry for incoming and outgoing cables. INCOMING: 1 Nos. MCCB, 250 Amps, 4 Pole, 35 kA with adjustable setting, thermal magnetic release with O/C & S/C protection as per specification and with following accessories. Note: It should have appropriate spacing between busbars for terminating 3.5 x 240 sq.mm XLPE insulated cable. BUS - BAR 4 Pole aluminum bus bars of 250 A capacity with heat shrinkable coloured sleeves i/c SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 35 KA for 1 sec. INSTRUMENTS & ACCESSORIES 1 No. 96 mm x 96 mm digital type Voltmeter with suitable range for 3 phase, 4 wire operation with LED display and selector switch backup by 3 nos of 2Amp MCB . 1 No. 96 mm x 96 mm digital type Ammeter for 3 phase 4 wire operation with LED display and selector switch. 5 Nos of LED type phase indicating lamps (R,Y,B,ON/OFF) with controlled by 2 Amp MCB . OUTGOING: 3 Nos. 63A, 4pole, 35kA, MCCB with suitable four pole contactor, auto/ manual selector switches and necessary wiring etc. Outgoing Feedar shall have ON, OFF LED light with back up 2 Amp SP MCB. Note: It should have appropriate spacing between busbars for terminating 3.5 x 240 sq.mm XLPE insulated cable. | 1.00 | Job |  | 158256.00 | 158256.00 | 225000.00 | 225000.00 | 182339.00 | 182339.00 | 150000.00 | 150000.00 | 135000.00 | 135000.00 | 135000.00 | Awasthi Electric Works
6.00 | Outdoor LT Feeder pillar Panel (PTTA)
6.10 | Supply, Installation, Testing and Commissioning of LT Feeder pillar Panel, cubicle type, made out of 2 mm thick CRCA sheet steel, totally enclosed, outdoor weather proof, protection free standing, floor mounting, dust and vermin proof, indoor, compartmentalized, powder coated painting, suitable for operation on 3 phase and neutral, 415V, 50Hz AC supply system with busbars extensible on both sides, interconnections with suitable size of copper leads/ solid aluminium strips,MS stand including cement concrete foundation work, door locking arrangement, provision of bottom entry for incoming and outgoing cables. INCOMING: 1 Nos. MCCB, 400 Amps, 4 Pole, 35 kA with adjustable setting, thermal magnetic release with O/C & S/C protection as per specification and with following accessories. Note: It should have appropriate spacing between busbars for terminating 3.5 x 240 sq.mm XLPE insulated cable. BUS - BAR: 4 Pole aluminum bus bars of 400 A capacity with heat shrinkable coloured sleeves i/c SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 35 KA for 1 sec. INSTRUMENTS & ACCESSORIES: 1 No. 96 mm x 96 mm digital type Voltmeter with suitable range for 3 phase, 4 wire operation with LED display and selector switch backup by 3 nos of 2Amp MCB . 1 No. 96 mm x 96 mm digital type Ammeter for 3 phase 4 wire operation with LED display and selector switch. 5 Nos of LED type phase indicating lamps (R,Y,B,ON/OFF) with controlled by 2 Amp MCB . OUTGOING: 1) 6 Nos. 100A, 4pole, 35kA, MCCB with suitable four pole contactor, auto/ manual selector switches and necessary wiring etc. Outgoing Feedar shall have ON, OFF LED light with back up 2 Amp SP MCB. Note: It should have appropriate spacing between busbars for terminating 3.5 x 240 sq.mm XLPE insulated cable. 2) 2 Nos. 63A, 4 pole, 35kA, MCCB with suitable four pole contactor, 0-24 hours astroniomical timer, auto/ manual selector switches and necessary wiring etc. Outgoing Feedar shall have ON, OFF LED light with back up 2 Amp SP MCB. Note: It should have appropriate spacing between busbars for terminating 4 x 25 sq.mm XLPE insulated cable. | 2.00 | Job |  | 269940.00 | 539880.00 | 325000.00 | 650000.00 | 212425.00 | 424850.00 | 240000.00 | 480000.00 | 285000.00 | 570000.00 | 424850.00 | Taral Electricals
7.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and 20 mm dia medium class GI watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required | 2.00 | Set |  | 16000.00 | 32000.00 | 16000.00 | 32000.00 | 14927.00 | 29854.00 | 12500.00 | 25000.00 | 14500.00 | 29000.00 | 25000.00 | Manish Electricals
8.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and and 20 mm dia medium class GI watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Set |  | 8000.00 | 32000.00 | 8000.00 | 32000.00 | 8464.00 | 33856.00 | 7500.00 | 30000.00 | 6000.00 | 24000.00 | 24000.00 | Awasthi Electric Works
9.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia medium class G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 50.00 | Mtr. |  | 1303.00 | 65150.00 | 1200.00 | 60000.00 | 1424.00 | 71200.00 | 1250.00 | 62500.00 | 1300.00 | 65000.00 | 60000.00 | SHEKHAWATI BUILDCON PRIVATE LIMITRD
10.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia medium class G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 70.00 | Mtr. |  | 453.00 | 31710.00 | 500.00 | 35000.00 | 422.00 | 29540.00 | 1250.00 | 87500.00 | 470.00 | 32900.00 | 29540.00 | Taral Electricals
11.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 30.00 | Mtr. |  | 14.00 | 420.00 | 40.00 | 1200.00 | 26.00 | 780.00 | 30.00 | 900.00 | 22.00 | 660.00 | 420.00 | Mona Generator Services Pvt. Ltd.
12.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.
12.10 | 3.5 X 240 sqmm | 14.00 | Set |  | 808.00 | 11312.00 | 800.00 | 11200.00 | 862.00 | 12068.00 | 1000.00 | 14000.00 | 850.00 | 11900.00 | 11200.00 | SHEKHAWATI BUILDCON PRIVATE LIMITRD
12.20 | 3.5 X 70 sqmm | 4.00 | Set |  | 297.00 | 1188.00 | 500.00 | 2000.00 | 369.00 | 1476.00 | 600.00 | 2400.00 | 450.00 | 1800.00 | 1188.00 | Mona Generator Services Pvt. Ltd.
12.30 | 4 X 10 sqmm | 4.00 | Set |  | 144.00 | 576.00 | 200.00 | 800.00 | 253.00 | 1012.00 | 400.00 | 1600.00 | 150.00 | 600.00 | 576.00 | Mona Generator Services Pvt. Ltd.
13.00 | Dismantling/ Opening of already terminated PVC insulated and PVC sheathed/XLPE aluminium conductor cable of 1.1 kV with brass compression gland and aluminium lugs by cutting the cable and pluging the hole with sealant after drawing the cable for following size as required.
13.10 | 3.5 X 240 sqmm | 14.00 | Set |  | 450.00 | 6300.00 | 250.00 | 3500.00 | 115.00 | 1610.00 | 200.00 | 2800.00 | 150.00 | 2100.00 | 1610.00 | Taral Electricals
13.20 | 4 X 35 sqmm | 1.00 | Set |  | 200.00 | 200.00 | 220.00 | 220.00 | 81.00 | 81.00 | 200.00 | 200.00 | 100.00 | 100.00 | 81.00 | Taral Electricals
13.30 | 4 X 16 sqmm | 4.00 | Set |  | 175.00 | 700.00 | 200.00 | 800.00 | 40.00 | 160.00 | 100.00 | 400.00 | 100.00 | 400.00 | 160.00 | Taral Electricals
13.40 | 4 X 10 sqmm | 4.00 | Set |  | 175.00 | 700.00 | 200.00 | 800.00 | 40.00 | 160.00 | 100.00 | 400.00 | 100.00 | 400.00 | 160.00 | Taral Electricals
14.00 | Dismantling of existing installed Feeder panel of approx size of 1.78 x 1.34 x 0.55 mtr. i/c taking of dismantaled Feeder panel to the within Airport premises as per direction of Engineer-in-Charge. | 3.00 | Job |  | 4000.00 | 12000.00 | 4000.00 | 12000.00 | 5130.00 | 15390.00 | 5000.00 | 15000.00 | 2000.00 | 6000.00 | 6000.00 | Awasthi Electric Works
15.00 | Dismantling of existing installed 32.5 KVA DG set i/c taking of dismantaled DG set to the within Airport premises as per direction of Engineer-in-Charge. | 1.00 | Job |  | 13000.00 | 13000.00 | 8000.00 | 8000.00 | 28451.00 | 28451.00 | 20000.00 | 20000.00 | 4000.00 | 4000.00 | 4000.00 | Awasthi Electric Works
| Total in Figures |  |  |  |  | 1597000.00 |  | 1502220.00 |  | 1442367.00 |  | 1619500.00 |  | 1589660.00
Lowest Amount Quoted BY: Taral Electricals(1442367.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of DG Set of DVOR at Surat Airport Tender ID: 2021_AAI_85454_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Taral Electricals | 1442367.00 | L1
| 2 | SHEKHAWATI BUILDCON PRIVATE LIMITRD | 1502220.00 | L2
| 3 | Awasthi Electric Works | 1589660.00 | L3
| 4 | Mona Generator Services Pvt. Ltd. | 1597000.00 | L4
| 5 | Manish Electricals | 1619500.00 | L5