## BoQ1
Government eProcurement System Created By: SHALENDERA KUMAR Created Date/Time: 27-Sep-2021 12:42 PM Tender Title: Replacement of Distribution Panels and Energy Meters in Residential Colony at Imphal International Airport Tender ID: 2021_AAI_87672_1
Tender Inviting Authority: Asstt. General Manager (Engg-Electrical)-II, AAI, Imphal Airport.
Name of Work: Replacement of Distribution Panels and Energy Meters in Residential Colony at Imphal International Airport.
Contract No: 2021_AAI_87672_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | BR Power Control and Automation Services(GSTN-06AREPS4024K1ZP) |  | KHARIBAM MAIMUSINGH(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Fabrication, S.I.T.C of Indoor MV Panel with Single door arrangement made out of 2mm thick outer sheet, dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing, suitable for operation at 433 V, 3 phase, 4 wire, 50 Hz, A.C. Power Supply System complete with all accessories, interconnection, connection, earthing, painting, grouting, providing pedastal UPTO THE HEIGHT OF 300 MM, Cable Entry provision etc. as required and comprising of following: 1.1 One No. of 100 A, 36 KA, 4P MCCBs with Microprocessor Based Releases for OC/SC/EF Protection as INCOMER with CT Operated MFM of Conserve Make Model EM6400 or Equivalent, ON/OFF/TRIP Indication Lamps and Phase Indication Lamps, as required. 1.2 Two No. of 32 A, 25 KA, 4P MCCB with Thermal Magnetic Releases for Protection as Outgoing, ON/OFF/TRIP Indication Lamps as required. 1.3 Six Nos. 32 A, DP "C" curve, 10KA MCB for single phase supply, with Single Phase Electronic Energy Meter with LCD display of range 5-30A as required. 1.4 One Set of 150 Amps Al. Bus Bars with at Par Neutral BUS BARS as required. 1.5 All accessories such as fuses, auxillary contactors, auxillary switches, etc. as required. ALL AS ABOVE 1.1 To 1.5 | 1.00 | Job |  | 149955.00 | 149955.00 | 113260.00 | 113260.00 | 113260.00 | KHARIBAM MAIMUSINGH
2.00 | Fabrication, S.I.T.C of Outdoor MV Feeder Pillar Panel with double door arrangement made out of 3mm thick outer sheet and 2mm thick inner sheet and partition CRCA sheet steel, dust tight, vermin proof, totally enclosed, cubicle type WITH TOP CANOPY FOR RAIN PROTECTION, floor mounting, free standing, suitable for operation at 433 V, 3 phase, 4 wire, 50 Hz, A.C. Power Supply System complete with all accessories, interconnection, connection, earthing, painting, grouting, providing pedastal UPTO THE HEIGHT OF 450 MM, Cable Entry provision etc. as required and comprising of following: 2.1 One No. of 125 A, 36 KA, 4P MCCBs with Microprocessor Based Releases for OC/SC/EF Protection as INCOMER with CT Operated MFM of Conserve Make Model EM6400 or Equivalent, ON/OFF/TRIP Indication Lamps and Phase Indication Lamps, as required. 2.2 Four No. of 40 A, 25 KA, 4P MCCB with Thermal Magnetic Releases for Protection as Outgoing, ON/OFF/TRIP Indication Lamps as required. 2.3 Four Nos. 32 A, DP "C" curve, 10KA MCB for single phase supply as required. 2.4 One Set of 200 Amps Al. Bus Bars with at Par Neutral BUS BARS as required. ALL AS ABOVE 2.1 To 2.4 | 1.00 | Job |  | 167943.00 | 167943.00 | 136640.00 | 136640.00 | 136640.00 | KHARIBAM MAIMUSINGH
3.00 | Supply of following sizes XLPE insulated PVC sheathed armoured aluminium conductor cable of 1.1 KV Grade conforming to IS:7098 (Part 1) with upto date amendment etc. complete as required.
3.10 | 3.5 core x 95 Sqmm. | 200.00 | Meter |  | 538.00 | 107600.00 | 458.00 | 91600.00 | 91600.00 | KHARIBAM MAIMUSINGH
3.20 | 3.5 core x 70 Sqmm. | 330.00 | Meter |  | 428.00 | 141240.00 | 343.00 | 113190.00 | 113190.00 | KHARIBAM MAIMUSINGH
3.30 | 3.5 core x 35 Sqmm. | 200.00 | Meter |  | 246.00 | 49200.00 | 195.00 | 39000.00 | 39000.00 | KHARIBAM MAIMUSINGH
3.40 | 4 core x 25 Sqmm. | 130.00 | Meter |  | 214.00 | 27820.00 | 175.00 | 22750.00 | 22750.00 | KHARIBAM MAIMUSINGH
4.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required.
4.10 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 220.00 | Meter |  | 142.00 | 31240.00 | 250.00 | 55000.00 | 31240.00 | BR Power Control and Automation Services
4.20 | 90 mm dia (OD-90 mm & ID-76 mm nominal) | 250.00 | Meter |  | 91.00 | 22750.00 | 198.00 | 49500.00 | 22750.00 | BR Power Control and Automation Services
5.00 | Providing and Fixing of 100 mm dia (medium class) G. I. pipes i/c digging work of 0.5 meter depth & 0.3 meter width for the road crossing & filling the surface with 1:3:6 PCC of 1 feet width and 4 inches deep complete as required. | 120.00 | Meter |  | 1867.00 | 224040.00 | 1600.00 | 192000.00 | 192000.00 | KHARIBAM MAIMUSINGH
6.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required.
6.10 | Above 35 sq. mm and upto 95 sq. mm | 350.00 | Meter |  | 76.00 | 26600.00 | 106.00 | 37100.00 | 26600.00 | BR Power Control and Automation Services
6.20 | Upto 35 sq. mm | 250.00 | Meter |  | 57.00 | 14250.00 | 93.00 | 23250.00 | 14250.00 | BR Power Control and Automation Services
7.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
7.10 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 130.00 | Meter |  | 89.00 | 11570.00 | 155.00 | 20150.00 | 11570.00 | BR Power Control and Automation Services
7.20 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 50.00 | Meter |  | 63.00 | 3150.00 | 101.00 | 5050.00 | 3150.00 | BR Power Control and Automation Services
8.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
8.10 | 4 X 25 sq. mm (28mm) | 5.00 | Set |  | 476.00 | 2380.00 | 302.00 | 1510.00 | 1510.00 | KHARIBAM MAIMUSINGH
8.20 | 3.5 X 95 sq. mm (45mm) | 2.00 | Set |  | 921.00 | 1842.00 | 530.00 | 1060.00 | 1060.00 | KHARIBAM MAIMUSINGH
8.30 | 3.5 X 70 sq. mm (38mm) | 6.00 | Set |  | 1047.00 | 6282.00 | 473.00 | 2838.00 | 2838.00 | KHARIBAM MAIMUSINGH
8.40 | 3.5 X 35 sq. mm (32mm) | 2.00 | Set |  | 587.00 | 1174.00 | 296.50 | 593.00 | 593.00 | KHARIBAM MAIMUSINGH
8.50 | 3 X 10 sq. mm (22mm) | 9.00 | Set |  | 294.00 | 2646.00 | 24.00 | 216.00 | 216.00 | KHARIBAM MAIMUSINGH
9.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. (with charcoal/ coke and salt) as required. | 4.00 | Set |  | 11334.00 | 45336.00 | 4557.00 | 18228.00 | 18228.00 | KHARIBAM MAIMUSINGH
10.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Meter |  | 139.00 | 2780.00 | 870.00 | 17400.00 | 2780.00 | BR Power Control and Automation Services
11.00 | SITC of Single Phase, 240 V, 50 Hz Electronic Energy Sub-Meter with LCD display and Box of range (5-30) Amp. at different locations. | 15.00 | Each |  | 1894.00 | 28410.00 | 2444.00 | 36660.00 | 28410.00 | BR Power Control and Automation Services
| Total in Figures |  |  |  |  | 1068208.00 |  | 976995.00
Lowest Amount Quoted BY: KHARIBAM MAIMUSINGH(976995.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Distribution Panels and Energy Meters in Residential Colony at Imphal International Airport Tender ID: 2021_AAI_87672_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | KHARIBAM MAIMUSINGH | 976995.00 | L1
| 2 | BR Power Control and Automation Services | 1068208.00 | L2