## BoQ1
Government eProcurement System Created By: ANBU MURUGAN S Created Date/Time: 12-Oct-2021 01:09 PM Tender Title: Installation of new ILS at MBB Airport, Agartala (SH- Construction of Localizer hut and platform including internal electrification and associated work) Tender ID: 2021_AAI_88550_1
Tender Inviting Authority: AIRPORTS AUTHORITY OF INDIA
Name of Work : Installation of new ILS at MBB Airport, Agartala (SH: Construction of Localizer hut and platform i/c internal electrification and associated work)
Contract No: 2021_AAI_88550_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Subhas Malakar(GSTN-16ADGPM0192E1ZT) |  | M/s Sadguru Engineers & Allied Services Pvt. Ltd.(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I (Civil Works) Providing and fixing of Fire retardant water proof Frangible Hut for localizer and Glide path inside the operational area etc., complete as per the direction of E-I-C. The wall and roof shall be made of 40mm thick PUF panels having density 40±2 Kg/M³, outer skin and inner skin shall be made of 2mm thick FRP Sheets. The jointing system should be tounge and groove configuration. The size of hut shall be 7Mtr x 3.5Mtr x 3Mtr having one partition and 2 nos doors including fixtures. Hut shall have adjoining toilet of size 1.2Mtr x 1.8Mtr x 2Mtr having one door including fixtures. Necessary provision should be made availble for fixing of Electrical Panels, AC units, light fittings, Taps, water lines, sewer line , EWC, water tank etc.,. The outer structure shall be painted with white and red 2 feet X 2 feet and inner wall & ceiling shall be painted with off white. The flooring shall be with antistatic mat flooring. Shop drawing shall be got approved before starting of the work. | 2.00 | Set |  | 2650000.00 | 5300000.00 | 830781.50 | 1661563.00 | 1661563.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
2.00 | Earth work in surface excavation not exceeding 30 cm in depth but exceeding 1.5 m in width as well as 10 sqm on plan including getting out and disposal of excavated earth upto 50 m and lift upto 1.5 m, as directed by Engineer-in-Charge: All kinds of soil | 6540.00 | Sqm |  | 20.00 | 130800.00 | 135.00 | 882900.00 | 130800.00 | Subhas Malakar
3.00 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth, lead upto 50m and lift upto 1.5m, disposed earth to be levelled and neatly dressed. All kinds of soil | 1405.00 | Cum |  | 160.00 | 224800.00 | 320.00 | 449600.00 | 224800.00 | Subhas Malakar
4.00 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil. | 180.00 | Cum |  | 160.00 | 28800.00 | 575.00 | 103500.00 | 28800.00 | Subhas Malakar
5.00 | Excavating trenches of required width for pipes, cables, etc including excavation for sockets, and dressing of sides, ramming of bottoms, depth upto 1.5 m, including getting out the excavated soil, and then returning the soil as required, in layers not exceeding 20 cm in depth, including consolidating each deposited layer by ramming, watering, etc. and disposing of surplus excavated soil as directed, within a lead of 50 m : All kinds of soil : Pipes, cables etc. exceeding 80 mm dia. but not exceeding 300 mm dia | 275.00 | M |  | 60.00 | 16500.00 | 675.00 | 185625.00 | 16500.00 | Subhas Malakar
6.00 | Extra for every additional lift of 1.5 m or part thereof in excavation /banking excavated or stacked materials. :All kinds of soil. : From 1.5 m to 3.0m | 75.00 | Cum |  | 10.00 | 750.00 | 150.00 | 11250.00 | 750.00 | Subhas Malakar
7.00 | Extra for every additional lift of 1.5 m or part thereof in excavation /banking excavated or stacked materials. :All kinds of soil. : From 3.0 m to 4.5m | 40.00 | Cum |  | 10.00 | 400.00 | 320.00 | 12800.00 | 400.00 | Subhas Malakar
8.00 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m | 5448.00 | Cum |  | 20.00 | 108960.00 | 250.00 | 1362000.00 | 108960.00 | Subhas Malakar
9.00 | Filling of earth brought from outside (excluding rock) in trenches, open areas, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering etc., complete as per the direction of Engineer in Charge. | 1000.00 | Cum |  | 330.00 | 330000.00 | 800.00 | 800000.00 | 330000.00 | Subhas Malakar
10.00 | Supplying and filling in plinth with sand under floors, including watering, ramming, consolidating and dressing complete. | 30.00 | Cum |  | 900.00 | 27000.00 | 2500.00 | 75000.00 | 27000.00 | Subhas Malakar
11.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:4:8 (1 Cement : 4 Sand : 8 graded stone aggregate 40 mm nominal size) | 565.00 | Cum |  | 8200.00 | 4633000.00 | 6400.00 | 3616000.00 | 3616000.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
12.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:2:4 (1 cement : 2 Sand : 4 graded stone aggregate 20 mm nominal size) | 75.00 | Cum |  | 9800.00 | 735000.00 | 10000.00 | 750000.00 | 735000.00 | Subhas Malakar
13.00 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level : 1:1.5:3 (1 cement : 1.5 Sand and: 3 graded stone aggregate 20 mm nominal size). | 175.00 | Cum |  | 11000.00 | 1925000.00 | 9000.00 | 1575000.00 | 1575000.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
14.00 | Centering and shuttering including strutting, propping etc. and removal of form for : Foundations, footings, bases of columns, etc. for mass concrete. | 239.00 | Sqm |  | 300.00 | 71700.00 | 520.00 | 124280.00 | 71700.00 | Subhas Malakar
15.00 | Centering and shuttering including strutting, propping etc. and removal of form for : Suspended floors, roofs, landings, balconies and access platform | 20.00 | Sqm |  | 320.00 | 6400.00 | 940.00 | 18800.00 | 6400.00 | Subhas Malakar
16.00 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level.Thermo-Mechanically Treated bars. | 17500.00 | Kg |  | 76.00 | 1330000.00 | 120.00 | 2100000.00 | 1330000.00 | Subhas Malakar
17.00 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in: Cement mortar 1:6 (1 cement : 6 Sand) | 20.00 | Cum |  | 6500.00 | 130000.00 | 8800.00 | 176000.00 | 130000.00 | Subhas Malakar
18.00 | Providing and laying brick aggregate of 40mm nominal size to the soak pit including all labour and cost of materials etc., complete | 3.00 | Cum |  | 2600.00 | 7800.00 | 2900.00 | 8700.00 | 7800.00 | Subhas Malakar
19.00 | 12 mm cement plaster of mix : 1:4 (1 cement: 4 sand) | 160.00 | Sqm |  | 200.00 | 32000.00 | 950.00 | 152000.00 | 32000.00 | Subhas Malakar
20.00 | Smooth finishing of the exposed surface of R.C.C. work with 6 mm thick cement mortar 1:3 (1 Cement : 3 sand). | 350.00 | Sqm |  | 200.00 | 70000.00 | 350.00 | 122500.00 | 70000.00 | Subhas Malakar
21.00 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | 1195.00 | Kg |  | 110.00 | 131450.00 | 135.00 | 161325.00 | 131450.00 | Subhas Malakar
22.00 | Providing and fixing mild steel round holding down bolts with nuts and washer plates complete. | 73.00 | Kg |  | 100.00 | 7300.00 | 120.00 | 8760.00 | 7300.00 | Subhas Malakar
23.00 | Supplying and fixing C.I. manhole cover with frame of Rectangular or Square or Circular in shape for manholes of suitable size as per the direction of Engineer In Charge | 500.00 | Kg |  | 125.00 | 62500.00 | 115.00 | 57500.00 | 57500.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
24.00 | Providing and laying vitrified floor tiles of antiskid type mat finish in different sizes (thickness to be specified by the manufacturer) with water absorption less than 0.08% and conforming to IS: 15622, of approved make, in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement : 4 sand), jointing with grey cement slurry @ 3.3kg/sqm including grouting the joints with white cement and matching pigments etc., complete. Size of Tile 600x600 mm | 60.00 | Sqm |  | 1700.00 | 102000.00 | 1700.00 | 102000.00 | 102000.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd., Subhas Malakar
25.00 | Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 (thickness to be specified by the manufacturer), of approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. | 30.00 | Sqm |  | 1100.00 | 33000.00 | 1200.00 | 36000.00 | 33000.00 | Subhas Malakar
26.00 | Providing and laying Ceramic glazed floor tiles of size 300x300 mm (thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours such as White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick cement mortar 1:4 (1 Cement : 4 sand), jointing with grey cement slurry @ 3.3kg/sqm including pointing the joints with white cement and matching pigment etc., complete. | 10.00 | Sqm |  | 1100.00 | 11000.00 | 1150.00 | 11500.00 | 11000.00 | Subhas Malakar
27.00 | Providing and laying 60mm thick factory made cement concrete interlocking paver block of M -30 grade made by block making machine with strong vibratory compaction, of approved size, design & shape, laid in required colour and pattern over and including 50mm thick compacted bed of fine sand, filling the joints with fine sand etc. all complete as per the direction of Engineer-in-charge. | 5120.00 | Sqm |  | 1000.00 | 5120000.00 | 1011.00 | 5176320.00 | 5120000.00 | Subhas Malakar
28.00 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, IS : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. Circular tank | 2000.00 | Ltr. |  | 30.00 | 60000.00 | 12.00 | 24000.00 | 24000.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
29.00 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge.Internal work - Exposed on wall 15 mm nominal outer dia Pipes | 30.00 | M |  | 100.00 | 3000.00 | 350.00 | 10500.00 | 3000.00 | Subhas Malakar
30.00 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge.Internal work - Exposed on wall 20 mm nominal outer dia Pipes | 30.00 | M |  | 125.00 | 3750.00 | 410.00 | 12300.00 | 3750.00 | Subhas Malakar
31.00 | Providing and fixing 100/110mm Dia soil, waste and vent pipes of SWR quality including all fittings like bends, Tees, Elbows,collars, junction, inspection doors, cowls, offsets, access pipes, jointing with rubber ring /solvent cement by application of leak proof adhesive like FRP paste including cutting holes in walls and floors and making good, clipping to walls and slabs, trenching, refilling etc., complete | 60.00 | M |  | 600.00 | 36000.00 | 350.00 | 21000.00 | 21000.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
32.00 | Providing and fixing GI pipe of 150mm dia (3mm wall thick) including jointing of pipes & fittings etc, complete in the already excavated trench. | 275.00 | M |  | 800.00 | 220000.00 | 500.00 | 137500.00 | 137500.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
33.00 | Providing and fixing HDPE pipe of 150mm dia including jointing of pipes & fittings etc, complete in the already excavated trench. | 275.00 | M |  | 600.00 | 165000.00 | 1300.00 | 357500.00 | 165000.00 | Subhas Malakar
34.00 | Providing and fixing ball valve (brass) of approved quality, High or low pressure, with plastic floats complete : 20 mm nominal bore | 6.00 | Each |  | 300.00 | 1800.00 | 450.00 | 2700.00 | 1800.00 | Subhas Malakar
35.00 | Providing and fixing white vitreous china pedestal type water closet (European type W.C. pan) with seat and lid, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlled device (handle lever), conforming to IS : 7231, with all fittings and fixtures complete, including cutting and making good the walls and floors wherever required : W.C. pan with ISI marked white solid plastic seat and lid | 2.00 | Each |  | 5500.00 | 11000.00 | 9500.00 | 19000.00 | 11000.00 | Subhas Malakar
36.00 | Providing and fixing wash basin with C.I. brackets, 15 mm C.P. brass pillar taps, 32 mm C.P. brass waste of standard pattern,15mm Connection hose, including painting of fittings and brackets, cutting and making good the walls wherever require:White Vitreous China Wash basin size 550x400 mm with a pair of 15 mm C.P. brass pillar taps | 2.00 | Each |  | 5000.00 | 10000.00 | 4200.00 | 8400.00 | 8400.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
37.00 | Providing and fixing 600x450 mm beveled edge mirror of superior glass (of approved quality) complete with 6 mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | 2.00 | Each |  | 350.00 | 700.00 | 2100.00 | 4200.00 | 700.00 | Subhas Malakar
38.00 | Providing and Fixing of C.P Health faucet of 1.5m length, hand operated spray unit (in stand type) of approved make and as per direction of Engineer-in-Charge. | 2.00 | Each |  | 1200.00 | 2400.00 | 2800.00 | 5600.00 | 2400.00 | Subhas Malakar
39.00 | Providing and fixing white vitreous china flat back or wall corner type urinal basin of size 430mmX260mmX350 and 430mmX260mmX265 sizes respectively with urinal valve of manual type with standrad connecting pipe, C.P brass spreaders with unions and G.I clamps complete, including painting of fittings and brackets, cutting and making good the walls/floors wherever required | 2.00 | Each |  | 3200.00 | 6400.00 | 2100.00 | 4200.00 | 4200.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
40.00 | Providing and fixing PVC floor trap of self cleansing type with or without vent arm and with jali (grating) complete including cutting making good the walls and floor. 110mm inlet X 110mm outlet | 2.00 | Each |  | 100.00 | 200.00 | 2000.00 | 4000.00 | 200.00 | Subhas Malakar
41.00 | Providing and fixing 2 in 1 bib cock of approved make, 15mm nominal bore including necessary screws and fixtures all and as per the direction of Engineer in charge. | 2.00 | Each |  | 1200.00 | 2400.00 | 1500.00 | 3000.00 | 2400.00 | Subhas Malakar
42.00 | Boring/drilling bore well of required dia for casing/strainer pipe,by suitable method prescribed in IS:2800 (Part I) including hire and running charges of all equipments, tools, plants and machineries required for the job, all complete as per direction of Engineer in Charge upto 60m depth below ground level. All type of soil. 150mm Dia | 120.00 | M |  | 230.00 | 27600.00 | 1500.00 | 180000.00 | 27600.00 | Subhas Malakar
43.00 | Supplying,assembling,lowering and fixing in vertical position in bore well unplasticized PVC medium well casing (CM) pipe of required dia, conforming to IS:12818, including hire & labour charges, fittings & accessories etc., all complete for all depths as per the direction of Engineer in Charge. 100mm nominal size dia | 90.00 | M |  | 220.00 | 19800.00 | 900.00 | 81000.00 | 19800.00 | Subhas Malakar
44.00 | Supplying,assembling,lowering and fixing in vertical position in bore well unplasticized PVC medium well screen (RMS) pipes with ribs, conforming to IS:12818, including hire & labour charges, fittings & accessories etc., all complete for all depths as per the direction of Engineer in Charge. 100mm nominal size dia | 30.00 | M |  | 220.00 | 6600.00 | 900.00 | 27000.00 | 6600.00 | Subhas Malakar
45.00 | Gravel Packing in tubewell construction in accordance with Is:4097,including providing gravel fine/medium/coarse in required grading & sizes as per actual requirement, all complete as per direction of Engineer in Charge | 6.00 | Cum |  | 6000.00 | 36000.00 | 2100.00 | 12600.00 | 12600.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
46.00 | Development of tube well in accordance with IS:2800(Part I)and IS:11189 to establish maximum rate of usable water yield without sand content (beyond permissible limit) with required capacity air compressor,running the compressor for required time till well is fully developed etc., all complete, including hire and labour charges of air compressor, tools & accessories etc., all as per requirement and direction of Engineer in Charge | 150.00 | Hour |  | 200.00 | 30000.00 | 1300.00 | 195000.00 | 30000.00 | Subhas Malakar
47.00 | Providing and fixing suitable size threaded mild steel cap or spot welded plate to the top of bore well housing/casing pipe, removable as per requirement, allcomplete for borewell of: 100mm Dia | 2.00 | Each |  | 100.00 | 200.00 | 275.00 | 550.00 | 200.00 | Subhas Malakar
48.00 | Providing and fixing bail plug/Bottom plug of required dia to the bottom of pipe assembly of tubewell as per IS:2800 (Part 1): 100mm Dia | 2.00 | Each |  | 100.00 | 200.00 | 310.00 | 620.00 | 200.00 | Subhas Malakar
49.00 | Taking out existing Cement Concrete interlocking paver blocks from road / footpath/ central verge, including removal of rubbish etc., disposal of unserviceable material to the dumping ground, for which payment shall be made separately and stacking of serviceable material within 50 metre lead as per direction of Engineer-in-Charge. | 1284.20 | Sqm |  | 150.00 | 192630.00 | 125.00 | 160525.00 | 160525.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
50.00 | Laying old cement concrete interlocking paver blocks of any design/ shape laid in required line, level, curvature, colour and pattern over and including 50 mm thick compacted bed of coarse sand, filling the joints with fine sand etc. all complete as per the direction of Engineer-in charge. (Old Cement Concrete paver blocks shall be supplied by the department free of cost). | 522.00 | Sqm |  | 200.00 | 104400.00 | 415.00 | 216630.00 | 104400.00 | Subhas Malakar
51.00 | Preparation and consolidation of sub grade with power road roller of 8 to 12 tonne capacity after excavating earth to an average of 22.5 cm depth, dressing to camber and consolidating with road roller including making good the undulations etc. and re-rolling the sub grade and disposal of surplus earth with lead upto 50 metres. | 2236.00 | Sqm |  | 50.00 | 111800.00 | 210.00 | 469560.00 | 111800.00 | Subhas Malakar
52.00 | Construction of granular sub-base by providing close graded Material conforming to specifications, mixing in a mechanical mix plant at OMC, carriage of mixed material by tippers to work site, for all leads & lifts, spreading in uniform layers of specified thickness with motor grader on prepared surface and compacting with vibratory power roller to achieve the desired density, complete as per specifications and directions of Engineer-in-Charge. With material conforming to Grade-II (size range 53 mm to 0.075 mm ) having CBR Value-25 | 680.00 | Cum |  | 6500.00 | 4420000.00 | 3300.00 | 2244000.00 | 2244000.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
53.00 | Construction of dry lean cement concrete sub base over a prepared sub-grade/sub base with coarse and fine aggregate conforming to IS:383, the size of coarse aggregate not exceeding 25 mm, aggregate cement ratio not to exceed 15:1, aggregate gradation after blending to be as per specifications, cement content not to be less than 150 Kg/cum, optimum moisture content to be determined during trial length construction, concrete strength not to be less than 10 Mpa at 7 days, mixed in a batching plant, transported to site, for all leads & lifts, laid with a mechanical paver, compacting with 8-10 tonne vibratory roller, finishing and curing etc. complete as per direction of Engineer in-charge. | 172.00 | Cum |  | 10500.00 | 1806000.00 | 4500.00 | 774000.00 | 774000.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
54.00 | Providing and laying LDPE sheet of 300micron thickness over the DRLC and overlapping the adjacent sheets of 150mm including labours, other necessary tools etc., as per the direction of Engineer in charge. | 1980.00 | Sqm |  | 50.00 | 99000.00 | 75.00 | 148500.00 | 99000.00 | Subhas Malakar
55.00 | Cement concrete 1:2:4 (1 cement : 2 sand : 4 graded stone aggregate 40 mm nominal size) in pavements, laid to required slope and camber in panels as required including form work, consolidation finishing and tamping complete. | 435.00 | Cum |  | 10300.00 | 4480500.00 | 6000.00 | 2610000.00 | 2610000.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
56.00 | Providing and laying in position bitumen hot sealing compound for expansion joints etc: Using grade 'A' sealing compound. | 500.00 | Cm/Cm/M |  | 10.00 | 5000.00 | 4500.00 | 2250000.00 | 5000.00 | Subhas Malakar
57.00 | SH- II (Electrical Works) Supply of 45 W LED outdoor type street light fitting with all accessories made of high pressure die cast aluminium housing with heat resistance toughened glass & IP 66 protection (minimum) complete as required, suitable to operate on 230V± 10%, 50Hz, Single Phase, AC Supply as per technical specification attached. | 6.00 | Each |  | 900.00 | 5400.00 | 2900.00 | 17400.00 | 5400.00 | Subhas Malakar
58.00 | Supply of 2x18W LED tube light fitting for surface mounting indoor application, IP 20 protection (minimum) complete as required, suitable to operate on 230V± 10%, 50Hz, Single Phase, AC Supply as per technical specification attached. | 16.00 | Each |  | 2500.00 | 40000.00 | 2800.00 | 44800.00 | 40000.00 | Subhas Malakar
59.00 | Supply of 1200 mm sweep ceiling fan ISI marked confirming to IS - 394/1979 specification and BEE 5 star rating suitable to operate on 230V ±, 10% single phase, AC supply along with all accessories except regulator. | 2.00 | Each |  | 3000.00 | 6000.00 | 3700.00 | 7400.00 | 6000.00 | Subhas Malakar
60.00 | Supply of 1.5 TR capacity of inverter Split type indoor wall mounted 5 star (ISEER 2018- minimum 4.5) Air conditioners fitted with suitable compressors and refrigerant including accessories etc conforming to relevant IS as per manufacturer recommendation capable of performing cooling, dehumidifying, air circulating and filtering suitable for operating on 230V± 10%, 50Hz, Single Phase, AC Supply etc. complete as required. | 8.00 | Each |  | 5400.00 | 43200.00 | 62000.00 | 496000.00 | 43200.00 | Subhas Malakar
61.00 | Supply of dual AC controller with seven segment display, protection of AC against under voltage, over voltage, under load and over load, alarm for AC fail, power fail and high temperature and suitable for operating at 230V ± 10%, 50 Hz single phase. | 4.00 | Each |  | 25000.00 | 100000.00 | 21000.00 | 84000.00 | 84000.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
62.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with piano type switch, phenolic laminated sheet, suitable size MS box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. - Group C | 20.00 | Point |  | 1200.00 | 24000.00 | 1300.00 | 26000.00 | 24000.00 | Subhas Malakar
63.00 | Wiring for circuit/submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required - 2x2.5 sq.mm. + 1x2.5 sq.mm. earth wire | 20.00 | M |  | 300.00 | 6000.00 | 150.00 | 3000.00 | 3000.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
64.00 | Supply and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/recessed steel/PVC conduit as required - 3 x 1.5 Sq. mm. | 120.00 | M |  | 380.00 | 45600.00 | 98.00 | 11760.00 | 11760.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
65.00 | Supply and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/recessed steel/PVC conduit as required - 3 x 4.0 Sq.mm. | 120.00 | M |  | 600.00 | 72000.00 | 215.00 | 25800.00 | 25800.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
66.00 | Supplying and fixing of following sizes of steel conduit along with accessorice in surface/recessed including painting in case of surface conduit or cutting the wall and making good the same in case of recessed conduit as required - 20 mm | 120.00 | M |  | 100.00 | 12000.00 | 175.00 | 21000.00 | 12000.00 | Subhas Malakar
67.00 | Supplying and fixing of following sizes of steel conduit along with accessorice in surface/recessed including painting in case of surface conduit or cutting the wall and making good the same in case of recessed conduit as required - 25 mm | 80.00 | M |  | 130.00 | 10400.00 | 155.00 | 12400.00 | 10400.00 | Subhas Malakar
68.00 | Supplying and fixing of following sizes of steel conduit along with accessorice in surface/recessed including painting in case of surface conduit or cutting the wall and making good the same in case of recessed conduit as required - 32 mm | 20.00 | M |  | 180.00 | 3600.00 | 215.00 | 4300.00 | 3600.00 | Subhas Malakar
69.00 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required - 1 or 2 Module (75mm x 75mm) | 4.00 | Each |  | 300.00 | 1200.00 | 99.00 | 396.00 | 396.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
70.00 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required - 3 Module (100mm x 75mm) | 20.00 | Each |  | 400.00 | 8000.00 | 149.00 | 2980.00 | 2980.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
71.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required - 15/16 amps switch | 20.00 | Each |  | 500.00 | 10000.00 | 119.00 | 2380.00 | 2380.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
72.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required - 6 pin 15/16 amps socket outlet | 20.00 | Each |  | 300.00 | 6000.00 | 148.00 | 2960.00 | 2960.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
73.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required - Telephone socket outlet | 4.00 | Each |  | 250.00 | 1000.00 | 83.00 | 332.00 | 332.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
74.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) - 4 way (4 + 12), Double door | 4.00 | Each |  | 9300.00 | 37200.00 | 3700.00 | 14800.00 | 14800.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
75.00 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) - 4 way, Double door | 2.00 | Each |  | 200.00 | 400.00 | 1410.00 | 2820.00 | 400.00 | Subhas Malakar
76.00 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) - 8 way, Double door | 2.00 | Each |  | 1500.00 | 3000.00 | 1605.00 | 3210.00 | 3000.00 | Subhas Malakar
77.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, MCB suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required - Triple pole and neutral | 2.00 | Each |  | 2200.00 | 4400.00 | 1359.00 | 2718.00 | 2718.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
78.00 | Supplying and fixing following rating, 415 volts, C Curve, MCB in the exisiting MCB DB complete with connections, testing and commisioning etc. as required - Triple pole and neutral, 40 Amp. | 2.00 | Each |  | 1200.00 | 2400.00 | 2210.00 | 4420.00 | 2400.00 | Subhas Malakar
79.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, “C” curve, MCB suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required - Single pole | 16.00 | Each |  | 200.00 | 3200.00 | 229.00 | 3664.00 | 3200.00 | Subhas Malakar
80.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, “C” curve, MCB suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required - Double pole | 4.00 | Each |  | 980.00 | 3920.00 | 710.00 | 2840.00 | 2840.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
81.00 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 10.00 | Each |  | 20.00 | 200.00 | 49.00 | 490.00 | 200.00 | Subhas Malakar
82.00 | Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top along with 20 amps "C" curve SP, MCB, in sheet steel enclosure, on surface or in recess with chained metal cover for the socket out let and complete with connections, testing and commisioning etc. as required. | 8.00 | Each |  | 1800.00 | 14400.00 | 1499.00 | 11992.00 | 11992.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
83.00 | Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32 A, 240 V "C" curve SP MCB complete with connections, testing and commissioning etc. as required. | 2.00 | Each |  | 150.00 | 300.00 | 3100.00 | 6200.00 | 300.00 | Subhas Malakar
84.00 | Supply and fixing of Surge protection device (SPD - Type 2/Class B) of Imax 100kA, having protection against direct and indirect lightning surges alongwith 2 Module CRCA sheet steel enclosure including making connection etc., as required as per the site condition. | 4.00 | Each |  | 22000.00 | 88000.00 | 3900.00 | 15600.00 | 15600.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
85.00 | Supplying and fixing two module stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | 2.00 | Each |  | 350.00 | 700.00 | 410.00 | 820.00 | 700.00 | Subhas Malakar
86.00 | ITC of pre-wired, fluorescent fitting /LED fitting/ compact fluorescent fitting of all types, complete with all accessories and tube/lamp etc. directly on ceiling/ wall, including connections with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 16.00 | Each |  | 80.00 | 1280.00 | 390.00 | 6240.00 | 1280.00 | Subhas Malakar
87.00 | ITC of street light fitting with with all types of accessories i/c. providing of GI mounting bracket made of 40mm dia, medium class GI pipe with bend to shape (Approx length of bracket 2 Mtrs.) including 2 Nos. MS clamp 4 Nos SS Nut, bolts and washers, painting of MS part etc. as required as per the site condition. | 6.00 | Each |  | 120.00 | 720.00 | 710.00 | 4260.00 | 720.00 | Subhas Malakar
88.00 | ITC of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable etc. as required. | 2.00 | Each |  | 150.00 | 300.00 | 1615.00 | 3230.00 | 300.00 | Subhas Malakar
89.00 | ITC of 1.5 TR capacity of Split type Inverter Air Conditioner including connecting copper refrigerant piping, drain piping, electrical interconnection between outdoor and indoor units, providing power coated MS stand / concreate base for installation of outdoor unit etc. complete as required a per the site condition. | 8.00 | Each |  | 1000.00 | 8000.00 | 4300.00 | 34400.00 | 8000.00 | Subhas Malakar
90.00 | Supply and fixing of extra copper refrigerant piping for 1.5TR split type Air-conditioner, complete with suction/discharge line, insulation (cunifoam with neoprene/rubber lining), electrical cabling and all the accessories as per site requirement. | 30.00 | M |  | 300.00 | 9000.00 | 2100.00 | 63000.00 | 9000.00 | Subhas Malakar
91.00 | Supply and fixing 12Amp, 170V-270 1Ø Voltage Staibilizer, suitable for 1.5 TR Split AC including interconnection etc. as required as per the site condition. | 8.00 | Each |  | 15000.00 | 120000.00 | 4350.00 | 34800.00 | 34800.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
92.00 | Supply Installation Testing Commissioning of 2 Cross Zone Conventional Fire Alarm Panel with built-in microprocessor based gas release module with wide range of implementation in Gas release Automation system as required as per the site condition. | 2.00 | Job |  | 24000.00 | 48000.00 | 33000.00 | 66000.00 | 48000.00 | Subhas Malakar
93.00 | Supply, installation, testing and commissioning of Optical Smoke Detector with base with the provision of remote LED output, blinking LED, 2 wire, operating DC voltage 10 to 33V, with alarm indicator etc. as required as per the site condition. | 8.00 | Each |  | 21000.00 | 168000.00 | 4200.00 | 33600.00 | 33600.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
94.00 | Supply, installation, testing and commissioning of surface mountable Manual Call point with front protection glass cover, ABS housing with back box, operating voltage 17V to 28V D.C., amber/yellow to indicate a short circuit etc. as required as per the site condition. | 2.00 | Each |  | 2000.00 | 4000.00 | 4200.00 | 8400.00 | 4000.00 | Subhas Malakar
95.00 | Supply, installation, testing and commissioning of Sounder/Hooter with operating voltage 20 to 26V D.C. material made of FR Polymer ABS etc. as required as per the site condition. | 2.00 | Each |  | 19000.00 | 38000.00 | 1200.00 | 2400.00 | 2400.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
96.00 | Supply, installation, testing and commissioning of Auto dialer with totaly microcontroller based system, 2 line, 16 character LCD with backlight, 20 telephone number with speech, telephone number checking facility, key pad access code and etc. as required as per the site condition. | 2.00 | Job |  | 25000.00 | 50000.00 | 107000.00 | 214000.00 | 50000.00 | Subhas Malakar
97.00 | Supply and laying of copper 2x1.5 Sqmm XLPE/PVC insulated 1.1kv steel wire armoured cable with all acessories as required as per the site condition. | 140.00 | M |  | 120.00 | 16800.00 | 99.00 | 13860.00 | 13860.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
98.00 | SITC of 3 HP, 1-Ø, 230V, 50 Hz, AC submersible pump set having capacity of 1000 LPH (minimum) in the existing borewell i/c. jointing of cable, connection of pipes etc. complete as required as per the site requirement. (Approx total depth of borewell 60 mtr ; Head - 50 Mtr.) | 2.00 | Job |  | 27000.00 | 54000.00 | 88000.00 | 176000.00 | 54000.00 | Subhas Malakar
99.00 | Supply & laying of PVC insulated & PVC sheathed 1.1 KV grade 3x x 4 Sq.mm flat copper conductor industrial cable conforming to IS-694 for Submersible Pump Motors alongwith existing GI pipe from pump set to submersible pump control panel including necessary connection/termination and sheddle/clamping with wall surface complete as required as per the site requirement. | 140.00 | M |  | 170.00 | 23800.00 | 299.00 | 41860.00 | 23800.00 | Subhas Malakar
100.00 | Supply & fixing of SS wire rope of 8mm dia. complete with shakles for fixing of pump set during & after lowering to avoid slippage of the same complete as required as per the site requirement. | 100.00 | M |  | 500.00 | 50000.00 | 2000.00 | 200000.00 | 50000.00 | Subhas Malakar
101.00 | SITC of control panel in the sheet steel enclosure suitable for 3 HP submersible pump set including suitable rating 2-P contactor, 2-P relay, DOL starter arrangement alongwith ammeter complete as required as per the site requirement. | 2.00 | Job |  | 4000.00 | 8000.00 | 45000.00 | 90000.00 | 8000.00 | Subhas Malakar
102.00 | Supply, fixing & lowering of 40 mm dia. medium class GI pipe i/c providing & fixing of 6 mm thick GI flange duly welded at both end of pipe complete with rubber packing, nuts and bolts for making water tight arrangement complete as required as per the site requirement. | 120.00 | M |  | 450.00 | 54000.00 | 1900.00 | 228000.00 | 54000.00 | Subhas Malakar
103.00 | Supply & fixing of Non-return valve for the above pump set. | 2.00 | Each |  | 1600.00 | 3200.00 | 9800.00 | 19600.00 | 3200.00 | Subhas Malakar
104.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC / HUME / METAL / HDPE pipe as required a) Upto 35 Sq. mm. | 240.00 | M |  | 60.00 | 14400.00 | 325.00 | 78000.00 | 14400.00 | Subhas Malakar
105.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC / HUME / METAL / HDPE pipe as required b) Above 95 Sq. mm and upto 185 Sq. mm. | 50.00 | M |  | 60.00 | 3000.00 | 1490.00 | 74500.00 | 3000.00 | Subhas Malakar
106.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required a) Upto 35 Sq. mm (clamped with 1 mm thick saddle) | 20.00 | M |  | 200.00 | 4000.00 | 325.00 | 6500.00 | 4000.00 | Subhas Malakar
107.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required a) 3.5 c X 35 Sq. mm. (32 mm) | 6.00 | Set |  | 250.00 | 1500.00 | 175.00 | 1050.00 | 1050.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
108.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required b) 4c X 16 Sq. mm (28 mm) | 8.00 | Set |  | 250.00 | 2000.00 | 325.00 | 2600.00 | 2000.00 | Subhas Malakar
109.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required c) 3c X 16 Sq. mm (25 mm) | 4.00 | Set |  | 400.00 | 1600.00 | 255.00 | 1020.00 | 1020.00 | M/s Sadguru Engineers & Allied Services Pvt. Ltd.
110.00 | Laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part-II complete with fitting and cutting, jointing etc. direct in ground / concreate / all kinds of soil (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. a) 63 mm dia (OD-63mm & ID-51 mm nominal) | 240.00 | M |  | 480.00 | 115200.00 | 1490.00 | 357600.00 | 115200.00 | Subhas Malakar
111.00 | Laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part-II complete with fitting and cutting, jointing etc. direct in ground / concreate / all kinds of soil (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. a) 120 mm dia (OD-120mm & ID-103 mm nominal) | 50.00 | M |  | 400.00 | 20000.00 | 3500.00 | 175000.00 | 20000.00 | Subhas Malakar
| Total in Figures |  |  |  |  | 33809860.00 |  | 32493210.00
Lowest Amount Quoted BY: M/s Sadguru Engineers & Allied Services Pvt. Ltd.(32493210.00)

## BOQ Summary
BOQ Summary Details Tender Title: Installation of new ILS at MBB Airport, Agartala (SH- Construction of Localizer hut and platform including internal electrification and associated work) Tender ID: 2021_AAI_88550_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/s Sadguru Engineers & Allied Services Pvt. Ltd. | 32493210.00 | L1
| 2 | Subhas Malakar | 33809860.00 | L2