## BoQ1
Government eProcurement System Created By: Ravindra singh Mehrok Created Date/Time: 21-Oct-2021 06:00 PM Tender Title: Construction of ATC Tower Cum Technical Block at Civil Aerodrome Vadodara.SH Supply Installation, Testing and Commissioning of 750 KVA DG Sets and Allied works Tender ID: 2021_AAI_88747_1
Tender Inviting Authority: Asst.Gen. Manager(E-E), AAI, CA, Vadodara
Name of Work: Construction of ATC Tower Cum Technical Block at Civil Aerodrome Vadodara. SH: Supply Installation, Testing and Commissioning of 750 KVA DG Sets and Allied works .
Contract No: AAI/BO/E-E/NIT-02/ATC TOWER/DG SETS/2021-22
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION(GSTN-09AOTPS2578C1ZC) |  | RADIANT ELECTRIC CORPORATION(GSTN-23AAFFR0514H1ZP) |  | Power Engineering India Pvt Ltd(GSTN-30AACCC2414P1ZY) |  | Konstelec Engineers Pvt. Ltd.(GSTN-27AAACK2747D1ZS) |  | Choubay And Co.(Agencies) Pvt.Ltd.(GSTN-09AAACC6073E1ZT) |  | Power And Instrumentation Guj Ltd(GSTN-24AACCP4292Q1ZW) |  | Mona Generator Services Pvt. Ltd.(GSTN-07AAFCM4263P1ZZ) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5) |  | Supernova Engineers Ltd(GSTN-24AACCS6758G1Z7) |  | Manish Electricals(GSTN-22ABLPM9012E1ZY) |  | Sabari and Leon Electricals Pvt Ltd(GSTN-33AAGCS9735D2ZA) |  | VIJAYPOWER GENERATORS LIMITED(GSTN-07AAACV0191N1Z4)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Providing, Installing, Testing and Commissioning of ‘Silent Type’ Diesel Generating set alongwith having Prime Power Rating of 750 KVA,3 Phase,50 Hz, 415 V AC System, comprising of Deisel Engine, Alternator, Engine Mounted instrument panel, Sound Attenuated Acoustic and weather proof enclosure as required complete with all other accessories as per specifications and as required. (A) Diesel Engine :- Diesel engine multi cylinder, 4 stroke, water cooled, with engine driven or electrical motor driven radiator, turbo charged - after / inter cooled with charged air cooling, vaccume indicator, lube oil system, electronic governor, electric start, of suitable BHP at 1500 RPM for above output of alternator at 46 Degree C, and conforming to BS 5514, BS 649, IS 10000. The engine shall be fitted with all required accessories as per specifications. (B) Alternator :- Synchronous alternator rated at 750 KVA, 415 V at 1500 RPM, 3 phase, 50 Hz, AC supply with 0.8 lagging power factor at 46 Degree C. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self-regulated through AVR/DVR conforming to IS: 4722/BS 2613 suitable for tropical conditions and with class-H insulation. (C ) Other Accessories/Equipment :- i) Engine mounted Instrument panel with mocroprocessor based fully integrated generating set controller (PCC 3.3 / WOODWARD / DEIF or equivalent) having digital display & Control devices for safety and monitoring alongwith indicators as required as per specifications. ii) Both Engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on a suitable cement concrete foundation and spring type vibration isolation arrangement as per recommendation of manufacturer. iii) Calibrated Day storage tank for 990 ltr capacity fabricated with 3 mm thick MS sheet complete with flanged inlet & outlet, overflow, drain, vent, high & low level indicator, 450 mm dia Access hole on top with cover and alarm contacts with C' class MS piping system etc. complete as per site requirement. iv) Residential / Hospital type silencer, SS braided rubber expansion bellows/ joints, exhaust piping upto silencer etc. as required. v) Necessary batteries (minimum 2 nos of 180 AH capacity each) complete with leads, charger and battery stand etc. vi) Terminal Arrangement suitable for 1600 A aluminium Busduct connections, initial charging of lubricants, coolants etc. All the above (except Day Oil tank) housed in an Accoustic and weather proof enclosure of thickness not less than 16 SWG CRCA sheet steel with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air into the atmosphere complying to CPCB norms etc. complete as required. Diesel Generating set (750 KVA) as described above. | 2.00 | Set |  | 4750000.00 | 9500000.00 | 5160500.00 | 10321000.00 | 5303099.00 | 10606198.00 | 4184725.00 | 8369450.00 | 6000000.00 | 12000000.00 | 5159853.00 | 10319706.00 | 5088393.20 | 10176786.40 | 6125000.00 | 12250000.00 | 5150000.00 | 10300000.00 | 3985000.00 | 7970000.00 | 5000000.00 | 10000000.00 | 5118000.00 | 10236000.00 | 7970000.00 | Manish Electricals
2.00 | Providing and fixing in position exhaust pipe of following dia welded black MS pipe conforming to IS: 3589 cut to required lengths and installed with necessary bends, supports and clamps, anti-vibration mounting, SS braided Rubber expansion bellows, insulation of exhaust system with 50 mm thick mineral wool/ Rockwool of density not less than 120 kg/ cu. m, covered with 0.8 mm thick Aluminium cladding etc. as required. a) 300 mm dia (5.2 mm thick) | 100.00 | Mtr |  | 10500.00 | 1050000.00 | 5750.00 | 575000.00 | 13592.00 | 1359200.00 | 14450.00 | 1445000.00 | 5000.00 | 500000.00 | 5933.00 | 593300.00 | 5373.50 | 537350.00 | 7500.00 | 750000.00 | 5000.00 | 500000.00 | 1650.00 | 165000.00 | 12000.00 | 1200000.00 | 5892.00 | 589200.00 | 165000.00 | Manish Electricals
3.00 | Providing & fixing of MS support structure for exhaust fume pipes from DG Sets (Exhaust pipe to be measured and paid for separately) along horizontal and vertical runs upto the height (as per CPCB norms) including cutting, welding etc. and applying red oxide primer and two coats of synthetic enamelled paint of colour and shade as directed by Engineer-in-charge. The design of the support structure shall be done by the contractor & get the approval from Engineer-in-charge before execution etc. as required. | 8000.00 | Kg |  | 80.00 | 640000.00 | 130.00 | 1040000.00 | 162.00 | 1296000.00 | 110.00 | 880000.00 | 100.00 | 800000.00 | 104.00 | 832000.00 | 76.00 | 608000.00 | 135.00 | 1080000.00 | 110.00 | 880000.00 | 108.00 | 864000.00 | 125.00 | 1000000.00 | 120.00 | 960000.00 | 608000.00 | Mona Generator Services Pvt. Ltd.
4.00 | Fabricating, Supply, Installing, Testing & Commissioning of Automatic Mains Failure (AMF) panel suitable for 750 KVA silent type DG set complete with relays, timers, set of CTs for metering & protection and energy analyser to indicate currents, phase and line voltages, frequency, power factor, KWH, KVARH & provision for overload, short circuit, restricted earth fault, under frequency, control cabling from AMF panel to diesel engine and elsewhere if required, all complete and inter locking including the following facilities:- a) 1 Nos. of 1600 A 4 pole Electricaly operated drawout type ACB with Ics=Icu=Icw 50kA having Microprocessor based releases for O/L, S/C & E/F . b) To receive 1600 A Al. bus duct for incoming and outgoing power. c) Energy analyser unit to indicate current, voltage, frequency ,power factor and KWH etc. d) Indicating lamps for load on mains and load on set. e) Fuse / MCBs for instruments. f) Battery charger, complete with transformer/ rectifier, D.C. voltmeter and ammeter, selector switch for trickle, off and boost and current adjustment. g) Main supply failure monitor, supply failure timer and restoration timer. h) Control unit with three impulse automatic engine start/stop and failure to start lockout. i) ON/OFF/Control circuit switch with indicator. j) Audio/Video annunciation for High water temperature, Low lubricating oil pressure, Engine over speed, Engine fails to start, Full load/maximum load warning. | 2.00 | Set |  | 700000.00 | 1400000.00 | 435500.00 | 871000.00 | 446812.00 | 893624.00 | 882782.00 | 1765564.00 | 450000.00 | 900000.00 | 383729.00 | 767458.00 | 280000.65 | 560001.30 | 425000.00 | 850000.00 | 325000.00 | 650000.00 | 2190000.00 | 4380000.00 | 500000.00 | 1000000.00 | 615000.00 | 1230000.00 | 560001.30 | Mona Generator Services Pvt. Ltd.
| Total in Figures |  |  |  |  | 12590000.00 |  | 12807000.00 |  | 14155022.00 |  | 12460014.00 |  | 14200000.00 |  | 12512464.00 |  | 11882137.70 |  | 14930000.00 |  | 12330000.00 |  | 13379000.00 |  | 13200000.00 |  | 13015200.00
Lowest Amount Quoted BY: Mona Generator Services Pvt. Ltd.(11882137.70)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of ATC Tower Cum Technical Block at Civil Aerodrome Vadodara.SH Supply Installation, Testing and Commissioning of 750 KVA DG Sets and Allied works Tender ID: 2021_AAI_88747_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Mona Generator Services Pvt. Ltd. | 11882137.70 | L1
| 2 | Supernova Engineers Ltd | 12330000.00 | L2
| 3 | Konstelec Engineers Pvt. Ltd. | 12460014.00 | L3
| 4 | Power And Instrumentation Guj Ltd | 12512464.00 | L4
| 5 | PRAGYA ELECTRIC AND ELECTRONICS CORPORATION | 12590000.00 | L5
| 6 | RADIANT ELECTRIC CORPORATION | 12807000.00 | L6
| 7 | VIJAYPOWER GENERATORS LIMITED | 13015200.00 | L7
| 8 | Sabari and Leon Electricals Pvt Ltd | 13200000.00 | L8
| 9 | Manish Electricals | 13379000.00 | L9
| 10 | Power Engineering India Pvt Ltd | 14155022.00 | L10
| 11 | Choubay And Co.(Agencies) Pvt.Ltd. | 14200000.00 | L11
| 12 | Awasthi Electric Works | 14930000.00 | L12