## BoQ1
Government eProcurement System Created By: KAMBLE TANAJI Created Date/Time: 13-Oct-2021 11:52 AM Tender Title: Strengthening of power supply Tender ID: 2021_AAI_89389_1
Tender Inviting Authority: Asst. General Manager (Engg-Elect), Pune Airport
Name of Work: Strengthening of power supply system and modification of existing LT panels at Pune Airport (SH- Provision of Active Harmonic Filter, replacement of APFC, LTACB)
Contract No: 2021_AAI_89389_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | P2 Power Solutions Pvt ltd(GSTN-09AAECP0915G2ZK) |  | Standard Capacitors(GSTN-07AAGPG3069D1Z0)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, fabrication, factory assembling, factory testing, supply, installation, site testing, commissioning of 3-phase 415V 4-wire hybrid APFC panel 250kVAR passive bank with 100A Active Harmonic Filter as per detailed technical specification including dismantling of existing APFC panel and shifting it suitable location as decided by E-I-C, disconnection, reconnection of existing cable, earth connection from nearest earth strip, re-orientation of existing cable, any minor civil work etc. complete as required as per the site conditions. (Make: Schneider, EPCOS TDK, L&T or equivalent) | 2.00 | Each |  | 845000.00 | 1690000.00 | 1029250.00 | 2058500.00 | 1690000.00 | P2 Power Solutions Pvt ltd
2.00 | Supply installation testing commissioning of 4-pole 415V ACB, In= 2500A, Isc=65kA for 1sec with all its accessories like shunt open release, shunt closing release, close/open auxiliary contacts, sectioning crank etc. The item shall be executed by OEM/OEM's autorised dealer. It shall include dismantling of existing ACB and shifting it to AAI store as decided by E-I-C, loading unloading of new ACB etc. complete as required. Testing of ACB shall be as per OEM's standard practice. (Make: ABB, model E3N 2500 PR122/P-LSIG or any suitable ACB of approved make of AAI with required modifications) | 1.00 | Each |  | 210000.00 | 210000.00 | 212570.00 | 212570.00 | 210000.00 | P2 Power Solutions Pvt ltd
3.00 | Supply installation testing commissioning of Surge Protection Device (SPD) of type 2 /class-II, 4-module, 3-ph, 415V of discharge current (8/20µs) In=20kA and Imax= 40kA as per technical specification suitable for protection against lightning, switching surges etc. including providing anf fixing 35mm DIN rail, suitable size copper cabling, lugs, glands, termination etc. comoplete as required at suitable location within the existing panel compartment as directed by E-I-C. (Make: Dehn, model: VT2 M TT 320 FM or equivalent) | 3.00 | Each |  | 2500.00 | 7500.00 | 4600.00 | 13800.00 | 7500.00 | P2 Power Solutions Pvt ltd
4.00 | Supply of 50kVAR 3-ph 415V 50Hz MPP dielectric low loss capacitor with discharge resistor as per technical specification of suitable size to replace the capacitor in existing APFC panel. | 2.00 | Each |  | 9000.00 | 18000.00 | 11500.00 | 23000.00 | 18000.00 | P2 Power Solutions Pvt ltd
5.00 | Supply of 63A semiconductor fuse of suitable size for existing APFC panel | 17.00 | Each |  | 1000.00 | 17000.00 | 517.00 | 8789.00 | 8789.00 | Standard Capacitors
6.00 | Supply of 125A semiconductor fuse of suitable size for existing APFC panel. | 2.00 | Each |  | 1500.00 | 3000.00 | 862.00 | 1724.00 | 1724.00 | Standard Capacitors
7.00 | Buy Back of old 250kVAR APFC panel with all its accessories like switchgear, capacitor, reactor, thyristor etc. but excluding incoming cable as dismantled at BOQ item no.-01. | 2.00 | Each |  | 0.00 | 0.00 | 25000.00 | -50000.00 | -50000.00 | Standard Capacitors
| Total in Figures |  |  |  |  | 1945500.00 |  | 2268383.00
Lowest Amount Quoted BY: P2 Power Solutions Pvt ltd(1945500.00)

## BOQ Summary
BOQ Summary Details Tender Title: Strengthening of power supply Tender ID: 2021_AAI_89389_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | P2 Power Solutions Pvt ltd | 1945500.00 | L1
| 2 | Standard Capacitors | 2268383.00 | L2