## BoQ1
Government eProcurement System Created By: Sanjib Kumar Dey Created Date/Time: 11-Jan-2022 01:57 PM Tender Title: Miscellaneous Electrical Works. (SH Provision of Electrical Installation and Renovation of Hostel Building and Garage at FSTC, Narayanpur) Tender ID: 2021_AAI_93758_1
Tender Inviting Authority: AGM (E-E), AAI, RHQ,ER
Name of Work: Miscelleneous Electrical Works. SH.: (Provision of Electrical Installations & renovation of Hostel Building & Garrage at FSTC, Narayanpur)
Contract No: AAI/ER/KOL/EE/NIT-03/2021-22
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Youngmen Traders(GSTN-19AEIPB6323B1ZZ) |  | M/s. Das Electricals(GSTN-19AFOPD0681F1ZG) |  | Kundu Enterprise(GSTN-NA) |  | ALFA DEAL PRIVATE LIMITED(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of Submersible Pump of 5 HP capacity alongwith suitable rating starter to deliver 400 Cum per Hr at 34 Mtr. head etc. as complete set. Make KSB model MR 5C A- 60-50-34 or equivalent as per AAI approved make. Installation testing and commissioning of borewell submersible pump, suitable for operation on 415 volt ±10%, 3 phase, 50 Hz A.C. supply, including necessary length power cable of suitable size (approx 20 Mtr. length) and suitable length alongwith the G.I. Guy wire for lifting and lower of the same as per OEM Recommendation, indoor type DOL starter of required rating (M.S. Fabricated in cubicle box). | 2.00 | Job |  | 28000.00 | 56000.00 | 32000.00 | 64000.00 | 48000.00 | 96000.00 | 49501.00 | 99002.00 | 56000.00 | Youngmen Traders
2.00 | Supplyof Vertical monobloc submersible dewatering pumps of 1.5-1.75 HP to deliver 130-300 Cum per Hr at 10 Mtr. head etc. as complete set. Make KSB model AMA PORTER 503 SE or equivalent as per AAI approved make. Installation testing and commissioning of borewell submersible pump, suitable for operation on 240 volt ±10%, 1 phase, 50 Hz A.C. supply, including necessary submersible power cable of suitable size (approx 20 Mtr. length) alongwith the G.I. Guy wire for lifting and lower of the same as per OEM Recommendation, indoor type DOL starter of required rating (M.S. Fabricated in cubicle pattern) | 1.00 | Job |  | 32000.00 | 32000.00 | 33000.00 | 33000.00 | 28000.00 | 28000.00 | 70031.00 | 70031.00 | 28000.00 | Kundu Enterprise
3.00 | Supply of following size 1.1 kv grade, XLPE insulated and PVC inner sheathed Aluminum conductor armored power cable conforming to IS: 7098(Part 1)1988/ IS: 7098 (Part 1) with up to date amendments etc. complete as required
3.10 | 4 x 16 Sq. mm. | 450.00 | Meter |  | 140.00 | 63000.00 | 150.00 | 67500.00 | 125.00 | 56250.00 | 148.00 | 66600.00 | 56250.00 | Kundu Enterprise
4.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
4.10 | Upto 35 sq. mm | 20.00 | Meter |  | 300.00 | 6000.00 | 200.00 | 4000.00 | 298.00 | 5960.00 | 173.00 | 3460.00 | 3460.00 | ALFA DEAL PRIVATE LIMITED
5.00 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required.
5.10 | Upto 35 sq. mm | 20.00 | Meter |  | 98.00 | 1960.00 | 70.00 | 1400.00 | 352.00 | 7040.00 | 173.00 | 3460.00 | 1400.00 | M/s. Das Electricals
6.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
6.10 | Upto 35 sq. mm | 30.00 | Meter |  | 35.00 | 1050.00 | 3.00 | 90.00 | 40.00 | 1200.00 | 58.00 | 1740.00 | 90.00 | M/s. Das Electricals
7.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
7.10 | Upto 35 sq. mm | 10.00 | Meter |  | 22.00 | 220.00 | 4.00 | 40.00 | 40.00 | 400.00 | 46.00 | 460.00 | 40.00 | M/s. Das Electricals
7.20 | Above 35 sq. mm and upto 95 sq. mm | 15.00 | Meter |  | 35.00 | 525.00 | 19.00 | 285.00 | 50.00 | 750.00 | 127.00 | 1905.00 | 285.00 | M/s. Das Electricals
8.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
8.10 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 350.00 | Meter |  | 40.00 | 14000.00 | 16.00 | 5600.00 | 61.00 | 21350.00 | 63.00 | 22050.00 | 5600.00 | M/s. Das Electricals
8.20 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 20.00 | Meter |  | 57.00 | 1140.00 | 30.00 | 600.00 | 63.00 | 1260.00 | 155.00 | 3100.00 | 600.00 | M/s. Das Electricals
9.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.10 | 4 X 16 sq. mm (28mm) | 6.00 | Each |  | 192.00 | 1152.00 | 150.00 | 900.00 | 160.00 | 960.00 | 543.00 | 3258.00 | 900.00 | M/s. Das Electricals
9.20 | 3½ X 35 sq. mm (32mm) | 4.00 | Each |  | 195.00 | 780.00 | 200.00 | 800.00 | 190.00 | 760.00 | 940.00 | 3760.00 | 760.00 | Kundu Enterprise
10.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 20.00 | Each |  | 940.00 | 18800.00 | 800.00 | 16000.00 | 1400.00 | 28000.00 | 671.00 | 13420.00 | 13420.00 | ALFA DEAL PRIVATE LIMITED
11.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 10.00 | Each |  | 580.00 | 5800.00 | 500.00 | 5000.00 | 1440.00 | 14400.00 | 554.00 | 5540.00 | 5000.00 | M/s. Das Electricals
12.00 | Wiring for light / power plug with 2x4 sq mm FRLSH PVC insulated copper conductor single core cable in surface/recessed steel conduit alongwith 1 No 4 sq.mm FRLSH PVC insulated copper conductor single core cable for loop earthing as required. | 120.00 | Meter |  | 120.00 | 14400.00 | 175.00 | 21000.00 | 295.00 | 35400.00 | 147.00 | 17640.00 | 14400.00 | Youngmen Traders
13.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLSH PVC insulated copper conductor, single core cable in surface/recessed steel conduit as required.
13.10 | 2 x 1.5 sq. mm + 1 x 1.5 sq. mm earth wire | 210.00 | Meter |  | 140.00 | 29400.00 | 181.00 | 38010.00 | 240.00 | 50400.00 | 61.00 | 12810.00 | 12810.00 | ALFA DEAL PRIVATE LIMITED
13.20 | 2 x 2.5 sq. mm + 1 x 2.5 sq. mm earth wire | 70.00 | Meter |  | 160.00 | 11200.00 | 180.00 | 12600.00 | 265.00 | 18550.00 | 98.00 | 6860.00 | 6860.00 | ALFA DEAL PRIVATE LIMITED
14.00 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required | 10.00 | Each |  | 9.00 | 90.00 | 18.00 | 180.00 | 29.00 | 290.00 | 24.00 | 240.00 | 90.00 | Youngmen Traders
15.00 | Supply of 36 Watt Surface / recessed mounted LED luminaires with efficacy >100 lumen/watt (600mm x 600mm) constructed of CRCA sheet metal with premium epoxy white powder coating complete for Glare free uniform illumination with longer life suitable for 230V, 50 Hz power supply (Make: Havells , Cat No.VENUSNEOHE2X2R36WLED840PI or equivalent make conforming to tender technical specifications. ) | 18.00 | Each |  | 3200.00 | 57600.00 | 3000.00 | 54000.00 | 2600.00 | 46800.00 | 2452.00 | 44136.00 | 44136.00 | ALFA DEAL PRIVATE LIMITED
16.00 | Supply of LED High Bay light of innovative die-cast Aluminum/Magensium Alloy IP65 light fixture having efficacy > 110 lumen/watt and High efficiency long life minimum CCT of 5000 to 6500K i/c necessary electronic driver, high power LED lamp suitable to operate on 230V ac power supply with connector etc as per tender specifications complete as required.
16.10 | 40 Watt LED High Bay Light ( Havells : STUPEWGP40WLED757SSYMTOPCGRY or Equivalent under AAI Approved Make) | 16.00 | Each |  | 2000.00 | 32000.00 | 2100.00 | 33600.00 | 1800.00 | 28800.00 | 1698.00 | 27168.00 | 27168.00 | ALFA DEAL PRIVATE LIMITED
17.00 | Supply of 18 Watt recessed mounted LED luminaires with efficacy >100 lumen/watt constructed of CRCA sheet metal with premium epoxy white powder coating complete for Glare free uniform illumination with longer life suitable for 230V, 50 Hz power supply (Make: Havells , Cat No.EDGEPRORDDLR18WLED840S or Equivalent). | 15.00 | Each |  | 950.00 | 14250.00 | 1150.00 | 17250.00 | 1800.00 | 27000.00 | 1194.00 | 17910.00 | 14250.00 | Youngmen Traders
18.00 | Installation, Testing, Commissioning of high/ medium bay light fittings of all sizes and shapes complete with all accessories including connections etc. as required. | 15.00 | Each |  | 95.00 | 1425.00 | 175.00 | 2625.00 | 110.00 | 1650.00 | 173.00 | 2595.00 | 1425.00 | Youngmen Traders
19.00 | Installation ,Testing, Commissioning of wall bracket /ceiling fittings of all sizes and shapes containing upto two GLS/CFL/LED lamps per fitting, complete with all accessories including connections etc. as required. | 15.00 | Each |  | 48.00 | 720.00 | 82.00 | 1230.00 | 50.00 | 750.00 | 184.00 | 2760.00 | 720.00 | Youngmen Traders
20.00 | Supply of 1200mm sweep ceiling fan suitable for operation at 230 ± 10 V, 50HZ AC supply with all its accessories. The supplied fan should be BEE-5 star rated (Make: Havells ES NEO or equivalent as per the approved make list.) | 15.00 | Each |  | 1750.00 | 26250.00 | 1700.00 | 25500.00 | 3200.00 | 48000.00 | 3114.00 | 46710.00 | 25500.00 | M/s. Das Electricals
21.00 | Installation, testing and commissioning of ceiling fan, including down rods of standard length (upto 30 cm) with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable etc. as required | 10.00 | Each |  | 95.00 | 950.00 | 100.00 | 1000.00 | 65.00 | 650.00 | 173.00 | 1730.00 | 650.00 | Kundu Enterprise
22.00 | Supply of 300 mm sweep Exhaust fan with metallic body suitable for operation at 230 ± 10 V, 50Hz AC supply with all its accessories. (Make: Havells Ventil Air - DB or equivalent as per the approved make list.) | 6.00 | Each |  | 1550.00 | 9300.00 | 1600.00 | 9600.00 | 2600.00 | 15600.00 | 2276.00 | 13656.00 | 9300.00 | Youngmen Traders
23.00 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. Upto 450 mm sweep | 5.00 | Each |  | 248.00 | 1240.00 | 200.00 | 1000.00 | 90.00 | 450.00 | 173.00 | 865.00 | 450.00 | Kundu Enterprise
24.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 4.00 | Each |  | 4400.00 | 17600.00 | 4100.00 | 16400.00 | 3440.00 | 13760.00 | 13631.00 | 54524.00 | 13760.00 | Kundu Enterprise
25.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Each |  | 6200.00 | 24800.00 | 5000.00 | 20000.00 | 12500.00 | 50000.00 | 10038.00 | 40152.00 | 20000.00 | M/s. Das Electricals
26.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 30.00 | Meter |  | 98.00 | 2940.00 | 120.00 | 3600.00 | 94.00 | 2820.00 | 181.00 | 5430.00 | 2820.00 | Kundu Enterprise
27.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 20.00 | Meter |  | 175.00 | 3500.00 | 200.00 | 4000.00 | 92.00 | 1840.00 | 169.00 | 3380.00 | 1840.00 | Kundu Enterprise
28.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 35.00 | Meter |  | 40.00 | 1400.00 | 20.00 | 700.00 | 33.00 | 1155.00 | 23.00 | 805.00 | 700.00 | M/s. Das Electricals
29.00 | Supplying and fixing of following ways surface/ recessmounting, vertical loadline DB type, 415 V, TPN MCB distribution board ofsheet steel, dust protected, duly powder painted, inclusive of200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer ) as required .
29.10 | 4 way (4 + 12), Double door | 1.00 | Each |  | 2400.00 | 2400.00 | 8000.00 | 8000.00 | 8000.00 | 8000.00 | 1104.00 | 1104.00 | 1104.00 | ALFA DEAL PRIVATE LIMITED
29.20 | 8 way (4 + 24), Double door | 2.00 | Each |  | 3200.00 | 6400.00 | 10769.00 | 21538.00 | 10500.00 | 21000.00 | 1379.00 | 2758.00 | 2758.00 | ALFA DEAL PRIVATE LIMITED
29.30 | 12 way (4 + 36), Double door | 1.00 | Each |  | 4800.00 | 4800.00 | 14988.00 | 14988.00 | 14400.00 | 14400.00 | 1670.00 | 1670.00 | 1670.00 | ALFA DEAL PRIVATE LIMITED
30.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
30.10 | Single pole | 35.00 | Each |  | 145.00 | 5075.00 | 180.00 | 6300.00 | 180.00 | 6300.00 | 194.00 | 6790.00 | 5075.00 | Youngmen Traders
30.20 | Double pole | 2.00 | Each |  | 270.00 | 540.00 | 575.00 | 1150.00 | 800.00 | 1600.00 | 528.00 | 1056.00 | 540.00 | Youngmen Traders
30.30 | Triple pole | 4.00 | Each |  | 460.00 | 1840.00 | 900.00 | 3600.00 | 1200.00 | 4800.00 | 851.00 | 3404.00 | 1840.00 | Youngmen Traders
30.40 | Triple pole and neutral | 4.00 | Each |  | 570.00 | 2280.00 | 1200.00 | 4800.00 | 1500.00 | 6000.00 | 965.00 | 3860.00 | 2280.00 | Youngmen Traders
31.00 | Providing and fixing following rating and breaking capacity and pole MCCB with thermomagnetic release and terminal spreaders in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
31.10 | 63 A, 25 KA,TP MCCB | 2.00 | Each |  | 4650.00 | 9300.00 | 6555.00 | 13110.00 | 3200.00 | 6400.00 | 4559.00 | 9118.00 | 6400.00 | Kundu Enterprise
31.20 | 100 A, 25 KA,TP MCCB | 1.00 | Each |  | 5300.00 | 5300.00 | 5555.00 | 5555.00 | 3800.00 | 3800.00 | 4559.00 | 4559.00 | 3800.00 | Kundu Enterprise
32.00 | Supplying and fixing of TPN MCB distribution board in weather proof cabinet with IP 65 protection on wall or recessed surface as per the site requirement. 8 Module | 1.00 | Each |  | 1650.00 | 1650.00 | 2000.00 | 2000.00 | 300.00 | 300.00 | 1846.00 | 1846.00 | 300.00 | Kundu Enterprise
33.00 | Supply of 1 Phase, 1.0 TR split type of 5 star rating Inverter type Air-conditioners along with high wall type indoor unit suitable to operate from 230±10%, 50 Hz, 1 phase power supply (along with necessary wiring from nearest power source to the required outdoor and indoor units) having high EER Compressor with Indoor & Outdoor Copper coil refrrigeration having aluminum fins firmly bonded to copper tubes assembled in zinc coated steel frame with Eco friendly R 32 or equivalent Refregiration Gas alongwith copper conductor PVC insulated PVC sheathed multicore power cable from indoor to outdoor unit. The indoor unit should have real time clock, operating facility from cordless remote, along with time and temperature display. Outdoor unit to be installed as Directed by Engineer-in-Charge. | 4.00 | Each |  | 33000.00 | 132000.00 | 46700.00 | 186800.00 | 52000.00 | 208000.00 | 53897.00 | 215588.00 | 132000.00 | Youngmen Traders
34.00 | Supply and fixing of extra copper refrigerant piping complete with suction / liquid line, insulation (i.e. cunifoam with neoprene / rubber lining), and all the accessories i/c Control Cable as per site requirement as directed by Engineer-in-Charge.
34.10 | Suitable for 1 TR Split Inverter AC along with its Control Cable | 15.00 | Meter |  | 450.00 | 6750.00 | 850.00 | 12750.00 | 725.00 | 10875.00 | 1445.00 | 21675.00 | 6750.00 | Youngmen Traders
35.00 | ITC of the following TR split type of Inverter Air-conditioners along with Outdoor/ Indoor unit suitable to operate on 1 Phase Power supply.
35.10 | 1 TR Split Inverter AC | 4.00 | Each |  | 400.00 | 1600.00 | 1600.00 | 6400.00 | 380.00 | 1520.00 | 4025.00 | 16100.00 | 1520.00 | Kundu Enterprise
36.00 | Supply and laying of 25 mm dia PVC pipe to be used for drainage of condensate from indoor units to the nearest drain-port as directed by Engineer-in-Charge. | 20.00 | Meter |  | 32.00 | 640.00 | 150.00 | 3000.00 | 265.00 | 5300.00 | 54.00 | 1080.00 | 640.00 | Youngmen Traders
37.00 | Providing, Laying, jointing, testing and commissioning of following C class heavy duty MS Pipe IS 1239 direct in ground with accessories like tees, elbow, flanged joints, reducers complete with painting, wrapping and coating of the pipes as per IS: 10211 in all kings of soil including bitumen/Paver block at a appropriate depth as required including excavation, refilling and making good the trench, civil works etc. complete as required.
37.10 | 80 mm | 10.00 | Meter |  | 1250.00 | 12500.00 | 700.00 | 7000.00 | 1200.00 | 12000.00 | 916.00 | 9160.00 | 7000.00 | M/s. Das Electricals
37.20 | 150 mm | 30.00 | Meter |  | 1650.00 | 49500.00 | 2000.00 | 60000.00 | 2000.00 | 60000.00 | 1878.00 | 56340.00 | 49500.00 | Youngmen Traders
38.00 | Laying, testing and commissioning of Dismantled 150mm MS Pipe in item no.- 40 direct in ground with accessories like tees, elbow, flanged joints, reducers complete with painting, wrapping and coating of the pipes as per IS: 10211 wherever required in all kinds of soil including bitumen/Paver block at a appropriate depth as required including excavation, refilling and making good the trench, civil works etc. complete as required. | 35.00 | Meter |  | 175.00 | 6125.00 | 159.00 | 5565.00 | 300.00 | 10500.00 | 201.00 | 7035.00 | 5565.00 | M/s. Das Electricals
39.00 | Providing and fixing MS channel/angle iron support including cutting, welding and painting of one coat primer and two or more coat synthetic enamel paint for support of 80/150 mm dia MS pipe as required. | 15.00 | Meter |  | 590.00 | 8850.00 | 972.00 | 14580.00 | 500.00 | 7500.00 | 565.00 | 8475.00 | 7500.00 | Kundu Enterprise
40.00 | Dismantling of the existing fire Hydrant on surface or in ground by removing the MS angle support, 150mm MS Pipe and keeping intact the pipe for reuse or as per the directions of the EIC. | 35.00 | Meter |  | 185.00 | 6475.00 | 150.00 | 5250.00 | 625.00 | 21875.00 | 288.00 | 10080.00 | 5250.00 | M/s. Das Electricals
41.00 | Excavation for cable trenches/trench for pipe laying in soft soil, depth upto 1.2 m including dressing of sides lift upto 1.5 m, including getting out the excavated soil, refilling with sand and or good soil after laying of cable/ pipe etc in layers of 20 cm, ramming, watering and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 4.00 | Cum |  | 480.00 | 1920.00 | 579.00 | 2316.00 | 800.00 | 3200.00 | 633.00 | 2532.00 | 1920.00 | Youngmen Traders
42.00 | Cutting of paved surface (flexible/ rigid) for laying of Hume Pipes/ GI/ HDPE pipe upto 150 mm at a depth of atleast 450 mm width including making the surface good with cement concrete (1:2:4)complete as required. | 3.00 | Cum |  | 1250.00 | 3750.00 | 600.00 | 1800.00 | 1800.00 | 5400.00 | 518.00 | 1554.00 | 1554.00 | ALFA DEAL PRIVATE LIMITED
43.00 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings as required excluding excavation and refilling. 50 mm | 15.00 | Meter |  | 550.00 | 8250.00 | 500.00 | 7500.00 | 460.00 | 6900.00 | 476.00 | 7140.00 | 6900.00 | Kundu Enterprise
44.00 | Supply of 225/230mm sweep Exhaust fan with metallic body suitable for operation at 230 ± 10 V, 50Hz AC supply with all its accessories. (Make: Havells Ventil Air - DB or equivalent as per the approved make list.) | 5.00 | Each |  | 1600.00 | 8000.00 | 1600.00 | 8000.00 | 2800.00 | 14000.00 | 2276.00 | 11380.00 | 8000.00 | Youngmen Traders, M/s. Das Electricals
| Total in Figures |  |  |  |  | 737437.00 |  | 863512.00 |  | 1045915.00 |  | 1001461.00
Lowest Amount Quoted BY: Youngmen Traders(737437.00)

## BOQ Summary
BOQ Summary Details Tender Title: Miscellaneous Electrical Works. (SH Provision of Electrical Installation and Renovation of Hostel Building and Garage at FSTC, Narayanpur) Tender ID: 2021_AAI_93758_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Youngmen Traders | 737437.00 | L1
| 2 | M/s. Das Electricals | 863512.00 | L2
| 3 | ALFA DEAL PRIVATE LIMITED | 1001461.00 | L3
| 4 | Kundu Enterprise | 1045915.00 | L4