## BoQ1
Government eProcurement System Created By: GUNDA SHIVA KUMAR Created Date/Time: 09-Dec-2021 04:44 PM Tender Title: Provision of Turn Pad and fillets for link taxi track for operation of B777-300ER type of aircraft at Coimbatore International Airport. SH. Electrical Works. Tender ID: 2021_AAI_95791_1
Tender Inviting Authority: Asst.Gen.Manager (E-E), Airports Authority of India, Coimbatore International Airport, Coimbatore - 641014.
Name of Work: Provision of Turn Pad and fillets for link taxi track for operation of B777-300ER type of aircraft at Coimbatore International Airport. SH: Electrical Works.
Tender ID: 2021_AAI_95791_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Techno Electricals(GSTN-24AAGFT9086M1ZG) |  | Vardhman Airport Solutions Pvt Ltd(GSTN-07AAECN5914F1ZK) |  | Balaji Engineering(GSTN-33ADGPV2628A1ZV) |  | CREATIVE TRADING CO(GSTN-07AMEPK8023F1Z9) |  | Hi Elect Enterprises(GSTN-32ACXPN0529N1Z3)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH I : Supply Supply of 2 x 105W bi-directional halogen type inset fitting with yellow and clear filters for Runway edge applications suitable for use in 6.6A airfield lighting circuits normally supplied from 200W isolating transformer and complete with lens support mechanism, lens clamping mechanism, gaskets, two pin secondary leads, including shallow base other accessories etc. complete as required meeting the requirement of ICAO Annex -14 and aerodrome design manual part - IV. | 22.00 | No's |  | 56000.00 | 1232000.00 | 51768.00 | 1138896.00 | 59000.00 | 1298000.00 | 60000.00 | 1320000.00 | 70000.00 | 1540000.00 | 1138896.00 | Vardhman Airport Solutions Pvt Ltd
2.00 | Supply of 2 x 105W bi-directional halogen type inset fitting with clear filters for Runway edge applications suitable for use in 6.6A airfield lighting circuits normally supplied from 200W isolating transformer and complete with lens support mechanism, lens clamping mechanism, gaskets, two pin secondary leads, including shallow base other accessories etc. complete as required meeting the requirement of ICAO Annex -14 and aerodrome design manual part - IV. | 12.00 | No's |  | 56000.00 | 672000.00 | 50350.00 | 604200.00 | 59000.00 | 708000.00 | 60000.00 | 720000.00 | 70000.00 | 840000.00 | 604200.00 | Vardhman Airport Solutions Pvt Ltd
3.00 | Supply of medium intensity elevated type omni-directional taxiway/turning pad edge light fitting fitted with 1W LED complete with all accessories including blue lens for LED and CI base plate etc complete as required and as per ICAO standards. | 48.00 | No's |  | 5450.00 | 261600.00 | 4389.00 | 210672.00 | 4500.00 | 216000.00 | 4300.00 | 206400.00 | 4500.00 | 216000.00 | 206400.00 | CREATIVE TRADING CO
4.00 | Supply of 1x16 sq.mm 5 KV grade Airfield lighting cable conforming IS 1554 (Part II) with upto date amendment as required confirming to particular specifications etc. as required. | 3620.00 | Mtr |  | 211.00 | 763820.00 | 197.00 | 713140.00 | 250.00 | 905000.00 | 250.00 | 905000.00 | 170.00 | 615400.00 | 615400.00 | Hi Elect Enterprises
5.00 | Supply of 1x6 sq.mm. 5 KV grade Airfield lighting cable conforming IS 1554 (Part II) with upto date amendment as required confirming to particular specifications etc. as required. | 700.00 | Mtr |  | 111.00 | 77700.00 | 103.00 | 72100.00 | 95.00 | 66500.00 | 115.00 | 80500.00 | 70.00 | 49000.00 | 49000.00 | Hi Elect Enterprises
6.00 | Supply of 5 KV grade plug and receptacle suitable for 1 x 16 Sq.mm AFL cable | 93.00 | No's |  | 425.00 | 39525.00 | 543.00 | 50499.00 | 350.00 | 32550.00 | 315.00 | 29295.00 | 600.00 | 55800.00 | 29295.00 | CREATIVE TRADING CO
7.00 | Supply of 5 KV grade plug and receptacle suitable for 1 x 6 Sq.mm AFL cable | 20.00 | No's |  | 425.00 | 8500.00 | 543.00 | 10860.00 | 350.00 | 7000.00 | 315.00 | 6300.00 | 650.00 | 13000.00 | 6300.00 | CREATIVE TRADING CO
8.01 | Supply of 2C x 4 sq.mm secondary lead of following length made out of multi stranded copper conductor, EPR insulalted PCP sheathed, treated 600V grade cable as specified in particular specification and as required. 20 mtr length | 12.00 | No's |  | 3000.00 | 36000.00 | 3382.00 | 40584.00 | 2000.00 | 24000.00 | 2575.00 | 30900.00 | 4000.00 | 48000.00 | 24000.00 | Balaji Engineering
8.02 | Supply of 2C x 4 sq.mm secondary lead of following length made out of multi stranded copper conductor, EPR insulalted PCP sheathed, treated 600V grade cable as specified in particular specification and as required. 30 mtr length | 3.00 | No's |  | 4253.00 | 12759.00 | 4881.00 | 14643.00 | 3000.00 | 9000.00 | 3800.00 | 11400.00 | 5000.00 | 15000.00 | 9000.00 | Balaji Engineering
8.03 | Supply of 2C x 4 sq.mm secondary lead of following length made out of multi stranded copper conductor, EPR insulalted PCP sheathed, treated 600V grade cable as specified in particular specification and as required. 40 mtr length | 5.00 | No's |  | 5321.00 | 26605.00 | 6379.00 | 31895.00 | 4000.00 | 20000.00 | 5005.00 | 25025.00 | 7500.00 | 37500.00 | 20000.00 | Balaji Engineering
8.04 | Supply of 2C x 4 sq.mm secondary lead of following length made out of multi stranded copper conductor, EPR insulalted PCP sheathed, treated 600V grade cable as specified in particular specification and as required. 50 mtr length | 8.00 | No's |  | 6625.00 | 53000.00 | 7878.00 | 63024.00 | 5000.00 | 40000.00 | 6300.00 | 50400.00 | 9000.00 | 72000.00 | 40000.00 | Balaji Engineering
9.00 | Supply of 5 KV grade 200 W 20/6.6 A Isolating Transformer | 33.00 | No's |  | 4252.00 | 140316.00 | 4528.00 | 149424.00 | 5000.00 | 165000.00 | 4200.00 | 138600.00 | 5000.00 | 165000.00 | 138600.00 | CREATIVE TRADING CO
10.00 | Supply of 5 KV grade 15 W 20/6.6 A Isolating Transformer | 55.00 | No's |  | 2950.00 | 162250.00 | 2838.00 | 156090.00 | 3200.00 | 176000.00 | 2400.00 | 132000.00 | 3000.00 | 165000.00 | 132000.00 | CREATIVE TRADING CO
11.00 | Supply of Cylindrical type CI Transformer Housing Box of outside dia 330mm height 450mm made of 10mm thick all round except on top surface which is 15mm thick having a clear opening of 220mm at the top surface and 6 Nos. M10 tapped holes at the hole centre of 260mm to receive light fittings base plate and bolts, provided with clear holes at two side surface centre at 75mm above bottom surface and suitable to receive 50mm dia B class GI pipes and check nuts etc as required. | 98.00 | No's |  | 4600.00 | 450800.00 | 4934.00 | 483532.00 | 5000.00 | 490000.00 | 5100.00 | 499800.00 | 4000.00 | 392000.00 | 392000.00 | Hi Elect Enterprises
12.00 | Supply of DOBEFIL 60 of Dr. Beck & Co. or equivalent sealant material suitable for fixing bottom box of inset approach/threshold fitting etc. as required | 699.00 | Kg |  | 364.00 | 254436.00 | 411.00 | 287289.00 | 400.00 | 279600.00 | 530.00 | 370470.00 | 325.00 | 227175.00 | 227175.00 | Hi Elect Enterprises
13.00 | Supply of hardener 758 for DOBEFIL 60 sealant as required | 209.00 | kg |  | 923.00 | 192907.00 | 906.00 | 189354.00 | 400.00 | 83600.00 | 1100.00 | 229900.00 | 900.00 | 188100.00 | 83600.00 | Balaji Engineering
14.00 | SH II Work Laying of one number PVC insulated and PVC sheathed/XLPE power cable of 5 kV grade 6 sq. mm / 16 Sq.mm size in the existing RCC/HUME/METAL/ duct/culvert/ drainage pipe as required. | 4064.00 | Mtr |  | 15.00 | 60960.00 | 22.00 | 89408.00 | 20.00 | 81280.00 | 20.00 | 81280.00 | 30.00 | 121920.00 | 60960.00 | Techno Electricals
15.00 | Excavation for cable trenches in soft soil, depth upto 1.2m including dressing of sides lift upto 1.5 m, getting out the excavated soil, refilling with excavated soil after laying of cable/ pipe etc. and disposal of surplus excavated soil as directed, within a lead of 50 meters etc as required. | 887.00 | Cum |  | 285.00 | 252795.00 | 261.00 | 231507.00 | 150.00 | 133050.00 | 380.00 | 337060.00 | 500.00 | 443500.00 | 133050.00 | Balaji Engineering
16.00 | Supplying and laying of following size ISI marked DWC HDPE pipe along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.in the existing trench/ duct ., complete as required. 50 mm OD, 38 mm ID | 3380.00 | Mtr |  | 112.00 | 378560.00 | 157.00 | 530660.00 | 65.00 | 219700.00 | 115.00 | 388700.00 | 130.00 | 439400.00 | 219700.00 | Balaji Engineering
17.00 | Cutting of cable groove with kerf cutting machine for laying following number of 2x4 Sqmm secondary leads meant for inset type taxiway fitting on the concrete/ bituminous taxiway surface including kerfing, chiselling, cleaning and filling the groove with departmentally supplied sealant compound after laying secondary lead including jute covering for protection etc. as required. a) 01 run of cable | 888.00 | Mtr |  | 200.00 | 177600.00 | 214.00 | 190032.00 | 250.00 | 222000.00 | 238.00 | 211344.00 | 200.00 | 177600.00 | 177600.00 | Techno Electricals, Hi Elect Enterprises
18.00 | Installation, testing and commissioning of inset type Runway edge light fittings in the bitumen/ concrete surface using core cutting machine and departmentally supplied Dobefil 60 compound & Hardener 758, installation and aligning of inset fitting using suitable jig, closing of shallow base with sealant material, connecting with secondary leads, providing Insulation tape etc. as required. | 28.00 | Job |  | 5825.00 | 163100.00 | 4880.00 | 136640.00 | 5000.00 | 140000.00 | 2800.00 | 78400.00 | 1500.00 | 42000.00 | 42000.00 | Hi Elect Enterprises
19.00 | Supply and fixing of MS base plates of 10mm thick, 330 mm dia provided with 6 nos holes for M-10 SS bolts, for covering the CI transformer housing box including providing gaskets, and SS bolts etc. complete as required | 28.00 | Job |  | 1000.00 | 28000.00 | 833.00 | 23324.00 | 750.00 | 21000.00 | 1200.00 | 33600.00 | 2500.00 | 70000.00 | 21000.00 | Balaji Engineering
20.00 | Dismantling of the existing runway/ turning pad/taxiway edge light fittings including disconnecting the isolating transformers and series cable, shifting the dismantled items to store/ new location etc. as required . | 56.00 | Job |  | 100.00 | 5600.00 | 122.00 | 6832.00 | 200.00 | 11200.00 | 150.00 | 8400.00 | 50.00 | 2800.00 | 2800.00 | Hi Elect Enterprises
21.00 | Installation testing and commissioning of Elevated type Runway turning pad/ runway edge/ taxiway edge on the existing transformer housing boxes including connecting the Esna connectors with the series cables, connecting the secondary lead, isolating transformers, levelling, aligning complete as required and as specified. | 60.00 | Job |  | 150.00 | 9000.00 | 122.00 | 7320.00 | 200.00 | 12000.00 | 200.00 | 12000.00 | 100.00 | 6000.00 | 6000.00 | Hi Elect Enterprises
22.00 | Numbering of Taxiway/ Runway light fittings with ISI approved enamel paint with double coat yellow paint as background and numbering with black paint of suitable size serially etc., complete as required. | 290.00 | No's |  | 65.00 | 18850.00 | 61.00 | 17690.00 | 30.00 | 8700.00 | 150.00 | 43500.00 | 50.00 | 14500.00 | 8700.00 | Balaji Engineering
23.00 | Earthing with G.I. earth pipe 2.75 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 6.00 | Set |  | 6000.00 | 36000.00 | 6100.00 | 36600.00 | 5000.00 | 30000.00 | 8500.00 | 51000.00 | 8000.00 | 48000.00 | 30000.00 | Balaji Engineering
24.00 | Supply and laying of 6 SWG dia GI wire along with cable including providing lugs for termination, etc. complete as required | 4112.00 | Mtr |  | 15.00 | 61680.00 | 16.00 | 65792.00 | 20.00 | 82240.00 | 22.00 | 90464.00 | 30.00 | 123360.00 | 61680.00 | Techno Electricals
| Total in Figures |  |  |  |  | 5576363.00 |  | 5552007.00 |  | 5481420.00 |  | 6091738.00 |  | 6128055.00
Lowest Amount Quoted BY: Balaji Engineering(5481420.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Turn Pad and fillets for link taxi track for operation of B777-300ER type of aircraft at Coimbatore International Airport. SH. Electrical Works. Tender ID: 2021_AAI_95791_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Balaji Engineering | 5481420.00 | L1
| 2 | Vardhman Airport Solutions Pvt Ltd | 5552007.00 | L2
| 3 | Techno Electricals | 5576363.00 | L3
| 4 | CREATIVE TRADING CO | 6091738.00 | L4
| 5 | Hi Elect Enterprises | 6128055.00 | L5