## BoQ1
Government eProcurement System Created By: S.THIRVMAL MURUGAN Created Date/Time: 22-Dec-2021 01:14 PM Tender Title: Provision of Standby Hydro Pneumatic System for RO Plant and associated Works at New Water Treatment Plant at Chennai Airport Tender ID: 2021_AAI_95922_1
Tender Inviting Authority: Jt.General Manager (Engg-Elect)-I, AMED-VI, Chennai Airport.
Name of Work: Provision of Standby Hydro-Pneumatic System for RO Plant & associated Works at New Water Treatment Plant at Chennai Airport.
Contract No: AAI/CHE/AMED-VI/2021-22/01
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | BI MARKETING AND SERVICES PRIVATE LIMITED(GSTN-33AABCB4871G1ZW) |  | CHENNAI ENGINEERING SERVICES(GSTN-33AADFC4373K1ZH) |  | DElite System Engineering (India) Pvt. Ltd.(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Hydropneumatic Pumping System With Variable Frequency Drive: (Grundfos Model No. Hydro MPC EF 3 X CRN 3-12 or its equivalent) Supply, Installation, Testing and Commissioning of compact packaged type skid mounted, self-contained variable frequency drive hydropneumatic system complete as per following technical specification complete as required:- (i) In-line vertical Single/Multistage centrifugal clear water pumpset with SS-304 casing, SS-304 impeller with SS-316 shaft ,CI base with CED coating complete directly coupled with TEFC induction motor of class "F" insulation & efficiency class IE-3, 2900rpm, suitable for operation on 415 Volts ±10%, 3 phase, 50 Hz A.C. supply complete. (ii) The entire system shall be mounted on a common base frame i/c common suction and common delivery of SS pipe headers with flanges, interconnecting piping with all required Conrol Valves, Non-return valves, pressure guage with isolation cock etc. and all requried accessories. (iii) Pressure vessel capacity of 178 Litres ( WM-14 Make or equivalent) & Qty 01 Nos made up of non-corrosive FRP composite construction lined with NSF/ FDA listed material, like high density polyethylene with fully replaceable polyurethane.
1.10 | (iv) Panel mounted microprocessor multi-pump controller with large graphical display and variable frequency drive (VFD) mounted inside a panel complete with pressure sensor transmitter. The graphical display capable to show number of pumps running & also communicate with other controllers following with open protocol through RS485 port. System should be capable to compensate for frictional losses at lower flows. All alarms should be displayed in the controller. The panel should also have provision for manual / automatic alternate (cyclic) operation of pumps, ON / OFF switch (v) Necessary foundationing bolts, vibration elimination pads and other accessories complete as required. (vi) Termination with Suitable cable and other accessories complete as required. (vii) The entire system alongwith pumps & control panel must be sourced from single manufacturer only for unit responsibility. No. of pumps : 03 Nos (02 Working + 01 Standby) with VFD 1.5KW Water Flow Rate : Min 3 Cum/Hr each Head : Min 57 Meters Location : New Water Treatment Plant (i) to (vii) = 1 Job | 1.00 | Set |  | 1000000.00 | 1000000.00 | 1196999.00 | 1196999.00 | 1100000.00 | 1100000.00 | 1000000.00 | BI MARKETING AND SERVICES PRIVATE LIMITED
2.00 | Modification and upgradation of existing RO Hydro-pneumatic System (HPS) Panel (Make: Grundfos) including supply & fixing of 2 Nos new 1.5 KW VFD (Make: Danfoss) alongwith all necessary wiring & accessories, software programming, integration with existing control unit etc as required for proper alteration of all pump speed to meet the preset pressure point. | 1.00 | Job |  | 200000.00 | 200000.00 | 69999.00 | 69999.00 | 35000.00 | 35000.00 | 35000.00 | DElite System Engineering (India) Pvt. Ltd.
3.00 | Supply & fixing of Negative pressure transmitter in Header of Hydro-Pnuematic systems including complete interconnections & necessary arrangements etc complete as required. | 1.00 | Job |  | 40000.00 | 40000.00 | 8999.00 | 8999.00 | 9299.00 | 9299.00 | 8999.00 | CHENNAI ENGINEERING SERVICES
4.00 | Providing and laying in position cement concrete of grade 1:2:4 (1 cement : 2 coarse sand (zone-III) : 4 graded stone aggregate 20 mm nominal size) etc complete as required. | 3.00 | Cum |  | 25000.00 | 75000.00 | 4999.00 | 14997.00 | 7000.00 | 21000.00 | 14997.00 | CHENNAI ENGINEERING SERVICES
5.00 | Supply of Copper Conductor, PVC/XLPE insulated and PVC sheathed armoured Power cable of 1.1 KV grade of size 4 Core X 4 Sq.mm conforming to IS-7098 (Part-I) 1988 with upto date amendements as and when required. | 150.00 | Mtr |  | 500.00 | 75000.00 | 209.00 | 31350.00 | 250.00 | 37500.00 | 31350.00 | CHENNAI ENGINEERING SERVICES
6.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
6.10 | Upto 35 sq. mm | 150.00 | Mtr |  | 600.00 | 90000.00 | 19.00 | 2850.00 | 25.00 | 3750.00 | 2850.00 | CHENNAI ENGINEERING SERVICES
7.00 | Providing and laying of approved make 1-1/4" (32 mm) Stainless Steel Schedule 10 pipeline including cutting, welding, grinding etc and interconnection with necessary SS fittings such as Tees, crosses, isolating ball valves,plugs, sockets, elbows, reducers, Union, flanges, sleeve pieces, checknuts, gaskets,nuts/bolts & other accessories etc complete as required for making necessary charging connections from Pressure Tank to discharge pipeline & for Pressure Tank drain pipeline connections. (Note: All SS fittings for necessary pipeline connections are to be arranged by the Contractor) | 20.00 | Mtr |  | 6500.00 | 130000.00 | 1499.00 | 29980.00 | 1900.00 | 38000.00 | 29980.00 | CHENNAI ENGINEERING SERVICES
8.00 | Providing and laying of approved make 2.5" Stainless Steel Schedule 10 pipeline including cutting, welding, grinding etc and interconnection with necessary SS fittings such as Tees, crosses, plugs, sockets, elbows, reducers, Union, sleeve pieces, checknuts, gaskets,nuts/bolts & other accessories etc complete as required for making necessary connections as follows: a)From existing Stainless Steel vessal Pipeline to HPS Common Suction Manifold b)From HPS Common Delivery Manifold to Existing Delivery Stainless Steel Pipeline (Note: All SS fittings for necessary pipeline connections are to be arranged by the Contractor) | 20.00 | Mtr |  | 8000.00 | 160000.00 | 1799.00 | 35980.00 | 1500.00 | 30000.00 | 30000.00 | DElite System Engineering (India) Pvt. Ltd.
9.00 | Supply & fixing of Ball type 65mm NRV (including flanges) PN-10 or above (Normax Make B-01 type or equivalent) suitable for vertical & horizontal installation Flanged Body & cover with MOC: Cast Iron, Ball:Nitrile Reinforced , Seat: lead Tin Bronze including cutting of pipeline,welding of flanges,grinding alongwith all accessories such as nuts, bolts, washer , gaskets etc complete as required. (Make:Conforming to respective IS standard.) | 2.00 | Job |  | 10500.00 | 21000.00 | 6999.00 | 13998.00 | 5999.00 | 11998.00 | 11998.00 | DElite System Engineering (India) Pvt. Ltd.
10.00 | Supplying, fixing, testing and commissioning of 65mm Butterfly Valve (including flanges) with CI body,SS disc,SS stem, nitrile/EPDM rubber seal,O - ring & PN 16 pressure rating including cutting of pipeline,welding of flanges,grinding alongwith all accessories such as nuts, bolts, washer , gaskets etc complete etc as required. | 3.00 | Job |  | 10000.00 | 30000.00 | 4999.00 | 14997.00 | 4999.00 | 14997.00 | 14997.00 | DElite System Engineering (India) Pvt. Ltd., CHENNAI ENGINEERING SERVICES
11.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess etc as required. | 30.00 | Mtr |  | 250.00 | 7500.00 | 59.00 | 1770.00 | 35.00 | 1050.00 | 1050.00 | DElite System Engineering (India) Pvt. Ltd.
12.00 | Supply and Installation of various Mild Steel structure fabricated using single section MS Channel/angle/flat/bar etc including cutting, welding, drilling, fixing in position using appropriate fasteners, grinding, painting with approved steel primer and two coats enamel paint etc. complete as required. | 75.00 | Kgs |  | 180.00 | 13500.00 | 89.00 | 6675.00 | 160.00 | 12000.00 | 6675.00 | CHENNAI ENGINEERING SERVICES
13.00 | Design, Fabrication, Supply and Installation of MS walkaway platform Structure with staircase suitable to bear load of min. 1000 kgs constructed using MS Structural members (Channels, angles, square tubes, plates, Handrail, etc.) including cutting, welding, grinding, buffing, polishing and making curvature (wherever required), painting with approved steel primer and two coats enamel paint & then applying FRP coating on entire structure and fitting the same with necessary fasteners, nuts, bolts etc of required size and necessary accessories for proper positioning & erection at Basement Floor alongwith dismantling of existing structure and shifting it to Old WTP complete as required. Note: The drawing of platform to be approved by Engineer-In-Charge before start of Fabrication Work. | 3250.00 | Kgs |  | 200.00 | 650000.00 | 199.00 | 646750.00 | 279.00 | 906750.00 | 646750.00 | CHENNAI ENGINEERING SERVICES
14.00 | Fabrication, Supply and Installation of MS Structure of approved design constructed using MS Structural members (Channels and angles) including cutting, welding, grinding, buffing, polishing, hoisting, fixing in position, Anchor Fastener in welded base plates, painting with approved steel primer and two coats enamel paint & then applying FRP coating on entire structure alongwith dismantling of existing structure & motor-agitator set, re-installation & re-connection of motor-agitator set after fabrication of new structure, shifting of dismantled structure to Old WTP complete as required. | 1000.00 | Kgs |  | 200.00 | 200000.00 | 159.00 | 159000.00 | 279.00 | 279000.00 | 159000.00 | CHENNAI ENGINEERING SERVICES
15.00 | Supply, Installation, Testing and Commissioning of ISI Double Layer Water tank of 7500 Litres Capacity (Make: Sintex or Equivalent) alongwith dismantling of existing Tank, Pipelines etc and installing new Tank & re-connecting inlet/outlet piping , valves etc for proper operation of Brine Tank. | 2.00 | Job |  | 10000.00 | 20000.00 | 92999.00 | 185998.00 | 92000.00 | 184000.00 | 20000.00 | BI MARKETING AND SERVICES PRIVATE LIMITED
| Total in Figures |  |  |  |  | 2712000.00 |  | 2420342.00 |  | 2684344.00
Lowest Amount Quoted BY: CHENNAI ENGINEERING SERVICES(2420342.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Standby Hydro Pneumatic System for RO Plant and associated Works at New Water Treatment Plant at Chennai Airport Tender ID: 2021_AAI_95922_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | CHENNAI ENGINEERING SERVICES | 2420342.00 | L1
| 2 | DElite System Engineering (India) Pvt. Ltd. | 2684344.00 | L2
| 3 | BI MARKETING AND SERVICES PRIVATE LIMITED | 2712000.00 | L3