## BoQ1
Government eProcurement System Created By: Rajeev Ranjan Created Date/Time: 27-Dec-2021 12:00 PM Tender Title: Expansion of Passenger Terminal Building at Gorakhpur Civil Enclave Gorakhpur SH Provision of Air Conditioning VRV/VRF System Tender ID: 2021_AAI_96479_1
Tender Inviting Authority: Asstt. Gen. Mgr. (Engg.-E), AAI, RHQ-NR, New Delhi - 110037
Name of Work: Expansion of Passenger Terminal Building at Gorakhpur Civil Enclave, Gorakhpur. SH: PROVISION OF AIR CONDITIONING (VRV/VRF) SYSTEM.
Tender ID No. : 2021_AAI_96479_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SAI H.V.A.C. SYSTEM(GSTN-27AFRPV9452P1Z2) |  | UNITY ENGINEERS(GSTN-09AHBPK7389L1ZN) |  | KRISHNA REFRIGERATION(GSTN-09AGYPK1790P1Z9) |  | Sai Cooling Point Private Limited(GSTN-09AAKCS2310Q1ZY) |  | M/S COOLING CENTER(GSTN-09AFFPA7913Q1Z1) |  | GLOBAL AIR TECNIX(GSTN-NA) |  | SAHU AGENCIES PRIVATE LIMITED(GSTN-NA) |  | SHINRYO SUVIDHA ENGINEERS INDIA PRIVATE LIMITED(GSTN-NA) |  | S G TECHNOFAB PVT LTD(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | PART -A OUTDOOR UNITS
1.01 | Supply, Installation, Testing & Commissioning of VRV/VRF outdoor units with multiple compressors complete with inverter based type Scroll/Rotary compressors, R-410A referigerant, cooling & heating mode both options, suitable for 415 +/- 10 % volt, 50 Hz, 3 phase AC supply for outdoor units, special pre-coated fin type heat exchanger, low noise direct driven propeller condenser fans in each module with top discharge.The electronic circuit in each module should be highly advance with Film Capacitors and refrigerant cooled circuits. Each module of outdoor Unit should have Full DC Inverter Scroll/Rotary Compressors & can have single inverter Scroll/Rotary compressor till 14 HP & multiple inverter Scroll/Rotary Compressors beyond 14 HP. In case of any of module failure, the rest of system should be capable of operation. GI coated condenser stands, microprocessor panel with sequential starting of condensing unit, coils, expansion valves, filters in referigerant circuits, single phase preventor, all vibration isolators, safeties, in all respect including foundation and anti vibration Pads for ODU, operating range of Compressor for Dry Bulb Temperature -5 to 52 Deg C ( i.e. in cooling mode) and heating mode should be -10 to 15.5 degree C, Machine Sound Level should not be more then 69 dB at distance of 1.5 Mtr. Quoted price shall also be inclusive of loading, unloading, lifting & shifting on terrace or other suitable locations as per drawing, and also iclusive of MS angle base frame duly painted & vibration isolation arrangement etc. complete as required. The COP at AHRI conditions shall not be less than 3.1 and IEER not less than 6.5. The unit shall deliver the below mentioned capacity at 42 deg ambient temperature based on the Gorakhpur (UP), India ambient conditions during summer.
1.02 | 20 HP (Minimum) for AHU Units | 7.00 | Each | 100.00 | 247478.00 | 1732346.00 | 346200.00 | 2423400.00 | 322609.00 | 2258263.00 | 328044.00 | 2296308.00 | 233000.00 | 1631000.00 | 368790.00 | 2581530.00 | 242270.00 | 1695890.00 | 260195.00 | 1821365.00 | 254584.00 | 1782088.00 | 1631000.00 | M/S COOLING CENTER
1.03 | 10 HP (Minimum ) For TFA Units | 2.00 | Each | 100.00 | 114108.00 | 228216.00 | 214800.00 | 429600.00 | 181033.00 | 362066.00 | 216480.00 | 432960.00 | 153000.00 | 306000.00 | 213750.00 | 427500.00 | 171960.00 | 343920.00 | 176500.00 | 353000.00 | 145920.00 | 291840.00 | 228216.00 | SAI H.V.A.C. SYSTEM
2.00 | INDOOR UNITS
2.01 | Supply, Installation, Testing & Commissioning of VRV/VRF In-door units & Accessories:- Indoor Units shall be Double skin type Air Handling Units, ceiling suspended type of ratings as specified with 24 Gauge pre coated G.I. outer and indoor skin and 40 mm of suitable PUF insulation, Horizontal type AHU complete with DIDW fans, fan motor Drive, 6 Row Deep DX Cooling Coil, with static 35mm pressure, MERV-8 pre filters, Mixing box device, thermal break profile, vibration isolator pad, Expansion Kit, communication kit and wired / wireless remote controller. The indoor units shall be suitable for operation on 415 ±10% volts, 50Hz, 3 phase AC power supply. The cooling coil shall be made of seamless copper tube. This shall includes Support structure, all accessories, complete as required.
2.02 | Ceiling Suspended type AHU: 11 TR (Minimum)/ 4500 CFM | 11.00 | Each | 10.00 | 31861.00 | 350471.00 | 172400.00 | 1896400.00 | 141304.00 | 1554344.00 | 172032.00 | 1892352.00 | 111000.00 | 1221000.00 | 182350.00 | 2005850.00 | 149600.00 | 1645600.00 | 158492.00 | 1743412.00 | 157650.00 | 1734150.00 | 350471.00 | SAI H.V.A.C. SYSTEM
3.00 | Supply, installation, testing & commissioning of Ceiling Suspended type Treated Fresh Air unit with Double skinned panels to be fabricated with extruded aluminium section framework bolted together with sandwich panel having 24 gauge pre-plasticized outer skin and 24 gauge plain GI inner skin injected with 40 mm thick thermal break profile having suitable PUF insulation of minimum 8 TR & 1600 CFM, 6 Row deep, static 35mm pressure with suitable electronic expansion valve which can communicate with the controller in the VRF condensing unit, complete with forward curved centrifugal driven set, MERV-8 pre filters, including wired / wireless remote control, all accessories, etc complete as required. | 2.00 | Each | 10.00 | 101300.00 | 202600.00 | 103750.00 | 207500.00 | 130435.00 | 260870.00 | 108816.00 | 217632.00 | 78000.00 | 156000.00 | 180280.00 | 360560.00 | 52392.00 | 104784.00 | 92179.00 | 184358.00 | 98145.00 | 196290.00 | 104784.00 | SAHU AGENCIES PRIVATE LIMITED
4.00 | Supply, Installation, Testing & Commissioning of VRV/VRF In-door units & Accessories:- Indoor Units shall be ceiling mounted Cassette type as specified. The indoor units shall be suitable for operation on 230 ±10% volts, 50Hz, 1 phase AC power supply. The indoor unit shall have independent electronic control valve to control the refrigerant flow rate respond to variations of the air-conditioning load of the room. The fan shall be aerodynamically designed turbo multiblade type. Statically and dynamically balanced to ensure lowest noise. The cooling coil shall be made of seamless copper tube. Indoor units shall have fittings, filter, drain pump in Cassette unit, Panel, required plugtop & cable to connect indoor unit to socket, including wireless remote control as per specified, all accessories, complete as required.
4.01 | Ceiling mounted 4 way Cassette type: 2 TR, Single Phase | 2.00 | Nos | 10.00 | 30824.00 | 61648.00 | 28050.00 | 56100.00 | 33587.00 | 67174.00 | 38200.00 | 76400.00 | 27500.00 | 55000.00 | 39535.00 | 79070.00 | 31895.00 | 63790.00 | 32176.00 | 64352.00 | 32467.00 | 64934.00 | 55000.00 | M/S COOLING CENTER
4.02 | Ceiling mounted 4 way Cassette type: 1.5 TR Single Phase | 3.00 | Nos | 10.00 | 25801.00 | 77403.00 | 24050.00 | 72150.00 | 31902.00 | 95706.00 | 37855.00 | 113565.00 | 27000.00 | 81000.00 | 38200.00 | 114600.00 | 32989.00 | 98967.00 | 31854.00 | 95562.00 | 31655.00 | 94965.00 | 72150.00 | UNITY ENGINEERS
5.00 | SITC of following nominal capacity unitary Inverter type highly efficient ceiling suspended / wall mounted following type Air conditioning units with air cooled condenser complete with inverter type scroll/ rotary compressor, condenser including, cordless remote, indoor units shall be ceiling suspended/ wall mounted type complete with evaporator, fan, filter, drier, expansion devices & microprocessor control panel along with all accessories with R-32 refrigerant & oil charge, remote controls , refrigerant piping of suitable size between Indoor to outdoor duly insulated & suitable size of copper conductor cables (approximate up to 15 m per unit to be provided), MS structure / frame stand (M S Angle size 50 x50 x6 mm.) for outdoor unit and required size of drain piping with insulation ( approx 15 Mtrs per unit), complete with indoor hanging arrangement, inclusive of initial charging of refrigerant, etc. complete as required. Makes as per approved make list.
5.01 | High Wall split ( COLD ONLY)Type : 1.5 TR, Nominal capacity, Single Phase, 5 star rated | 2.00 | Each | 10.00 | 32500.00 | 65000.00 | 36350.00 | 72700.00 | 38570.00 | 77140.00 | 39500.00 | 79000.00 | 30000.00 | 60000.00 | 27906.25 | 55812.50 | 36468.00 | 72936.00 | 29182.00 | 58364.00 | 64320.00 | 128640.00 | 55812.50 | GLOBAL AIR TECNIX
5.02 | Ceiling mounted ( HOT & COLD ONLY) 4 way Cassette type: 2 TR, Single Phase 5 star rated | 3.00 | Each | 10.00 | 101525.00 | 304575.00 | 87500.00 | 262500.00 | 55978.00 | 167934.00 | 83500.00 | 250500.00 | 70000.00 | 210000.00 | 43406.25 | 130218.75 | 84648.00 | 253944.00 | 42255.00 | 126765.00 | 107695.00 | 323085.00 | 126765.00 | SHINRYO SUVIDHA ENGINEERS INDIA PRIVATE LIMITED
6.00 | REFRIGERENT PIPING
6.01 | Supply installation testing and commissioning including vaccumiazation and Nitrogen testing of following nominal sizes of soft/hard drawn copper refrigerant piping for VRF/VRV system,complete with fittings, with suitable adjustable ring type hanger supports/clamp / MS hanger / MS support / MS angle, etc, as per site requirement, jointng/brazing including accesories insulated with XLPE Class O tubular insulation/with Class O closed cell elastemeric nitrile rubber tubular sleeves sections of specified thickness as below for Suction and Liquid lines, all accessories, as per specification. complete as reqd. Quoted price shall be inclusive of necessary glass cloth and minimum two layers of UV protection paint to be applied over insulation for all exposed pipes of approved make. Extra support for Y-joints/bend etc to be provided as per specification.
6.02 | 44.5 mm dia ( with 19mm thick insulation | 50.00 | Meter | 10.00 | 1020.00 | 51000.00 | 2820.00 | 141000.00 | 1549.00 | 77450.00 | 100.00 | 5000.00 | 650.00 | 32500.00 | 2640.00 | 132000.00 | 1648.00 | 82400.00 | 2444.00 | 122200.00 | 107.00 | 5350.00 | 5000.00 | Sai Cooling Point Private Limited
6.03 | 41.3 mm O.D. (insulation – 19 mm thick) | 100.00 | Meter | 10.00 | 1020.00 | 102000.00 | 2410.00 | 241000.00 | 1655.00 | 165500.00 | 1810.00 | 181000.00 | 650.00 | 65000.00 | 2400.20 | 240020.00 | 1515.00 | 151500.00 | 2287.00 | 228700.00 | 1779.00 | 177900.00 | 65000.00 | M/S COOLING CENTER
6.04 | 34.9 mm O.D. (insulation – 19 mm thick) | 80.00 | Meter | 10.00 | 980.00 | 78400.00 | 1820.00 | 145600.00 | 1222.00 | 97760.00 | 1535.00 | 122800.00 | 837.00 | 66960.00 | 1788.60 | 143088.00 | 1002.00 | 80160.00 | 1820.00 | 145600.00 | 1520.00 | 121600.00 | 66960.00 | M/S COOLING CENTER
6.05 | 28.6 mm O.D. (insulation – 19 mm thick) | 200.00 | Meter | 10.00 | 980.00 | 196000.00 | 1295.00 | 259000.00 | 855.00 | 171000.00 | 1245.00 | 249000.00 | 837.00 | 167400.00 | 1492.70 | 298540.00 | 913.00 | 182600.00 | 1441.00 | 288200.00 | 1116.00 | 223200.00 | 167400.00 | M/S COOLING CENTER
6.06 | 22.2 mm O.D. (insulation – 19 mm thick) | 30.00 | Meter | 10.00 | 980.00 | 29400.00 | 880.00 | 26400.00 | 666.00 | 19980.00 | 710.00 | 21300.00 | 753.00 | 22590.00 | 848.10 | 25443.00 | 903.00 | 27090.00 | 1045.00 | 31350.00 | 770.00 | 23100.00 | 19980.00 | KRISHNA REFRIGERATION
6.07 | 19.1 mm O.D. (insulation – 13 mm thick) | 135.00 | Meter | 10.00 | 980.00 | 132300.00 | 750.00 | 101250.00 | 577.00 | 77895.00 | 684.00 | 92340.00 | 498.00 | 67230.00 | 743.60 | 100386.00 | 703.00 | 94905.00 | 1004.00 | 135540.00 | 679.00 | 91665.00 | 67230.00 | M/S COOLING CENTER
6.08 | 15.9 mm O.D. (insulation – 13 mm thick) | 225.00 | Meter | 10.00 | 980.00 | 220500.00 | 650.00 | 146250.00 | 478.00 | 107550.00 | 571.00 | 128475.00 | 498.00 | 112050.00 | 715.00 | 160875.00 | 601.00 | 135225.00 | 882.00 | 198450.00 | 588.00 | 132300.00 | 107550.00 | KRISHNA REFRIGERATION
6.09 | 12.7 mm O.D. (insulation – 13 mm thick) | 60.00 | Meter | 10.00 | 980.00 | 58800.00 | 450.00 | 27000.00 | 318.00 | 19080.00 | 386.00 | 23160.00 | 283.00 | 16980.00 | 526.90 | 31614.00 | 423.00 | 25380.00 | 817.00 | 49020.00 | 430.00 | 25800.00 | 16980.00 | M/S COOLING CENTER
6.10 | 9.5 mm O.D. (insulation – 13 mm thick) | 110.00 | Meter | 10.00 | 780.00 | 85800.00 | 335.00 | 36850.00 | 239.00 | 26290.00 | 292.00 | 32120.00 | 283.00 | 31130.00 | 432.30 | 47553.00 | 353.00 | 38830.00 | 595.00 | 65450.00 | 354.00 | 38940.00 | 26290.00 | KRISHNA REFRIGERATION
6.11 | 6.4 mm dia with 13 mm thick insulation | 50.00 | Meter | 10.00 | 780.00 | 39000.00 | 235.00 | 11750.00 | 157.00 | 7850.00 | 199.00 | 9950.00 | 218.00 | 10900.00 | 338.80 | 16940.00 | 278.00 | 13900.00 | 505.00 | 25250.00 | 107.00 | 5350.00 | 5350.00 | S G TECHNOFAB PVT LTD
7.00 | Supplying, Fixing and commissioning of imported refrigerant joint/ Branch distributors indoor to outdoor complete with nitrile rubber insulation, supporting, etc, complete as per site requirement. | 12.00 | Each | 10.00 | 3600.00 | 43200.00 | 4035.00 | 48420.00 | 2772.00 | 33264.00 | 3700.00 | 44400.00 | 2800.00 | 33600.00 | 2750.00 | 33000.00 | 3500.00 | 42000.00 | 3684.00 | 44208.00 | 3802.00 | 45624.00 | 33000.00 | GLOBAL AIR TECNIX
8.00 | Supplying, Fixing and commissioning of imported refrigerant joint/ Branch distributors between Outdoor to outdoor complete with nitrile rubber insulation, supporting, etc, complete as per site requirement. | 8.00 | Each | 10.00 | 3500.00 | 28000.00 | 4035.00 | 32280.00 | 4185.00 | 33480.00 | 9000.00 | 72000.00 | 3200.00 | 25600.00 | 6050.00 | 48400.00 | 5500.00 | 44000.00 | 3684.00 | 29472.00 | 3293.00 | 26344.00 | 25600.00 | M/S COOLING CENTER
9.00 | Supplying, charging & testing of additional charge of Refrigerant R410-A including Pressure Testing, Vacumising, etc. complete as required. | 300.00 | KG | 10.00 | 850.00 | 255000.00 | 1060.00 | 318000.00 | 1141.00 | 342300.00 | 925.00 | 277500.00 | 580.00 | 174000.00 | 825.00 | 247500.00 | 620.00 | 186000.00 | 241.00 | 72300.00 | 895.00 | 268500.00 | 72300.00 | SHINRYO SUVIDHA ENGINEERS INDIA PRIVATE LIMITED
10.00 | Supply and installtion of hot dip G.I. cable tray perforation not more than 17.5% for specific dimensions along with tees, bends, reducers, cross members and other accessories such as suspender from ceiling/ fixed to wall with necessary angle/flat iron / hanging rod, clamps, anchor fastner, nuts, bolts, washers, etc. complete job as required. The tray shall be as follows :-
10.01 | 300 x 50 mm x 1.6mm thick | 80.00 | Meter | 10.00 | 410.00 | 32800.00 | 650.00 | 52000.00 | 800.00 | 64000.00 | 1250.00 | 100000.00 | 650.00 | 52000.00 | 670.65 | 53651.84 | 530.00 | 42400.00 | 837.00 | 66960.00 | 1002.00 | 80160.00 | 32800.00 | SAI H.V.A.C. SYSTEM
11.00 | DRAIN PIPING
11.01 | Supply and fixing of Rigid UPVC drain water piping complete with fittings, support as per specification and insulated with 06 mm thick insulated with closed cell Nitrile Rubber insulation.
11.02 | 25 mm dia ID | 50.00 | Meter | 10.00 | 120.00 | 6000.00 | 140.00 | 7000.00 | 127.00 | 6350.00 | 140.00 | 7000.00 | 120.00 | 6000.00 | 117.70 | 5885.00 | 103.00 | 5150.00 | 193.00 | 9650.00 | 160.00 | 8000.00 | 5150.00 | SAHU AGENCIES PRIVATE LIMITED
11.03 | 32 mm dia ID | 50.00 | Meter | 10.00 | 210.00 | 10500.00 | 200.00 | 10000.00 | 160.00 | 8000.00 | 155.00 | 7750.00 | 135.00 | 6750.00 | 132.00 | 6600.00 | 107.00 | 5350.00 | 236.00 | 11800.00 | 191.00 | 9550.00 | 5350.00 | SAHU AGENCIES PRIVATE LIMITED
11.04 | 40 mm dia ID | 80.00 | Meter | 10.00 | 240.00 | 19200.00 | 335.00 | 26800.00 | 230.00 | 18400.00 | 188.00 | 15040.00 | 140.00 | 11200.00 | 210.10 | 16808.00 | 123.00 | 9840.00 | 273.00 | 21840.00 | 228.00 | 18240.00 | 9840.00 | SAHU AGENCIES PRIVATE LIMITED
11.05 | 50 mm dia ID | 100.00 | Meter | 10.00 | 280.00 | 28000.00 | 440.00 | 44000.00 | 288.00 | 28800.00 | 205.00 | 20500.00 | 160.00 | 16000.00 | 297.00 | 29700.00 | 128.00 | 12800.00 | 349.00 | 34900.00 | 291.00 | 29100.00 | 12800.00 | SAHU AGENCIES PRIVATE LIMITED
12.00 | SHEET METAL DUCTING
12.01 | Supply, fabrication, erection and commissioning of factory /site fabricated rectangular/oval ducts of approved makes using GI Sheets as per site requirement and specification. The price shall include rolamate / TDF flanges, turning vanes, supports (factory fabricated, full threaded rod & GI slotted channel), sealent (neoprene gasket), hangers, access door etc. complete as required. All the longitudinal and transverse joints shall be sealed with silicon sealant. All ducts shall be pressure tested as per SMACNA standards for leaks at 2" WC pressure and be as per leakage class 24.
12.02 | 0.63 mm (24 Gauge) | 400.00 | Sq. Meter | 10.00 | 880.00 | 352000.00 | 820.00 | 328000.00 | 741.00 | 296400.00 | 925.00 | 370000.00 | 720.00 | 288000.00 | 1087.22 | 434887.20 | 975.00 | 390000.00 | 703.00 | 281200.00 | 931.00 | 372400.00 | 281200.00 | SHINRYO SUVIDHA ENGINEERS INDIA PRIVATE LIMITED
12.03 | 0.80mm (22 Gauge) | 600.00 | Sq. Meter | 10.00 | 950.00 | 570000.00 | 1060.00 | 636000.00 | 890.00 | 534000.00 | 1080.00 | 648000.00 | 820.00 | 492000.00 | 1172.19 | 703315.80 | 1180.00 | 708000.00 | 854.00 | 512400.00 | 979.00 | 587400.00 | 492000.00 | M/S COOLING CENTER
12.04 | 1.0mm (20 Gauge) | 50.00 | Sq. Meter | 10.00 | 1180.00 | 59000.00 | 1300.00 | 65000.00 | 1061.00 | 53050.00 | 1355.00 | 67750.00 | 930.00 | 46500.00 | 1377.27 | 68863.30 | 1380.00 | 69000.00 | 1049.00 | 52450.00 | 658.00 | 32900.00 | 32900.00 | S G TECHNOFAB PVT LTD
13.00 | DUCT DAMPERS/ DIFFUSERS/ GRILLES/ COLLAR DAMPERS
13.01 | Supply, installation, testing & balancing of Exhaust Valves for Toilet Exhaust, The valve should provided high initial resistance with wide throttling capability to offset the high system resistances, And finished with powder coating as per specifications & approved shop drawings of size ø 150mm. | 60.00 | Each | 10.00 | 550.00 | 33000.00 | 640.00 | 38400.00 | 429.00 | 25740.00 | 1800.00 | 108000.00 | 430.00 | 25800.00 | 990.00 | 59400.00 | 995.00 | 59700.00 | 680.00 | 40800.00 | 740.00 | 44400.00 | 25740.00 | KRISHNA REFRIGERATION
14.00 | SITC of Extruded Aluminum, Powder Coated fresh air damper. | 2.00 | Sq. Meter | 10.00 | 9735.00 | 19470.00 | 6660.00 | 13320.00 | 7174.00 | 14348.00 | 8850.00 | 17700.00 | 3800.00 | 7600.00 | 4373.66 | 8747.32 | 3990.00 | 7980.00 | 9772.00 | 19544.00 | 4806.00 | 9612.00 | 7600.00 | M/S COOLING CENTER
15.00 | SITC of Extruded Aluminum, Powder Coated Exhaust air louver | 2.00 | Sq. Meter | 10.00 | 9235.00 | 18470.00 | 6660.00 | 13320.00 | 8696.00 | 17392.00 | 8450.00 | 16900.00 | 3800.00 | 7600.00 | 6540.35 | 13080.70 | 5103.00 | 10206.00 | 5833.00 | 11666.00 | 4806.00 | 9612.00 | 7600.00 | M/S COOLING CENTER
16.00 | Supply, installation, testing and commissioning of aluminium powder coated supply and return air grilles/diffusers as per specifications and drawings.
16.01 | Supply Air Square/ liner Diffuser | 10.00 | Sq. Meter | 10.00 | 8103.00 | 81030.00 | 10750.00 | 107500.00 | 7826.00 | 78260.00 | 9900.00 | 99000.00 | 2500.00 | 25000.00 | 6466.63 | 64666.34 | 5800.00 | 58000.00 | 6813.00 | 68130.00 | 6603.00 | 66030.00 | 25000.00 | M/S COOLING CENTER
16.02 | Return Air Square/ liner Diffuser | 10.00 | Sq. Meter | 10.00 | 8103.00 | 81030.00 | 6860.00 | 68600.00 | 5870.00 | 58700.00 | 7520.00 | 75200.00 | 2500.00 | 25000.00 | 5214.85 | 52148.47 | 5800.00 | 58000.00 | 6813.00 | 68130.00 | 6603.00 | 66030.00 | 25000.00 | M/S COOLING CENTER
17.00 | Supply & installation of extruded aluminium volume control damper with blades, adjustable lever, frame etc for Supply Air and Fresh Air, as per specifications. | 10.00 | Sq. Meter | 10.00 | 8864.00 | 88640.00 | 5070.00 | 50700.00 | 5217.00 | 52170.00 | 8420.00 | 84200.00 | 3000.00 | 30000.00 | 5010.92 | 50109.23 | 4600.00 | 46000.00 | 3799.00 | 37990.00 | 4913.00 | 49130.00 | 30000.00 | M/S COOLING CENTER
18.00 | Supply & fixing of flexible connections constructed out of fire resistant double canvas sleeve as per specifications. | 5.00 | Sq. Meter | 10.00 | 7500.00 | 37500.00 | 4910.00 | 24550.00 | 1033.00 | 5165.00 | 3200.00 | 16000.00 | 2000.00 | 10000.00 | 4950.75 | 24753.75 | 2000.00 | 10000.00 | 2232.00 | 11160.00 | 1810.00 | 9050.00 | 5165.00 | KRISHNA REFRIGERATION
19.00 | THERMAL & ACOUSTIC INSULATION
19.01 | SITC of Thermal insulation of Supply air and Return air ducts for GI ducting as per specification using following thick closed cell Cross Linked Polyethylene Insulation with aluminium foil facing. Insulation in slab sections stuck to the duct & fixtures using manufacturer approved cold adhesive on both surface of the duct and inner face of the insulation slab section. The joints shall sealed with 48mm wide, 3mm thick self adehesive nitrile rubber tape.
19.02 | 13 mm thick insulation with Alu. foil | 400.00 | Sq. Meter | 10.00 | 210.00 | 84000.00 | 425.00 | 170000.00 | 272.00 | 108800.00 | 470.00 | 188000.00 | 320.00 | 128000.00 | 442.50 | 176999.46 | 913.00 | 365200.00 | 328.00 | 131200.00 | 235.00 | 94000.00 | 84000.00 | SAI H.V.A.C. SYSTEM
19.03 | 19 mm thick insulation with Alu. foil | 600.00 | Sq. Meter | 10.00 | 220.00 | 132000.00 | 515.00 | 309000.00 | 402.00 | 241200.00 | 582.00 | 349200.00 | 420.00 | 252000.00 | 516.26 | 309754.17 | 1153.00 | 691800.00 | 416.00 | 249600.00 | 847.00 | 508200.00 | 132000.00 | SAI H.V.A.C. SYSTEM
20.00 | SITC of Acoustic lining of ducting as per specification with 10mm thick open cell nitrile rubber foam of 140 to 180 kg/cum density, thermal conductivity 0.050w/mk and class 1 rating (Inside surface for the ducts shall be covered with adhesive recommended by manufacturer) | 40.00 | Sq. Meter | 10.00 | 440.00 | 17600.00 | 750.00 | 30000.00 | 1207.00 | 48280.00 | 810.00 | 32400.00 | 530.00 | 21200.00 | 726.83 | 29073.00 | 503.00 | 20120.00 | 664.00 | 26560.00 | 1939.00 | 77560.00 | 17600.00 | SAI H.V.A.C. SYSTEM
21.00 | Supply, Fabrication, Installation and Testing of the Insulated Flexible Ducting, complete with connecting rings, duct supports,The flexible duct shall be made of triple lamination of aluminium foil, polyester and Metalised Polyester film permanently bonded to a coated spring steel wire helix. The exterior shall be wrapped with 25mm thick 24 kg / m3 fibreglass insulation. The outer insulation jacket / vapour barrier shall be made of fibreglass reinforced Metalised Polyester film laminate etc. as per standards and specification.
21.01 | 300mm dia | 15.00 | Meter | 10.00 | 550.00 | 8250.00 | 425.00 | 6375.00 | 1837.00 | 27555.00 | 600.00 | 9000.00 | 450.00 | 6750.00 | 421.45 | 6321.75 | 501.00 | 7515.00 | 404.00 | 6060.00 | 593.00 | 8895.00 | 6060.00 | SHINRYO SUVIDHA ENGINEERS INDIA PRIVATE LIMITED
21.02 | 250 mm dia | 5.00 | Meter | 10.00 | 490.00 | 2450.00 | 340.00 | 1700.00 | 1543.00 | 7715.00 | 550.00 | 2750.00 | 350.00 | 1750.00 | 384.45 | 1922.26 | 453.00 | 2265.00 | 472.00 | 2360.00 | 593.00 | 2965.00 | 1700.00 | UNITY ENGINEERS
22.00 | Supply, Fabrication, installation and testing of the flexible ducting without insulation, complete with connecting rings, duct supports, inner core should be made of triple lamination of Aluminum Foil, Polyester & Metalized polyester film permanently bonded to a coated spring steel wire helix, etc as per standards and specification.
22.01 | 200mm dia | 5.00 | Meter | 10.00 | 395.00 | 1975.00 | 260.00 | 1300.00 | 1250.00 | 6250.00 | 400.00 | 2000.00 | 325.00 | 1625.00 | 299.97 | 1499.87 | 879.00 | 4395.00 | 222.00 | 1110.00 | 753.00 | 3765.00 | 1110.00 | SHINRYO SUVIDHA ENGINEERS INDIA PRIVATE LIMITED
22.02 | 150mm dia | 5.00 | Meter | 10.00 | 288.00 | 1440.00 | 215.00 | 1075.00 | 1087.00 | 5435.00 | 350.00 | 1750.00 | 300.00 | 1500.00 | 259.16 | 1295.82 | 348.00 | 1740.00 | 190.00 | 950.00 | 753.00 | 3765.00 | 950.00 | SHINRYO SUVIDHA ENGINEERS INDIA PRIVATE LIMITED
22.03 | 100mm dia | 5.00 | Meter | 10.00 | 288.00 | 1440.00 | 150.00 | 750.00 | 804.00 | 4020.00 | 250.00 | 1250.00 | 275.00 | 1375.00 | 236.93 | 1184.67 | 313.00 | 1565.00 | 176.00 | 880.00 | 753.00 | 3765.00 | 750.00 | UNITY ENGINEERS
23.00 | SITC of circular/cabinet inline fan complete with motor, BMS compatible starter, cabling between starter and fan etc. complete as required.
23.01 | 2000 CFM with 30 mm static | 3.00 | Each | 10.00 | 32485.00 | 97455.00 | 14700.00 | 44100.00 | 31522.00 | 94566.00 | 55000.00 | 165000.00 | 27000.00 | 81000.00 | 23454.55 | 70363.64 | 40301.00 | 120903.00 | 17973.00 | 53919.00 | 20504.00 | 61512.00 | 44100.00 | UNITY ENGINEERS
23.02 | 1000 CFM with 25 mm Static | 2.00 | Each | 10.00 | 25750.00 | 51500.00 | 10000.00 | 20000.00 | 16848.00 | 33696.00 | 33000.00 | 66000.00 | 22000.00 | 44000.00 | 9340.91 | 18681.82 | 35989.00 | 71978.00 | 16075.00 | 32150.00 | 16170.00 | 32340.00 | 18681.82 | GLOBAL AIR TECNIX
24.00 | Supply, Installation, Testing & Commissioning of Centralized Touch screen based Controller, suitable to control minimum 8 indoor unit, intelligent manager with required software for high speed transmission and necessary accessories including required cable/wire for connection termination of this system for complete installation at desired location at site etc complete as required. The following suitable controls shall be provided through this system for all indoor units indiviually:- 1) Temperature Controls, 2) ON/OFF Control, 3) Scheduling, 4) Monitoring & Control from a remote site. 5) Error Display | 2.00 | Each | 10.00 | 11092.00 | 22184.00 | 49600.00 | 99200.00 | 104891.00 | 209782.00 | 52200.00 | 104400.00 | 28000.00 | 56000.00 | 60000.00 | 120000.00 | 39500.00 | 79000.00 | 35724.00 | 71448.00 | 49620.00 | 99240.00 | 22184.00 | SAI H.V.A.C. SYSTEM
25.00 | L T PANELS
25.01 | Supplying, installation, testing and commissioning of cubical MV out door type electrical LT panel with IP 54 protection, suitable for 415 V, 3 phase, 50 Hz AC supply system fabricated in compartmentalised design from CRCA sheet steel of 2 mm thick for frame work and covers, 3mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, DMC/ SMC bus bar supports, bottom base channel of MS section not less than 100 mm x 50 mm x 5mm thick, fabrication shall be done in transportable sections, entire panel shall have a common aluminimum earth bar of size 50 mm x 5mm at the rear with 2 Nos. earth stud, soild connections from main bus bar to switch gears with required size of Al. bus bars and control wiring with 2.5 sq.mm. PVC insulated copper conductor S/C cable, cable alleys, cable gland plates. (as per specification & drawaing), i/c providing following switch gears:- INCOMING :- 320A, 35KA, FP MCCB (ICU=ICS) with Micro processor based release- 1 No. including Protection from Single phase preventer, Phase reversal, Overvoltage & undervoltage. Digital Voltmeter & Ammeter,- 1 set C.T's 300/5Amp , CL 1.0 - 01 set R,Y,B indicating LED- 01 set Control MCB-5A- 01 set Busbar: 500 Amps Aluminium TPN busbar - 1 Set OUTGOINGS :- 63 Amp, 25 KA, FP MCCB - 12 Nos. | 1.00 | Job | 10.00 | 310080.00 | 310080.00 | 211800.00 | 211800.00 | 418478.00 | 418478.00 | 275000.00 | 275000.00 | 165000.00 | 165000.00 | 317170.00 | 317170.00 | 86000.00 | 86000.00 | 246162.00 | 246162.00 | 211806.00 | 211806.00 | 86000.00 | SAHU AGENCIES PRIVATE LIMITED
26.00 | Supply, Installation, Testing and Commissioning of cubical type indoor LT panel with IP42 Protection, suitable for 415 V,3 phase, 50 Hz AC supply system fabricated in compartmentalised design from CRCA sheet steel of 2.0 mm thick for frame work and covers with LED indicator, etc. complete as required. (as per specification & drawaing) The following switch gears and accessories to be provided.MCCB shall be thermal magnetic release having overload, shortcicuit adjustable settings & Ics = Icu. Incomer: 63 Amp, 25 KA, FP MCCB (ICU=ICS) -01 No. (Tripping arrangement from the fire module should be made, as per requirement of site) Digital Voltmeter & Ammeter C.T's 100/5Amp , CL 1.0 R,Y,B indicating LED set Control MCB-5A Busbar: 150 Amp Aluminium TPN busbar. Outgoing: 32 Amp, 10KA, TPN MCB with DOL starter rated for 3HP with On /Off push buttons & LED Indicators - 8 sets | 2.00 | Job | 10.00 | 120600.00 | 241200.00 | 129500.00 | 259000.00 | 198370.00 | 396740.00 | 180000.00 | 360000.00 | 145000.00 | 290000.00 | 255200.00 | 510400.00 | 60000.00 | 120000.00 | 114987.00 | 229974.00 | 166250.00 | 332500.00 | 120000.00 | SAHU AGENCIES PRIVATE LIMITED
27.00 | Cable - Supply and laying
28.00 | Supply and laying, of 2C x 1.5 Sq. mm Copper conductor sheathed power control cum transmission cables with PVC conduit including fixing with clamps & proper connections to equipment etc.complete as required. | 1200.00 | Meter | 10.00 | 60.00 | 72000.00 | 125.00 | 150000.00 | 70.00 | 84000.00 | 117.00 | 140400.00 | 85.00 | 102000.00 | 66.87 | 80240.16 | 107.00 | 128400.00 | 107.00 | 128400.00 | 80.00 | 96000.00 | 72000.00 | SAI H.V.A.C. SYSTEM
29.00 | Supply of 4C X 2.5 sq. mm Power cable copper conductor, XLPE insulated, PVC sheathed, Armoured, 1100V grade as per IS 7098 (Part1) 1988 with upto date amendment etc., complete as required. | 600.00 | Meter | 10.00 | 110.00 | 66000.00 | 225.00 | 135000.00 | 147.00 | 88200.00 | 244.00 | 146400.00 | 140.00 | 84000.00 | 160.40 | 96239.29 | 183.00 | 109800.00 | 164.00 | 98400.00 | 514.00 | 308400.00 | 66000.00 | SAI H.V.A.C. SYSTEM
30.00 | Supply of 4C X 10 sq. mm. Power cable copper conductor, XLPE insulated, PVC sheathed, Armoured, 1100V grade as per IS 7098 (Part1) 1988 with upto date amendment etc., complete as required. | 200.00 | Meter | 10.00 | 310.00 | 62000.00 | 610.00 | 122000.00 | 463.00 | 92600.00 | 658.00 | 131600.00 | 210.00 | 42000.00 | 503.63 | 100725.97 | 663.00 | 132600.00 | 518.00 | 103600.00 | 577.00 | 115400.00 | 42000.00 | M/S COOLING CENTER
31.00 | Supply of 3.5X300 sqmm XLPE insulated & PVC sheathed, armoured aluminium conductor cable of 1.1KV grade as per latest IS code with up to date amendments etc. complete as required. | 100.00 | Meter | 10.00 | 610.00 | 61000.00 | 1850.00 | 185000.00 | 1306.00 | 130600.00 | 1975.00 | 197500.00 | 1400.00 | 140000.00 | 1541.17 | 154117.46 | 633.00 | 63300.00 | 1533.00 | 153300.00 | 353.00 | 35300.00 | 35300.00 | S G TECHNOFAB PVT LTD
32.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size above 185 sq. mm and upto 400 sq. mm direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. | 80.00 | Meter | 10.00 | 112.00 | 8960.00 | 470.00 | 37600.00 | 283.00 | 22640.00 | 1600.00 | 128000.00 | 1500.00 | 120000.00 | 275.00 | 22000.00 | 398.00 | 31840.00 | 279.00 | 22320.00 | 253.00 | 20240.00 | 8960.00 | SAI H.V.A.C. SYSTEM
33.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size above 185 sq. mm and upto 400 sq. mm in the existing masonry open duct as required. | 20.00 | Meter | 10.00 | 122.00 | 2440.00 | 235.00 | 4700.00 | 174.00 | 3480.00 | 900.00 | 18000.00 | 2200.00 | 44000.00 | 275.00 | 5500.00 | 550.00 | 11000.00 | 256.00 | 5120.00 | 127.00 | 2540.00 | 2440.00 | SAI H.V.A.C. SYSTEM
34.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size upto 35 sqmm on wall surface as required (clamped with 1mm thick saddle). | 200.00 | Meter | 10.00 | 416.00 | 83200.00 | 82.00 | 16400.00 | 65.00 | 13000.00 | 85.00 | 17000.00 | 50.00 | 10000.00 | 132.00 | 26400.00 | 303.00 | 60600.00 | 55.00 | 11000.00 | 69.00 | 13800.00 | 10000.00 | M/S COOLING CENTER
35.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size upto 35 sqmm on cable tray as required (clamped with 1mm thick saddle). | 600.00 | Meter | 10.00 | 547.00 | 328200.00 | 82.00 | 49200.00 | 87.00 | 52200.00 | 85.00 | 51000.00 | 50.00 | 30000.00 | 132.00 | 79200.00 | 303.00 | 181800.00 | 55.00 | 33000.00 | 253.00 | 151800.00 | 30000.00 | M/S COOLING CENTER
36.00 | Supplying and making end termination with brass compression gland and copper lugs for 4C X 10 sqmm of PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 KV grade as required. | 20.00 | Set | 10.00 | 490.00 | 9800.00 | 1175.00 | 23500.00 | 174.00 | 3480.00 | 180.00 | 3600.00 | 380.00 | 7600.00 | 550.00 | 11000.00 | 648.00 | 12960.00 | 213.00 | 4260.00 | 306.00 | 6120.00 | 3480.00 | KRISHNA REFRIGERATION
37.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3.5C X 300 sqmm of XLPE insulated and PVC sheathed Al conductor cable of 1.1 KV grade as required. | 2.00 | Set | 10.00 | 610.00 | 1220.00 | 10590.00 | 21180.00 | 1304.00 | 2608.00 | 450.00 | 900.00 | 1900.00 | 3800.00 | 1210.00 | 2420.00 | 5000.00 | 10000.00 | 658.00 | 1316.00 | 948.00 | 1896.00 | 900.00 | Sai Cooling Point Private Limited
38.00 | Supplying and making end termination with PG gland and copper lugs for following PVC insulated and PVC sheathed / XLPE copper conductor cable of 1.1 KV grade as required.
38.01 | 4 Core X 2.5 Sqmm Termination with PG Gland | 22.00 | Set | 10.00 | 150.00 | 3300.00 | 235.00 | 5170.00 | 65.00 | 1430.00 | 192.00 | 4224.00 | 175.00 | 3850.00 | 440.00 | 9680.00 | 135.00 | 2970.00 | 102.00 | 2244.00 | 184.00 | 4048.00 | 1430.00 | KRISHNA REFRIGERATION
38.02 | 2 Core X 1.5 Sqmm Termination with PG Gland | 22.00 | Set | 10.00 | 120.00 | 2640.00 | 190.00 | 4180.00 | 54.00 | 1188.00 | 192.00 | 4224.00 | 150.00 | 3300.00 | 440.00 | 9680.00 | 103.00 | 2266.00 | 88.00 | 1936.00 | 130.00 | 2860.00 | 1188.00 | KRISHNA REFRIGERATION
39.00 | Supply and fixing 8 SWG dia G.I. wire on surface or in recess for loop earthing as required | 300.00 | Meter | 10.00 | 140.00 | 42000.00 | 40.00 | 12000.00 | 17.00 | 5100.00 | 22.00 | 6600.00 | 20.00 | 6000.00 | 55.00 | 16500.00 | 98.00 | 29400.00 | 26.00 | 7800.00 | 155.00 | 46500.00 | 5100.00 | KRISHNA REFRIGERATION
40.00 | Part-B: Annual Cmprehensive Maintenance (Rate Prefixed)
41.00 | Annual Comprehensive Maintenance contract of all VRV/VRF system including all IDU & ODU of all capacity, including Referigerent & all copper pipes, drain pipe, axial fan, duct/PVC pipe with LT panel for ODU & IDU, split AC, including all installation of PART-A at extended Terminal Building, Gorarkpur Airport i/c carrying out monthly visit for servicing and maintenance of all components as per OEM standards by providing trained service engineer with all tools and plant and spares i/c attending all breakdown repairs, as & when required etc. complete as per specification & instructions of Engineer-in-Charge as required.
41.01 | For 1st Year after DLP (3% of Total of part-A) | 1.00 | Year | 10.00 | 224778.99 | 224778.99 | 310817.10 | 310817.10 | 281601.42 | 281601.42 | 320310.00 | 320310.00 | 217264.20 | 217264.20 | 331544.60 | 331544.60 | 276769.92 | 276769.92 | 262698.21 | 262698.21 | 283154.88 | 283154.88 | 217264.20 | M/S COOLING CENTER
41.02 | For 2nd Year after DLP (with 5% yearly cumulative escalation) | 1.00 | Year | 10.00 | 236017.94 | 236017.94 | 326357.95 | 326357.95 | 295681.49 | 295681.49 | 336325.50 | 336325.50 | 228127.41 | 228127.41 | 348121.83 | 348121.83 | 290608.42 | 290608.42 | 275833.12 | 275833.12 | 297312.62 | 297312.62 | 228127.41 | M/S COOLING CENTER
41.03 | For 3rd Year after DLP (with 5% yearly cumulative escalation) | 1.00 | Year | 10.00 | 247818.84 | 247818.84 | 342675.85 | 342675.85 | 310465.57 | 310465.57 | 353141.78 | 353141.78 | 239533.78 | 239533.78 | 365527.92 | 365527.92 | 305138.84 | 305138.84 | 289624.78 | 289624.78 | 312178.26 | 312178.26 | 239533.78 | M/S COOLING CENTER
41.04 | For 4th Year after DLP (with 5% yearly cumulative escalation) | 1.00 | Year | 10.00 | 260209.78 | 260209.78 | 359809.65 | 359809.65 | 325988.84 | 325988.84 | 370798.86 | 370798.86 | 251510.47 | 251510.47 | 383804.31 | 383804.31 | 320395.78 | 320395.78 | 304106.02 | 304106.02 | 327787.17 | 327787.17 | 251510.47 | M/S COOLING CENTER
41.05 | For 5th Year after DLP (with 5% yearly cumulative escalation) | 1.00 | Year | 10.00 | 273220.27 | 273220.27 | 377800.13 | 377800.13 | 342288.29 | 342288.29 | 389338.81 | 389338.81 | 264085.99 | 264085.99 | 402994.53 | 402994.53 | 336415.57 | 336415.57 | 319311.32 | 319311.32 | 344176.53 | 344176.53 | 264085.99 | M/S COOLING CENTER
| Total in Figures |  |  |  |  | 8734678.81 |  | 12078030.68 |  | 10942739.61 |  | 12446914.95 |  | 8442661.85 |  | 12883479.70 |  | 10754992.52 |  | 10208180.44 |  | 11003105.45
Lowest Amount Quoted BY: M/S COOLING CENTER(8442661.85)

## BOQ Summary
BOQ Summary Details Tender Title: Expansion of Passenger Terminal Building at Gorakhpur Civil Enclave Gorakhpur SH Provision of Air Conditioning VRV/VRF System Tender ID: 2021_AAI_96479_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/S COOLING CENTER | 8442661.85 | L1
| 2 | SAI H.V.A.C. SYSTEM | 8734678.81 | L2
| 3 | SHINRYO SUVIDHA ENGINEERS INDIA PRIVATE LIMITED | 10208180.44 | L3
| 4 | SAHU AGENCIES PRIVATE LIMITED | 10754992.52 | L4
| 5 | KRISHNA REFRIGERATION | 10942739.61 | L5
| 6 | S G TECHNOFAB PVT LTD | 11003105.45 | L6
| 7 | UNITY ENGINEERS | 12078030.68 | L7
| 8 | Sai Cooling Point Private Limited | 12446914.95 | L8
| 9 | GLOBAL AIR TECNIX | 12883479.70 | L9