## BoQ1
Government eProcurement System Created By: SINDHU L S Created Date/Time: 17-Dec-2021 11:43 AM Tender Title: PROVISION OF FIRE ALARM SYSTEM AT PUDUCHERRY AIRPORT Tender ID: 2021_AAI_96631_1
Tender Inviting Authority: SENIOR MANAGER (ENGG-ELECTRICAL), AAI, RHQ-SR, CHENNAI AIRPORT, CHENNAI - 600 027.
Name of Work: Provision of Fire Alarm system at Puducherry Airport.
Contract No: 2021_AAI_96631_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Item Code | Ponmani International (India) Pvt Ltd(GSTN-33AADCP6242R2ZZ) |  | RPN Systems And Solutions(GSTN-33AMEPL3915B1ZM)
[5 empty] | Rate Without Tax | Rate With Tax | Rate Without Tax | Rate With Tax | L1 Rate Without Tax | L1 Bidder Without Tax | L1 Rate With Tax | L1 Bidder With Tax
1.00 | SH 1
1.01 | Supply, installation, Testing & commissioning of UL/EN Listed 16 bit intelligent Addressable Fire Alarm Panel with 2 loops (each loop accessing at least 120 detectors ) including battery backup. The panel shal be microprocessor based with its own micro controller, memory, communication module and fire device loop interface cards for intelligent initiating and indicating devices and should also be networkable in peer-to-peer basis with other Addressable Fire Alarm Panels. The Panel shall be able to give pin point location of all Fire/Fault conditions of addressable units via the address codes for each unit. The Panel shall also be able to automatically switch off all control Switches when ever any Alarm is triggered. The Panel shall have Keypad operation, LCD unit to indicate Fire/Fault Signal of individual unit, etc complete in all respects. Battery shall be 54 Ah SMF type. The panel shall also have logic hardware and software built into it for initiating specific AHU tripping, time delay operation of hooter. Panel shall be networked to Main Panel. a)Programming software for the system b)automatic sytem test activates c)detector sensitivity adjustments d)alarm verification e)Alpha/numerical display f)provision to connect to PCs and external printers g)Support modbus/bacnet protocol (Make: As per list of approved makes) | 1.00 | Each | item1 | 144000.00 | 169920.00 | 135400.00 | 159772.00 | 135400.00 | RPN Systems And Solutions | 159772.00 | RPN Systems And Solutions
1.02 | Supply, installation, Testing & commissioning of Conventional Fire Alarm control Panel having minimum of 2 Zones suitable for connecting sensors manual call points, hooters and response indicators , operation with 220 Volts, 50 HZ Power supply , LCD display to indicate fire and normal operation & power supply status, Push button for accept and reset , sealed lead acid batteries with 2 Nos 12V, 7AH battery backup on alarm mode & normal operation with battery charger etc., shall be complete etc as required. (Make: As per list of approved makes) | 1.00 | Each | item2 | 9700.00 | 11446.00 | 14300.00 | 16874.00 | 9700.00 | Ponmani International (India) Pvt Ltd | 11446.00 | Ponmani International (India) Pvt Ltd
1.03 | Supply, Installation, Testing & Commissioning of UL/EN Listed Repeater panel for addressable Fire Alarm system with Piezosounder, LCD alpha numeric character display with accept/rest buttons for alarm address of any sensor/field address with room number etc as required. (Make: As per list of approved makes) | 1.00 | Each | item3 | 59600.00 | 70328.00 | 42000.00 | 49560.00 | 42000.00 | RPN Systems And Solutions | 49560.00 | RPN Systems And Solutions
1.04 | Supply, Installation, Testing & Commissioning of Auto Dialer for Fire Alarm system suitable to work with existing landline line telephone connections etc as required. | 1.00 | Each | item4 | 4000.00 | 4720.00 | 6500.00 | 7670.00 | 4000.00 | Ponmani International (India) Pvt Ltd | 4720.00 | Ponmani International (India) Pvt Ltd
1.05 | Supply & fixing of Photoelectric, Multi sensor smoke detectors along with mounting base with unique optical sensing chamber, visible LED's fully coated circuit boards with RF/transient protection, complete with all accessories including connections etc. as required. (Make: As per list of approved makes) | 27.00 | Each | item5 | 33480.00 | 39506.40 | 26730.00 | 31541.40 | 26730.00 | RPN Systems And Solutions | 31541.40 | RPN Systems And Solutions
1.06 | Supply, installation, Testing & commissioning of UL/EN Listed Analogue Addressable type Optical Smoke Detector complete with all accessories like base, base box, etc., to be installed under/above false ceilling, roof and concealed space, etc., interconnecting to loop cable complete as required. (Make: As per list of approved makes) | 19.00 | Each | item6 | 38950.00 | 45961.00 | 44650.00 | 52687.00 | 38950.00 | Ponmani International (India) Pvt Ltd | 45961.00 | Ponmani International (India) Pvt Ltd
1.07 | Supply, installation, testing and commissioning of UL/EN Listed intelligent Addressable type Optical Smoke cum heat Detector (3D) complete with all accessories like base, base box, etc to be installed under/above false ceiling, roof and concealed space etc. interconnecting to loop cable complete as required. (Make: As per list of approved makes) | 8.00 | Each | item7 | 17680.00 | 20862.40 | 20400.00 | 24072.00 | 17680.00 | Ponmani International (India) Pvt Ltd | 20862.40 | Ponmani International (India) Pvt Ltd
1.08 | Supply, installation, testing and commissioning of UL/EN Listed Analogue Addressable type heat Detector (fixed cum rate of rise type) with range 60 Degree complete with all accessories like base, base box, etc to be installed under/above false ceiling, roof and concealed space etc. interconnecting to loop cable complete as required. (Make: As per list of approved makes) | 1.00 | Each | item8 | 2110.00 | 2489.80 | 2350.00 | 2773.00 | 2110.00 | Ponmani International (India) Pvt Ltd | 2489.80 | Ponmani International (India) Pvt Ltd
1.09 | Supply, installation, testing and commissioning of response Indicators outside the rooms for getting fire indications of detectors installed above false ceiling area interconnecting to loop cable complete as required. (Make: As per list of approved makes) | 7.00 | Each | item9 | 1400.00 | 1652.00 | 1540.00 | 1817.20 | 1400.00 | Ponmani International (India) Pvt Ltd | 1652.00 | Ponmani International (India) Pvt Ltd
1.10 | Supply, installation, testing and commissioning of UL/EN Listed Addressable type Manual Call Point (break glass / pull station type) complete with input Module, Push Botton, enclosed in box with provision for cable or conduit coupling. (Make: As per list of approved makes) | 7.00 | Each | item10 | 20230.00 | 23871.40 | 17360.00 | 20484.80 | 17360.00 | RPN Systems And Solutions | 20484.80 | RPN Systems And Solutions
1.11 | Providing , installing, testing and commissioning of UL /EN Listed Hooter cum Strobe complete with Base plate, box etc., as required. (Make: As per list of approved makes) | 10.00 | Each | item11 | 44700.00 | 52746.00 | 22200.00 | 26196.00 | 22200.00 | RPN Systems And Solutions | 26196.00 | RPN Systems And Solutions
1.12 | Supply Installation, testing and commissioing of UL/EN Listed Infra Red Beam detector reflective type for up to 100m span and 15m width, complete with Transmitter, receiver, brackets and Input Module complete with four square reflector, all fixing accesssories like base, base box, etc. to be installed on wall, connected space, etc. interconnecting to to loop cable complete as required and PVC flexible conduit. (Make: As per list of approved makes) | 3.00 | Each | item12 | 123000.00 | 145140.00 | 103500.00 | 122130.00 | 103500.00 | RPN Systems And Solutions | 122130.00 | RPN Systems And Solutions
1.13 | Supply Installation, testing and commissioing of addressable and automatic commandable control modules etc as required. | 4.00 | Each | item13 | 13120.00 | 15481.60 | 9000.00 | 10620.00 | 9000.00 | RPN Systems And Solutions | 10620.00 | RPN Systems And Solutions
1.14 | Supply Installation, testing and commissioning of addressable loop Isolators etc as required. | 2.00 | Each | item14 | 4800.00 | 5664.00 | 4500.00 | 5310.00 | 4500.00 | RPN Systems And Solutions | 5310.00 | RPN Systems And Solutions
1.15 | Supply and laying of MS steel conduits ISI Marked red painted with all fittings and saddles for drawing detector control cables on surface /recess/above false ceiling/concealed space/wall concealed, etc of following sizes: 20 mm (Make: As per list of approved makes) | 500.00 | Meter | item15 | 92500.00 | 109150.00 | 45000.00 | 53100.00 | 45000.00 | RPN Systems And Solutions | 53100.00 | RPN Systems And Solutions
1.16 | Supply and laying of following size PVC insulated FRLS 2Cx1.5sq.mm copper conductor cable through conduits/surface/recess/above false ceiling/concealed space/wall concealed, etc. for control cabling for Fire detection & alarm devices and interconnecting etc as required. (Make: As per list of approved makes) | 500.00 | Meter | item16 | 35000.00 | 41300.00 | 32500.00 | 38350.00 | 32500.00 | RPN Systems And Solutions | 38350.00 | RPN Systems And Solutions
| Total in Figures |  |  |  | 644270.00 | 760238.60 | 527930.00 | 622957.40

## BOQ Summary
BOQ Summary Details Tender Title: PROVISION OF FIRE ALARM SYSTEM AT PUDUCHERRY AIRPORT Tender ID: 2021_AAI_96631_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | RPN Systems And Solutions | 622957.40 | L1
| 2 | Ponmani International (India) Pvt Ltd | 760238.60 | L2