## BoQ1
Government eProcurement System Created By: RAMESH BABU K Created Date/Time: 17-Jan-2022 05:30 PM Tender Title: Miscellaneous Electrical Works at Chennai Airport SH Providing Standby LT Power Supply at T1 T4 Carpark area external installations at Chennai Airport Chennai BALANCE WORK Tender ID: 2021_AAI_99470_1
Tender Inviting Authority: Jt. General Manager (Engg-Elect)-III, Electrical Maintenance Division-II, Operational Offices, Airports Authority of India, Chennai Airport, Chennai –600 016,
Name of Work:Miscellaneous Electrical Works at Chennai Airport. SH: Providing Standby LT Power Supply at T1 & T4 Carpark area External Installations at Chennai Airport, Chennai. – BALANCE WORK
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/s LEESHA ELECTRICALS(GSTN-27ABAPW8550C1ZK) |  | DEEPAKELECTRICALS(GSTN-33ALUPD3531C1ZI) |  | Shantha ELectricals and Engineers Pvt Ltd(GSTN-29AARCS2866G1ZP) |  | Aim electricals(GSTN-29ABMFA8709M1ZP) |  | vk sam engineering(GSTN-33AMZPS4037L1ZA) |  | CHENNAI ENGINEERING SERVICES(GSTN-33AADFC4373K1ZH) |  | PREMIER ENGINEERING TECHNICS PVT. LTD.(GSTN-27AADCP1420F1ZW) |  | SKYLINE ELECTRICALS(GSTN-36AHNPJ7347K1ZR) |  | SANGYA SAHARSHINI INFRA(GSTN-NA) |  | DElite System Engineering (India) Pvt. Ltd.(GSTN-NA) |  | HRI ASSOCIATES(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Fabrication, Supply, Installation, Testing & Commissioning of Outdoor MV Feeder Pillar Panel with IP65 double door arrangement, outer shell made up of 3mm and inner front, top covers and partitions made up of 2mm CRCA sheet steel, door dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing, including providing and fixing 400A Aluminium Bus bar with all accessorieswelding and earthing suitable for operation at 433 V, 3 phase, 4 wire, 50 Hz, A.C. Power Supply System complete with all accessories, interconnection, connection, earthing, painting, grouting, providing pedestal, Cable Entry provision etc. as required i/c. dismantling the old panel and handed over to AAI store and providing required brick pedestal etc. complete and comprising of following:-
1.10 | a. 200Amps ON Load Change over Switch and 200A, 35 KA, 4P MCCB with Thermal magnetic releases as incomer with R,Y,B,ON, OFF, TRIP indication lamps, resin cast CT's with multifunction meter - 1 set as incomer.
1.20 | b. 63A, 25KA, 4P MCCB with thermal magnetic releases as incomer with ON, OFF, TRIP indication lamps, resin cast CT's with digital meter as outgoing - 6 Sets. As outgoing.
1.30 | c. TP contact MNX80, L&T or equivalent contractor with 24 hrs. digital timer along with 2A, SP MCB and control wiring for Street light/Hi-mast lighting control - 1 set. with all necessary accessories etc. complete as required. (a to c above) | 1.00 | Job | 100.00 | 354936.00 | 354936.00 | 450000.00 | 450000.00 | 280000.00 | 280000.00 | 285000.00 | 285000.00 | 315000.00 | 315000.00 | 305299.00 | 305299.00 | 370000.00 | 370000.00 | 205000.00 | 205000.00 | 154600.00 | 154600.00 | 370999.00 | 370999.00 | 295000.00 | 295000.00 | 154600.00 | SANGYA SAHARSHINI INFRA
2.00 | Supply and fixing of 100amps Four pole ON Load Change over switch including Extendable handle in the existing feeder pillar including connection etc., as required L&T make Cat No.CO11000OOOO or equivalent etc., as required. | 4.00 | Nos | 100.00 | 5550.00 | 22200.00 | 9500.00 | 38000.00 | 7500.00 | 30000.00 | 6500.00 | 26000.00 | 5700.00 | 22800.00 | 12499.00 | 49996.00 | 7750.00 | 31000.00 | 8000.00 | 32000.00 | 5999.00 | 23996.00 | 15000.00 | 60000.00 | 25000.00 | 100000.00 | 22200.00 | M/s LEESHA ELECTRICALS
3.00 | Supply and fixing of 100amps Four pole ON Load Change over switch including Extendable handle in the existing feeder pillar including connection etc., as required L&T make Cat No.CO11000OOOO or equivalent etc., as required. | 2.00 | Nos | 10.00 | 9900.00 | 19800.00 | 9500.00 | 19000.00 | 7500.00 | 15000.00 | 6500.00 | 13000.00 | 5700.00 | 11400.00 | 12499.00 | 24998.00 | 12000.00 | 24000.00 | 8000.00 | 16000.00 | 5999.00 | 11998.00 | 15000.00 | 30000.00 | 25000.00 | 50000.00 | 11400.00 | vk sam engineering
4.00 | Supplying and laying of following size DWC HDPE pipe of approved make along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc., direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required.
4.10 | a) OD - 63mm (Nominal) & ID-51mm (Nominal) | 500.00 | Mtrs | 10.00 | 200.00 | 100000.00 | 210.00 | 105000.00 | 175.00 | 87500.00 | 250.00 | 125000.00 | 178.00 | 89000.00 | 259.00 | 129500.00 | 235.00 | 117500.00 | 240.00 | 120000.00 | 441.00 | 220500.00 | 200.00 | 100000.00 | 100.00 | 50000.00 | 50000.00 | HRI ASSOCIATES
4.20 | b) OD - 120mm (Nominal) & ID-103mm (Nominal) | 300.00 | Mtrs | 10.00 | 230.00 | 69000.00 | 280.00 | 84000.00 | 320.00 | 96000.00 | 325.00 | 97500.00 | 240.00 | 72000.00 | 319.00 | 95700.00 | 325.00 | 97500.00 | 290.00 | 87000.00 | 498.00 | 149400.00 | 230.00 | 69000.00 | 125.00 | 37500.00 | 37500.00 | HRI ASSOCIATES
5.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
5.10 | a) Upto 35 sq. mm | 400.00 | Mtrs | 10.00 | 30.00 | 12000.00 | 22.00 | 8800.00 | 70.00 | 28000.00 | 95.00 | 38000.00 | 35.00 | 14000.00 | 19.00 | 7600.00 | 30.00 | 12000.00 | 45.00 | 18000.00 | 41.00 | 16400.00 | 22.00 | 8800.00 | 35.00 | 14000.00 | 7600.00 | CHENNAI ENGINEERING SERVICES
5.20 | b) Above 35 sq. mm and upto 95 sq. mm | 450.00 | Mtrs | 10.00 | 30.00 | 13500.00 | 27.00 | 12150.00 | 95.00 | 42750.00 | 160.00 | 72000.00 | 50.00 | 22500.00 | 29.00 | 13050.00 | 50.00 | 22500.00 | 65.00 | 29250.00 | 61.00 | 27450.00 | 25.00 | 11250.00 | 45.00 | 20250.00 | 11250.00 | DElite System Engineering (India) Pvt. Ltd.
6.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
6.10 | a) up to 35 sq. mm (clamped with 1mm thick saddle) | 300.00 | Mtrs | 10.00 | 40.00 | 12000.00 | 31.00 | 9300.00 | 65.00 | 19500.00 | 105.00 | 31500.00 | 55.00 | 16500.00 | 49.00 | 14700.00 | 65.00 | 19500.00 | 60.00 | 18000.00 | 70.00 | 21000.00 | 22.00 | 6600.00 | 55.00 | 16500.00 | 6600.00 | DElite System Engineering (India) Pvt. Ltd.
6.20 | b) Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 120.00 | Mtrs | 10.00 | 40.00 | 4800.00 | 37.00 | 4440.00 | 110.00 | 13200.00 | 175.00 | 21000.00 | 65.00 | 7800.00 | 59.00 | 7080.00 | 120.00 | 14400.00 | 85.00 | 10200.00 | 95.00 | 11400.00 | 30.00 | 3600.00 | 65.00 | 7800.00 | 3600.00 | DElite System Engineering (India) Pvt. Ltd.
7.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
7.10 | a) Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 200.00 | Mtrs | 10.00 | 40.00 | 8000.00 | 37.00 | 7400.00 | 120.00 | 24000.00 | 160.00 | 32000.00 | 75.00 | 15000.00 | 99.00 | 19800.00 | 85.00 | 17000.00 | 70.00 | 14000.00 | 199.00 | 39800.00 | 35.00 | 7000.00 | 65.00 | 13000.00 | 7000.00 | DElite System Engineering (India) Pvt. Ltd.
8.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE armoured aluminium conductor cable of 1.1 KV grade as required.
8.10 | a) 3.5 x 35 Sq.mm. | 16.00 | Sets | 10.00 | 300.00 | 4800.00 | 200.00 | 3200.00 | 750.00 | 12000.00 | 450.00 | 7200.00 | 200.00 | 3200.00 | 249.00 | 3984.00 | 375.00 | 6000.00 | 426.00 | 6816.00 | 199.00 | 3184.00 | 500.00 | 8000.00 | 250.00 | 4000.00 | 3184.00 | SANGYA SAHARSHINI INFRA
8.20 | b) 3.5 x 50 Sq. mm. | 4.00 | sets | 10.00 | 300.00 | 1200.00 | 310.00 | 1240.00 | 950.00 | 3800.00 | 550.00 | 2200.00 | 325.00 | 1300.00 | 349.00 | 1396.00 | 425.00 | 1700.00 | 465.00 | 1860.00 | 199.00 | 796.00 | 500.00 | 2000.00 | 300.00 | 1200.00 | 796.00 | SANGYA SAHARSHINI INFRA
8.30 | c) 3.5 x 70 Sq.mm. | 4.00 | Sets | 10.00 | 300.00 | 1200.00 | 350.00 | 1400.00 | 1100.00 | 4400.00 | 650.00 | 2600.00 | 325.00 | 1300.00 | 449.00 | 1796.00 | 475.00 | 1900.00 | 765.00 | 3060.00 | 250.00 | 1000.00 | 500.00 | 2000.00 | 350.00 | 1400.00 | 1000.00 | SANGYA SAHARSHINI INFRA
8.40 | d) 3.5 x 95 Sq.mm. | 10.00 | Sets | 10.00 | 500.00 | 5000.00 | 400.00 | 4000.00 | 1300.00 | 13000.00 | 750.00 | 7500.00 | 450.00 | 4500.00 | 549.00 | 5490.00 | 625.00 | 6250.00 | 1200.00 | 12000.00 | 250.00 | 2500.00 | 500.00 | 5000.00 | 400.00 | 4000.00 | 2500.00 | SANGYA SAHARSHINI INFRA
9.00 | Supply and making straight through cable joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated PVC sheathed/XLPE Aluminium conductor power cable of 1.1KV grade as required.
9.10 | a) 3.5 x 35 Sq.mm. | 4.00 | Job | 10.00 | 1500.00 | 6000.00 | 1200.00 | 4800.00 | 6500.00 | 26000.00 | 2000.00 | 8000.00 | 2000.00 | 8000.00 | 2499.00 | 9996.00 | 2000.00 | 8000.00 | 2200.00 | 8800.00 | 4559.00 | 18236.00 | 1999.00 | 7996.00 | 2500.00 | 10000.00 | 4800.00 | DEEPAKELECTRICALS
9.20 | b) 3.5 x 50 sq.mm | 2.00 | Jobs | 10.00 | 1600.00 | 3200.00 | 1500.00 | 3000.00 | 5800.00 | 11600.00 | 2000.00 | 4000.00 | 2000.00 | 4000.00 | 2999.00 | 5998.00 | 2300.00 | 4600.00 | 2200.00 | 4400.00 | 4559.00 | 9118.00 | 1999.00 | 3998.00 | 3000.00 | 6000.00 | 3000.00 | DEEPAKELECTRICALS
9.30 | c) 3.5 x 70 sq.mm | 2.00 | Jobs | 10.00 | 2000.00 | 4000.00 | 1900.00 | 3800.00 | 6500.00 | 13000.00 | 2000.00 | 4000.00 | 3000.00 | 6000.00 | 3499.00 | 6998.00 | 2800.00 | 5600.00 | 2600.00 | 5200.00 | 8100.00 | 16200.00 | 2500.00 | 5000.00 | 3500.00 | 7000.00 | 3800.00 | DEEPAKELECTRICALS
9.40 | d) 3.5 x 95 sq.mm | 4.00 | Jobs | 10.00 | 2100.00 | 8400.00 | 2500.00 | 10000.00 | 7800.00 | 31200.00 | 2500.00 | 10000.00 | 3000.00 | 12000.00 | 3999.00 | 15996.00 | 3000.00 | 12000.00 | 2600.00 | 10400.00 | 8100.00 | 32400.00 | 3500.00 | 14000.00 | 4000.00 | 16000.00 | 8400.00 | M/s LEESHA ELECTRICALS
10.00 | Providing & Laying of 100mm dia 'B' class G.I pipe with GI fittings i/c Concrete road cutting, excavation, laying the G. I Pipe in depth of 30cm, re-filling with cement concrete 1:2:4 and making good the same etc., as required.
10.10 | a) 100 mm dia. | 125.00 | Mtrs | 10.00 | 1450.00 | 181250.00 | 1500.00 | 187500.00 | 2800.00 | 350000.00 | 1200.00 | 150000.00 | 2200.00 | 275000.00 | 2999.00 | 374875.00 | 2200.00 | 275000.00 | 1980.00 | 247500.00 | 1699.00 | 212375.00 | 2200.00 | 275000.00 | 1125.00 | 140625.00 | 140625.00 | HRI ASSOCIATES
11.00 | Providing & Laying of 100mm dia 'B' class G.I pipe with GI fittings i/c cutting Bituminous surface, (30cm deep) re-filling with cement concrete and making good surface the same as required.
11.10 | a) 100 mm dia. | 125.00 | Mtrs | 10.00 | 1400.00 | 175000.00 | 1400.00 | 175000.00 | 2300.00 | 287500.00 | 1200.00 | 150000.00 | 2200.00 | 275000.00 | 3499.00 | 437375.00 | 2000.00 | 250000.00 | 2050.00 | 256250.00 | 1699.00 | 212375.00 | 1500.00 | 187500.00 | 1125.00 | 140625.00 | 140625.00 | HRI ASSOCIATES
12.00 | Earthing with Copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement, 20mm GI watering pipe of 2.7 metre long and 40mm GI Pipe of 2.7metre long for supply and laying of 25 X 5mm thick copper strip with charcoal/ coke and salt etc., as required. | 25.00 | Jobs | 10.00 | 17500.00 | 437500.00 | 15000.00 | 375000.00 | 18000.00 | 450000.00 | 24750.00 | 618750.00 | 21000.00 | 525000.00 | 14999.00 | 374975.00 | 15000.00 | 375000.00 | 19000.00 | 475000.00 | 12000.00 | 300000.00 | 15000.00 | 375000.00 | 15000.00 | 375000.00 | 300000.00 | SANGYA SAHARSHINI INFRA
13.00 | Constructing masonry Chamber 60x60x75 cm inside, in brick work in cement mortar 1:4 (1 cement : 4 coarse sand) for cable chamber, with C.I. surface box 100mm top diameter, 160 mm bottom diameter and 180 mm deep ( inside) with chained lid and RCC top slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size ) , i/c necessary excavation, foundation concrete 1:5:10 (1 cement : 5 fine sand : 10 graded stone aggregate 40 mmnominal size) and inside plastering with cement mortar 1:3 (1 cement : 3 coarse sand) 12 mm thick, finished with a floating coat of neat cement complete as per standard design etc., as required. | 20.00 | Jobs | 10.00 | 500.00 | 10000.00 | 9000.00 | 180000.00 | 12000.00 | 240000.00 | 12000.00 | 240000.00 | 9500.00 | 190000.00 | 9999.00 | 199980.00 | 10000.00 | 200000.00 | 8000.00 | 160000.00 | 4800.00 | 96000.00 | 10000.00 | 200000.00 | 8000.00 | 160000.00 | 10000.00 | M/s LEESHA ELECTRICALS
14.00 | Supplying and laying 25 mm X 3 mm thick copper strip inside of 40mm G.I. Pipe ground/surface as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by bolt & spring washer spaced at 50mm) overlapping and with 2 sets of brass nut etc., as required. | 120.00 | Mtrs | 10.00 | 1200.00 | 144000.00 | 675.00 | 81000.00 | 980.00 | 117600.00 | 900.00 | 108000.00 | 1300.00 | 156000.00 | 1499.00 | 179880.00 | 1100.00 | 132000.00 | 680.00 | 81600.00 | 1589.00 | 190680.00 | 900.00 | 108000.00 | 850.00 | 102000.00 | 81000.00 | DEEPAKELECTRICALS
15.00 | Providing and fixing 25mm X 3mm copper strip on surface or in recess for connections etc., as required. | 150.00 | Mtrs | 10.00 | 800.00 | 120000.00 | 650.00 | 97500.00 | 950.00 | 142500.00 | 900.00 | 135000.00 | 775.00 | 116250.00 | 999.00 | 149850.00 | 700.00 | 105000.00 | 650.00 | 97500.00 | 999.00 | 149850.00 | 900.00 | 135000.00 | 650.00 | 97500.00 | 97500.00 | HRI ASSOCIATES, DEEPAKELECTRICALS, SKYLINE ELECTRICALS
16.00 | Replacement of existing broken and damaged RCC/CI earth pit enclosure with new 10mm thick MS chequred cover plate having locking arrangement with providing and fixing suitable size base frame on the existing earth pit chamber including civil works and making good surface the same etc., as required. | 25.00 | Jobs | 10.00 | 1000.00 | 25000.00 | 750.00 | 18750.00 | 6500.00 | 162500.00 | 3000.00 | 75000.00 | 3250.00 | 81250.00 | 4999.00 | 124975.00 | 1000.00 | 25000.00 | 1000.00 | 25000.00 | 889.00 | 22225.00 | 2000.00 | 50000.00 | 1200.00 | 30000.00 | 18750.00 | DEEPAKELECTRICALS
| Total in Figures |  |  |  |  | 1742786.00 |  | 1884280.00 |  | 2501050.00 |  | 2263250.00 |  | 2244800.00 |  | 2561287.00 |  | 2133450.00 |  | 1944836.00 |  | 1943483.00 |  | 2045743.00 |  | 1699400.00
Lowest Amount Quoted BY: HRI ASSOCIATES(1699400.00)

## BOQ Summary
BOQ Summary Details Tender Title: Miscellaneous Electrical Works at Chennai Airport SH Providing Standby LT Power Supply at T1 T4 Carpark area external installations at Chennai Airport Chennai BALANCE WORK Tender ID: 2021_AAI_99470_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | HRI ASSOCIATES | 1699400.00 | L1
| 2 | M/s LEESHA ELECTRICALS | 1742786.00 | L2
| 3 | DEEPAKELECTRICALS | 1884280.00 | L3
| 4 | SANGYA SAHARSHINI INFRA | 1943483.00 | L4
| 5 | SKYLINE ELECTRICALS | 1944836.00 | L5
| 6 | DElite System Engineering (India) Pvt. Ltd. | 2045743.00 | L6
| 7 | PREMIER ENGINEERING TECHNICS PVT. LTD. | 2133450.00 | L7
| 8 | vk sam engineering | 2244800.00 | L8
| 9 | Aim electricals | 2263250.00 | L9
| 10 | Shantha ELectricals and Engineers Pvt Ltd | 2501050.00 | L10
| 11 | CHENNAI ENGINEERING SERVICES | 2561287.00 | L11