## BoQ1
Government eProcurement System Created By: SUDHAKARA NAIK Created Date/Time: 08-Feb-2022 12:41 PM Tender Title: Construction of 10.5 m wide link taxi track connecting runway to the proposed FTO at Belagavi Airport. SH- Provision of Taxiway Lighting and Apron Flood Lighting Tender ID: 2021_AAI_99845_2
Tender Inviting Authority: Assistant General Manager (Engg-E), AAI, Belagavi Airport. Contact No.- 9513303290 / 8217365822
Name of Work: Construction of 10.5 m wide link taxi track connecting runway to the proposed FTO at Belagavi Airport. SH: Provision of Taxiway Lighting and Apron Flood Lighting.
Contract No: 2021_AAI_99845_2
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | jaydeep agency corporation(GSTN-24ACIPP6157B1ZQ) |  | Balaji Engineering(GSTN-33ADGPV2628A1ZV) |  | Taral Electricals(GSTN-24ACMPR0280M1Z9) |  | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED(GSTN-07ABDCS2796Q1ZH) |  | Vardhman Airport Solutions Pvt Ltd(GSTN-07AAECN5914F1ZK) |  | Techno Electricals(GSTN-24AAGFT9086M1ZG) |  | CREATIVE TRADING CO(GSTN-07AMEPK8023F1Z9) |  | Manish Electricals(GSTN-22ABLPM9012E1ZY) |  | DElite System Engineering (India) Pvt. Ltd.(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | TAXIWAY & APRON LIGHTING: INSET FITTINGS:
1.01 | Supply of Inset Type Runway Edge Light Fitting complete with bottom box and all accessories including 2X105W halogen lamp, lens / filter, reflector etc. as required and as specified. Left Clear/Right Clear | 2.00 | Each | 5.00 | 17500.00 | 35000.00 | 60000.00 | 120000.00 | 68212.50 | 136425.00 | 75000.00 | 150000.00 | 63471.00 | 126942.00 | 62000.00 | 124000.00 | 60000.00 | 120000.00 | 63500.00 | 127000.00 | 69000.00 | 138000.00 | 35000.00 | jaydeep agency corporation
1.02 | Installation, Testing and Commissioning of inset fitting with core cutting, aligning and setting i/c providing sealing material and installation of Isolating Transformer, Crimping / Jointing of Plug receptacles, laying of secondary lead in existing GI pipe in groove i/c cutting & sealing of groove & other accessories required for commissioning i/c supply of all materials except fixture, secondary lead, plug & receptacles & isolating transformer etc. as required. | 2.00 | Each | 5.00 | 3800.00 | 7600.00 | 10000.00 | 20000.00 | 9562.50 | 19125.00 | 10000.00 | 20000.00 | 12000.00 | 24000.00 | 7500.00 | 15000.00 | 6000.00 | 12000.00 | 6500.00 | 13000.00 | 6000.00 | 12000.00 | 7600.00 | jaydeep agency corporation
1.03 | Dismantling of HIRL/MIRL fixtures on the existing runway circuit. | 2.00 | Job | 5.00 | 8500.00 | 17000.00 | 250.00 | 500.00 | 701.25 | 1402.50 | 5000.00 | 10000.00 | 328.00 | 656.00 | 150.00 | 300.00 | 100.00 | 200.00 | 100.00 | 200.00 | 200.00 | 400.00 | 200.00 | CREATIVE TRADING CO, Manish Electricals
2.00 | TAXI WAY
2.01 | Supply of LED Type Elevated MIRL Taxiway Edge light fixtures up to 15 Watts & meeting ICAO requirments LED lamp of series circuit 2.8 - 6.6 amps current, complete with LED, LED driver, base plate, breakable coupling, mounting assembly, gasket, BLUE lens, one 2 pole-plug with leads etc. conforming to particular specification etc complete as required. | 50.00 | Each | 5.00 | 9800.00 | 490000.00 | 4500.00 | 225000.00 | 8287.50 | 414375.00 | 7500.00 | 375000.00 | 3750.00 | 187500.00 | 5500.00 | 275000.00 | 4500.00 | 225000.00 | 4800.00 | 240000.00 | 11000.00 | 550000.00 | 187500.00 | Vardhman Airport Solutions Pvt Ltd
2.02 | Installation, testing and commisiong of HIRL /MIRL elevated type (Suitable for Halogen lamp) type fittings on the existing transformer housing boxes including installation of transformer, lens, lamps gasket,nut bolts, lens holding clamp and other accessories i/c alignment, levelling,isolating transformer, connection, earth connection etc. complete as required. | 50.00 | Each | 5.00 | 750.00 | 37500.00 | 250.00 | 12500.00 | 376.38 | 18819.00 | 2500.00 | 125000.00 | 328.00 | 16400.00 | 150.00 | 7500.00 | 100.00 | 5000.00 | 200.00 | 10000.00 | 2000.00 | 100000.00 | 5000.00 | CREATIVE TRADING CO
2.03 | Supply of C.I. Isolating Transformer housing box,water tight round type,metal container of outside size 330mm height 450mm made of 10mm thick cast iron moulding suitable to receive a light fitting base plate on the top and underground housing associated with transformer power cable and having a clear hole centre at one side surface centre 75mm above bottom surface suitable to receive two of 50mm dia "B" class GI pipe, and including check nuts as required and another hole at 175mm from the bottom of the CI Box to receive one no. 15mm dia "B" class GI pipe and check nut as required.The box should have two SS earth bolts of M10 x 30mm tapped inside near the hole (4" away from the hole centre) and having a drain hole at the bottom suitably tapped to receive 15mm dia "B" class GI pipe and having clear opening of 220 mm at the top surface and 6 nos. M10 tapped hole at the hole centre 260 mm to receive fitting base plate and bolts as required as per the drawings. | 14.00 | Each | 5.00 | 17500.00 | 245000.00 | 5000.00 | 70000.00 | 5959.35 | 83430.90 | 10500.00 | 147000.00 | 5908.00 | 82712.00 | 5500.00 | 77000.00 | 5200.00 | 72800.00 | 4850.00 | 67900.00 | 17500.00 | 245000.00 | 67900.00 | Manish Electricals
2.04 | Installation of transformer housing box with a base concrete of 1:3:6 of size 630 x 630 x 100mm thick all round concrete of 1:2:4 150mm thick. The top sloped with 1:2:4 cement concrete including providing and fixing 10" long 1/2" dia "B" class GI pipe with checknuts for drainage of water including excavation of side shoulder and re-filling (wherever the transformer are in a line the same has to be aligned in such a way that the centers fall in a straight line) etc. complete as required. | 14.00 | Job | 5.00 | 2100.00 | 29400.00 | 2500.00 | 35000.00 | 5018.40 | 70257.60 | 5000.00 | 70000.00 | 2620.00 | 36680.00 | 2850.00 | 39900.00 | 2000.00 | 28000.00 | 1800.00 | 25200.00 | 2500.00 | 35000.00 | 25200.00 | Manish Electricals
2.05 | Supply of following rating 5000V, 50 Hz Series Isolating Transformers encapsulated in polyester resin, finally moulded in neoprene type rubber and with primary and secondary connections suitable to be operated System confirming to specification as required. a) 200 watts, 20/6.6 amps | 3.00 | Each | 5.00 | 9800.00 | 29400.00 | 5000.00 | 15000.00 | 5081.13 | 15243.39 | 4320.00 | 12960.00 | 4529.00 | 13587.00 | 4255.00 | 12765.00 | 4500.00 | 13500.00 | 5000.00 | 15000.00 | 7500.00 | 22500.00 | 12765.00 | Techno Electricals
2.06 | b) 15 watts, 6.6 / 6.6 amps. | 53.00 | Each | 5.00 | 7800.00 | 413400.00 | 3200.00 | 169600.00 | 3136.50 | 166234.50 | 3150.00 | 166950.00 | 2838.00 | 150414.00 | 2800.00 | 148400.00 | 2400.00 | 127200.00 | 2950.00 | 156350.00 | 4500.00 | 238500.00 | 127200.00 | CREATIVE TRADING CO
2.07 | c) 200 watts, 6.6/6.6 amps | 6.00 | Each | 5.00 | 8700.00 | 52200.00 | 5000.00 | 30000.00 | 5081.13 | 30486.78 | 4320.00 | 25920.00 | 4529.00 | 27174.00 | 4255.00 | 25530.00 | 4500.00 | 27000.00 | 4800.00 | 28800.00 | 7500.00 | 45000.00 | 25530.00 | Techno Electricals
3.00 | Supply of Following spares
3.01 | a) Base Plate without Gasket & Bolts | 59.00 | Each | 5.00 | 550.00 | 32450.00 | 1000.00 | 59000.00 | 1066.41 | 62918.19 | 600.00 | 35400.00 | 750.00 | 44250.00 | 1350.00 | 79650.00 | 1500.00 | 88500.00 | 990.00 | 58410.00 | 1200.00 | 70800.00 | 32450.00 | jaydeep agency corporation
3.02 | b) Gasket suitable for Base plate | 59.00 | Each | 5.00 | 285.00 | 16815.00 | 150.00 | 8850.00 | 125.46 | 7402.14 | 85.00 | 5015.00 | 110.00 | 6490.00 | 100.00 | 5900.00 | 200.00 | 11800.00 | 180.00 | 10620.00 | 500.00 | 29500.00 | 5015.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
3.03 | c) M-10 SS Hardware (Set of 6) | 59.00 | Set | 5.00 | 225.00 | 13275.00 | 50.00 | 2950.00 | 125.46 | 7402.14 | 120.00 | 7080.00 | 118.00 | 6962.00 | 100.00 | 5900.00 | 100.00 | 5900.00 | 150.00 | 8850.00 | 150.00 | 8850.00 | 2950.00 | Balaji Engineering
3.04 | d) Two pin Secondary plug assembly for AUN, ALN,and ALD fitting of lengh 12" or 0.3Mtr | 39.00 | Each | 5.00 | 475.00 | 18525.00 | 350.00 | 13650.00 | 263.46 | 10274.94 | 450.00 | 17550.00 | 358.00 | 13962.00 | 600.00 | 23400.00 | 400.00 | 15600.00 | 325.00 | 12675.00 | 1500.00 | 58500.00 | 10274.94 | Taral Electricals
3.05 | Supply of Dummy Plate 10 mm Thickness, 330 mm Dia,Including provision of 6 nos, M10 tapped holes on top and 6 nos through holes at bottom to fix M10 bolts for fixing on exisitng C.I. Transformer house boxes etc complet as required. | 6.00 | Each | 5.00 | 485.00 | 2910.00 | 1000.00 | 6000.00 | 1129.00 | 6774.00 | 1000.00 | 6000.00 | 963.00 | 5778.00 | 1000.00 | 6000.00 | 1000.00 | 6000.00 | 1250.00 | 7500.00 | 1500.00 | 9000.00 | 2910.00 | jaydeep agency corporation
3.06 | Supply of Connector kit suitable for use in the 5KV grade, PVC insulated, PVC sheathed single core copper conductor cable of size 6 Sq.mm/ 16 Sq.mm as required and confirming to AAI particular specifications. | 80.00 | set | 5.00 | 850.00 | 68000.00 | 400.00 | 32000.00 | 452.00 | 36160.00 | 475.00 | 38000.00 | 413.00 | 33040.00 | 450.00 | 36000.00 | 350.00 | 28000.00 | 425.00 | 34000.00 | 600.00 | 48000.00 | 28000.00 | CREATIVE TRADING CO
3.07 | Making field connections by crimping of 16 sqmm /6 sqmm sizes plug & receptable with suitable existing size single core PVC cu. Conductor cable of 5 KV grade Airfield cable including filling the gap with water sealent material applying PVC insulation tape etc. complete as reqd. | 80.00 | Each | 5.00 | 450.00 | 36000.00 | 250.00 | 20000.00 | 125.46 | 10036.80 | 250.00 | 20000.00 | 131.00 | 10480.00 | 150.00 | 12000.00 | 50.00 | 4000.00 | 180.00 | 14400.00 | 900.00 | 72000.00 | 4000.00 | CREATIVE TRADING CO
3.08 | SITC of Indoor Type Air Cooled Constant Current Regulator (CCR) of Micro Processor Controlled, Thyristor Type suitable for operation on single phase 230V / 2-phase 400V AC + PE ± 10%, 50 Hz input AC supply with 5 steps variation of current output and able to communicate with PC or PLC controlled system with digital output anmeter (0-10 Amps), over current, over voltage, open circuit and earth fault protection and earth leakage meter, two stage earth leakage detector, positive back indication equipments, hours run counter, LCD display complete as required for the following rating and confirm to specifications enclosed and suitable for operation on the existing Airfield Lighting Control and Monitoring System (ALCMS) with communication, local and remote control and monitoring event and data recording and history keeping etc complete as required - 4.0 KW (For Taxiway) | 2.00 | Each | 5.00 | 375000.00 | 750000.00 | 200000.00 | 400000.00 | 220809.00 | 441618.00 | 475000.00 | 950000.00 | 204600.00 | 409200.00 | 350000.00 | 700000.00 | 275000.00 | 550000.00 | 195000.00 | 390000.00 | 450000.00 | 900000.00 | 390000.00 | Manish Electricals
3.09 | Cutting groove of size 50mm wide and 100mm deep with saw cut machine, refilling and finishing the surface with chemical compound ,coarse sand, bitumen, etc complete as required. | 55.00 | Mtr | 5.00 | 850.00 | 46750.00 | 500.00 | 27500.00 | 878.22 | 48302.10 | 1000.00 | 55000.00 | 590.00 | 32450.00 | 500.00 | 27500.00 | 450.00 | 24750.00 | 750.00 | 41250.00 | 300.00 | 16500.00 | 16500.00 | DElite System Engineering (India) Pvt. Ltd.
3.10 | Supply, laying and fixing following dia G.I. pipe (medium class) in excavated trench/Groove complete with cutting,threading, fixing with check nuts, G.I. fittings including trenching (75 cm deep)and re-filling etc as required. (a) 50 mm dia | 60.00 | Mtr | 5.00 | 1175.00 | 70500.00 | 450.00 | 27000.00 | 803.00 | 48180.00 | 825.00 | 49500.00 | 735.00 | 44100.00 | 650.00 | 39000.00 | 600.00 | 36000.00 | 725.00 | 43500.00 | 900.00 | 54000.00 | 27000.00 | Balaji Engineering
3.11 | (b) 15 mm dia | 123.50 | Mtr | 5.00 | 425.00 | 52487.50 | 175.00 | 21612.50 | 362.57 | 44777.40 | 425.00 | 52487.50 | 305.00 | 37667.50 | 250.00 | 30875.00 | 175.00 | 21612.50 | 260.00 | 32110.00 | 300.00 | 37050.00 | 21612.50 | Balaji Engineering, CREATIVE TRADING CO
3.12 | (b) 25 mm dia | 18.00 | Mtr | 5.00 | 510.00 | 9180.00 | 200.00 | 3600.00 | 420.30 | 7565.40 | 525.00 | 9450.00 | 428.00 | 7704.00 | 350.00 | 6300.00 | 250.00 | 4500.00 | 475.00 | 8550.00 | 500.00 | 9000.00 | 3600.00 | Balaji Engineering
3.13 | Painting of Runway/ threshold /end /turnning pad light fixtures with avition yellow & CI box with black synethic enamelled paint including making the numbering on the each lighting fitting base plate etc as required. | 305.00 | Each | 5.00 | 115.00 | 35075.00 | 100.00 | 30500.00 | 125.00 | 38125.00 | 350.00 | 106750.00 | 66.00 | 20130.00 | 120.00 | 36600.00 | 200.00 | 61000.00 | 50.00 | 15250.00 | 350.00 | 106750.00 | 15250.00 | Manish Electricals
3.14 | Providing and fixing outdoor feeder boxes of size 250X250X150 mm made out of 03mm thick MS sheet on a suitable angle iron frame of size 40 X 40 X 6mm and fixing the same in the ground with concreting with 2 holes for 50mm B class GI pipe at the bottom including painting etc. as required. | 2.00 | Job | 5.00 | 2780.00 | 5560.00 | 10000.00 | 20000.00 | 5645.70 | 11291.40 | 4850.00 | 9700.00 | 13827.00 | 27654.00 | 5000.00 | 10000.00 | 10000.00 | 20000.00 | 12500.00 | 25000.00 | 9000.00 | 18000.00 | 5560.00 | jaydeep agency corporation
4.00 | Signages:
4.01 | Design, Supply, installation, testing and commissioning of guidance sign boards of various sizes (as per annexure) made of anodised 2 mm thick aluminium frame with suitable angle support with 1.5 mmm thick aluminium back cover and 4 mm thick poly carbonate sheet with glare free face, the letter and symbols should be screen printed with required colouring, suitable arrangement shall be made to function on both main and standby (runway/taxiway) circuits with internal control circuits i/c. installations of isolating transformers, providing secondary leads, ESNA connectors. Suitable arrangements shall be made for water tightness and locking arrangement, sign boards shall be uniformly internally illuminated with required number of LED lights to achieve required illumination level, operated on input source of 2.5 A to 6.6 A constant current without any flickering, including its supporting legs, breakable coupling and base frame etc. complete as required as per ICAO. | 12.00 | Sq.Mtr | 5.00 | 53000.00 | 636000.00 | 35000.00 | 420000.00 | 42656.40 | 511876.80 | 3500.00 | 42000.00 | 45000.00 | 540000.00 | 47500.00 | 570000.00 | 45000.00 | 540000.00 | 43500.00 | 522000.00 | 45000.00 | 540000.00 | 42000.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
5.00 | Supply of Cables:
5.01 | Supply of following Airfield Lighting (AFL) 5 KV grade, Copper Conductor, Copper shielded, XLPE insulated, and with inner and outer semi conductor, Polyethylene (PE) outer sheathed, Copper Braid, Unarmoured Underground Cable for airfield lighting Primary Circuit, confirming to specification as specified in technical specification of the following sizes as required. a) Single Core 6 Sq.mm | 2785.00 | Mtr | 5.00 | 110.00 | 306350.00 | 100.00 | 278500.00 | 120.00 | 334200.00 | 95.00 | 264575.00 | 182.00 | 506870.00 | 110.00 | 306350.00 | 95.00 | 264575.00 | 180.00 | 501300.00 | 200.00 | 557000.00 | 264575.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED, CREATIVE TRADING CO
5.02 | Supplying of following sizes aluminium conductor armoured XLPE insulated, PVC sheathed power cable for working voltage upto & i/c 1.1 KV. as per IS : 7098 (Part-I), 1988 with latest amendments. a) 4C x 16 Sq.mm | 920.00 | Mtr | 5.00 | 165.00 | 151800.00 | 175.00 | 161000.00 | 127.00 | 116840.00 | 238.00 | 218960.00 | 197.00 | 181240.00 | 167.00 | 153640.00 | 200.00 | 184000.00 | 160.00 | 147200.00 | 189.00 | 173880.00 | 116840.00 | Taral Electricals
5.03 | Supply of Secondary lead cable of size 2Cx 4 Sq.mm, PV insulated, PVC sheathed, anti-termite, anti-rodent Stranded copper conductor. | 202.00 | Mtr | 5.00 | 187.00 | 37774.00 | 135.00 | 27270.00 | 150.50 | 30401.00 | 185.00 | 37370.00 | 165.00 | 33330.00 | 143.00 | 28886.00 | 150.00 | 30300.00 | 210.00 | 42420.00 | 250.00 | 50500.00 | 27270.00 | Balaji Engineering
5.04 | Supply of PVC insulated and PVC sheathed / XLPE power cable of 1.1KV grade confirming to IS : 7098 of following sizes etc. completed as required. 4C x 25 Sq.mm - Aluminium Core - Armoured | 60.00 | Mtr | 5.00 | 200.00 | 12000.00 | 200.00 | 12000.00 | 180.60 | 10836.00 | 215.00 | 12900.00 | 257.00 | 15420.00 | 200.00 | 12000.00 | 200.00 | 12000.00 | 225.00 | 13500.00 | 220.00 | 13200.00 | 10836.00 | Taral Electricals
5.05 | 3C x 1.5 Sq.mm - Copper Core - Un-armoured - flexible cable | 585.00 | Mtr | 5.00 | 85.00 | 49725.00 | 120.00 | 70200.00 | 53.82 | 31484.70 | 95.00 | 55575.00 | 64.00 | 37440.00 | 75.00 | 43875.00 | 80.00 | 46800.00 | 150.00 | 87750.00 | 125.00 | 73125.00 | 31484.70 | Taral Electricals
5.06 | 2C x 25 Sq.mm - Aluminium Core - Armoured | 80.00 | Mtr | 5.00 | 122.00 | 9760.00 | 125.00 | 10000.00 | 138.00 | 11040.00 | 135.00 | 10800.00 | 77.00 | 6160.00 | 200.00 | 16000.00 | 200.00 | 16000.00 | 140.00 | 11200.00 | 150.00 | 12000.00 | 6160.00 | Vardhman Airport Solutions Pvt Ltd
6.00 | Laying of Cable:
6.01 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. a) 50 mm dia (OD-50 mm & ID-38 mm nominal)- | 1505.00 | Mtr | 5.00 | 175.00 | 263375.00 | 150.00 | 225750.00 | 203.24 | 305876.20 | 180.00 | 270900.00 | 174.00 | 261870.00 | 175.00 | 263375.00 | 200.00 | 301000.00 | 156.00 | 234780.00 | 230.00 | 346150.00 | 225750.00 | Balaji Engineering
6.02 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. a) 63 mm dia (OD-63 mm & ID-51 mm nominal)- | 1115.00 | Mtr | 5.00 | 238.00 | 265370.00 | 165.00 | 183975.00 | 240.00 | 267600.00 | 215.00 | 239725.00 | 211.00 | 235265.00 | 190.00 | 211850.00 | 200.00 | 223000.00 | 210.00 | 234150.00 | 275.00 | 306625.00 | 183975.00 | Balaji Engineering
6.03 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. in the existing trench, complete as required. a) 63 mm dia (OD-63 mm & ID-51 mm nominal) | 1115.00 | Mtr | 5.00 | 183.00 | 204045.00 | 100.00 | 111500.00 | 82.80 | 92322.00 | 215.00 | 239725.00 | 119.00 | 132685.00 | 100.00 | 111500.00 | 150.00 | 167250.00 | 90.00 | 100350.00 | 200.00 | 223000.00 | 92322.00 | Taral Electricals
6.04 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade & 5 KV gradeof following size in the existing RCC/HUME/STONE WARE/METAL/DWC-HDPE pipe as required. a) Upto 35 sq. mm-AFL Cable | 3352.00 | Mtr | 5.00 | 22.00 | 73744.00 | 20.00 | 67040.00 | 29.00 | 97208.00 | 35.00 | 117320.00 | 26.00 | 87152.00 | 20.00 | 67040.00 | 15.00 | 50280.00 | 20.00 | 67040.00 | 45.00 | 150840.00 | 50280.00 | CREATIVE TRADING CO
6.05 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 5 KV grade of following size in the existing masonry open duct as required. a) Upto 35 sq. mm | 170.74 | Mtr | 5.00 | 20.00 | 3414.80 | 20.00 | 3414.80 | 37.63 | 6424.95 | 35.00 | 5975.90 | 33.00 | 5634.42 | 20.00 | 3414.80 | 10.00 | 1707.40 | 25.00 | 4268.50 | 35.00 | 5975.90 | 1707.40 | CREATIVE TRADING CO
6.06 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | 58.00 | Each | 5.00 | 350.00 | 20300.00 | 500.00 | 29000.00 | 600.00 | 34800.00 | 250.00 | 14500.00 | 729.00 | 42282.00 | 350.00 | 20300.00 | 1000.00 | 58000.00 | 450.00 | 26100.00 | 1500.00 | 87000.00 | 14500.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
7.00 | EARTHING:
7.01 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 10.00 | Each | 5.00 | 4950.00 | 49500.00 | 6000.00 | 60000.00 | 8400.00 | 84000.00 | 8500.00 | 85000.00 | 6550.00 | 65500.00 | 7500.00 | 75000.00 | 7500.00 | 75000.00 | 7000.00 | 70000.00 | 13500.00 | 135000.00 | 49500.00 | jaydeep agency corporation
7.02 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 110.00 | Mtr | 5.00 | 248.00 | 27280.00 | 150.00 | 16500.00 | 205.00 | 22550.00 | 585.00 | 64350.00 | 262.00 | 28820.00 | 250.00 | 27500.00 | 200.00 | 22000.00 | 210.00 | 23100.00 | 150.00 | 16500.00 | 16500.00 | Balaji Engineering, DElite System Engineering (India) Pvt. Ltd.
7.03 | Providing and laying of 6 SWG GI wire inside the excavated cable trench/humepipe/DWC pipe for loop earthing etc complete as required. | 2786.50 | Mtr | 5.00 | 34.00 | 94741.00 | 20.00 | 55730.00 | 22.58 | 62919.17 | 45.00 | 125392.50 | 24.00 | 66876.00 | 25.00 | 69662.50 | 20.00 | 55730.00 | 25.00 | 69662.50 | 35.00 | 97527.50 | 55730.00 | Balaji Engineering, CREATIVE TRADING CO
8.00 | APRON FLOOD LIGHTING:
8.01 | Supply, installation, testing, commisioning of 150 Watt Area Light/flood LED IP66 flood light, pole mountable Flood Light for oudoor applications, suitable to operate on 230V, 50 Hz AC supply on existing Light pole, termination etc complete as required. Make: AAI approved make | 20.00 | Each | 5.00 | 6540.00 | 130800.00 | 12000.00 | 240000.00 | 6586.65 | 131733.00 | 7500.00 | 150000.00 | 9236.00 | 184720.00 | 5980.00 | 119600.00 | 7500.00 | 150000.00 | 6200.00 | 124000.00 | 17500.00 | 350000.00 | 119600.00 | Techno Electricals
8.02 | Erection of G.I/steel tubular pole of length not exceeding 2.0 meters fixed into base plate through Frangible coupling, Rotatable G.I. Pole top fabricated to mount Area LIght fitting with G.I.pole in existing Isolating Transformer Housing Box along with embedding following dia G.I. pipe (medium class) in pole collar/ foundation (during casting) for cable entry including bending the pipe to the required shape (Make: Jindal or equivalent approved make) for cable entry to C.I box etc as required, complete as per technical specifications. | 20.00 | Each | 5.00 | 2250.00 | 45000.00 | 3000.00 | 60000.00 | 4328.37 | 86567.40 | 850.00 | 17000.00 | 6550.00 | 131000.00 | 4000.00 | 80000.00 | 3000.00 | 60000.00 | 4500.00 | 90000.00 | 3500.00 | 70000.00 | 17000.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
8.03 | SITC of Wall Mounted FTO Apron flood light remote control panel including 4P-100A,MCCB & contactor, 4P Bakelite terminal, cable connectors, selector switch, LED indicatoras per particular specifications etc complete as required. | 2.00 | Each | 5.00 | 26500.00 | 53000.00 | 15000.00 | 30000.00 | 33874.20 | 67748.40 | 5500.00 | 11000.00 | 78600.00 | 157200.00 | 45000.00 | 90000.00 | 25000.00 | 50000.00 | 48500.00 | 97000.00 | 15000.00 | 30000.00 | 11000.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
8.04 | Supply and Fixing of Outdoor type Electrical panel of Suitable size weather proof-IP66, pole mounted, affixed onto Suitable Bracket/Pole with frangible Coupling Base, including MS clamp with nut bolts, 4P Bus bars to terminate incoming 4 Core cable, interconnected with SP MCB's-10 nos affixed onto Dinrails, Gasket including Grouting of Suitable Size etc Complete as required | 1.00 | Each | 5.00 | 28000.00 | 28000.00 | 2500.00 | 2500.00 | 9535.00 | 9535.00 | 5500.00 | 5500.00 | 9498.00 | 9498.00 | 10000.00 | 10000.00 | 25000.00 | 25000.00 | 12000.00 | 12000.00 | 15000.00 | 15000.00 | 2500.00 | Balaji Engineering
8.05 | Supplying and making end termination with brass (double) compression gland and bi-metallic (aluminium & copper) lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4 X 25 sq. mm (28mm) | 2.00 | Set | 5.00 | 325.00 | 650.00 | 1000.00 | 2000.00 | 677.00 | 1354.00 | 250.00 | 500.00 | 1864.00 | 3728.00 | 350.00 | 700.00 | 500.00 | 1000.00 | 500.00 | 1000.00 | 500.00 | 1000.00 | 500.00 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED
9.00 | MISCELLANEOUS :
9.01 | Providing and laying of 110 mm outer dia, PE80, PN6 rating HDPE pipe IS:4984, IS:14333 by Horizontal Directional Drilling including jointing/welding of HDPE pipes across the runway/taxiway and Roads by trencheless directional drilling (HDD) method by deploying HDD machines, mud mixing system, Earth movers etc. complete as required. | 160.00 | Mtr | 5.00 | 1050.00 | 168000.00 | 2000.00 | 320000.00 | 1373.00 | 219680.00 | 2500.00 | 400000.00 | 1376.00 | 220160.00 | 3700.00 | 592000.00 | 6000.00 | 960000.00 | 3200.00 | 512000.00 | 3000.00 | 480000.00 | 168000.00 | jaydeep agency corporation
9.02 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement: 4 coarse sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone- III) : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone- III) : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : Inside size 120x90 cm and 90 cm deep including C.I. cover with frame (medium duty) 500 mm internal diameter, total weight of cover and frame to be not less than 116 kg (weight of cover 58 kg and weight of frame 58 kg) : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 4.00 | Job | 5.00 | 9870.00 | 39480.00 | 20000.00 | 80000.00 | 34125.00 | 136500.00 | 35000.00 | 140000.00 | 36680.00 | 146720.00 | 18000.00 | 72000.00 | 30000.00 | 120000.00 | 16500.00 | 66000.00 | 25000.00 | 100000.00 | 39480.00 | jaydeep agency corporation
9.03 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement: 4 coarse sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone- III) : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone- III) : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : Inside size 120x90 cm and 2 Mtr deep including C.I. cover with frame (medium duty) 500 mm internal diameter, total weight of cover and frame to be not less than 116 kg (weight of cover 58 kg and weight of frame 58 kg) : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 4.00 | Job | 5.00 | 17500.00 | 70000.00 | 50000.00 | 200000.00 | 52944.00 | 211776.00 | 35000.00 | 140000.00 | 36680.00 | 146720.00 | 15625.00 | 62500.00 | 30000.00 | 120000.00 | 16500.00 | 66000.00 | 45000.00 | 180000.00 | 62500.00 | Techno Electricals
9.04 | Supply of 120 Watt Area Light/flood LED IP66 flood light, pole mountable Flood Light for oudoor applications, suitable to operate on 230V, 50 Hz AC supply on existing Light pole, termination etc complete as required. Make: AAI approved make | 4.00 | Each | 5.00 | 4980.00 | 19920.00 | 15000.00 | 60000.00 | 5708.43 | 22833.72 | 9500.00 | 38000.00 | 7015.00 | 28060.00 | 8000.00 | 32000.00 | 7000.00 | 28000.00 | 5200.00 | 20800.00 | 15000.00 | 60000.00 | 19920.00 | jaydeep agency corporation
| Total in Figures |  |  |  |  | 5274056.30 |  | 4096642.30 |  | 4644733.52 |  | 5171830.90 |  | 4640282.92 |  | 4783713.30 |  | 5070004.90 |  | 4529186.00 |  | 6898673.40
Lowest Amount Quoted BY: Balaji Engineering(4096642.30)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of 10.5 m wide link taxi track connecting runway to the proposed FTO at Belagavi Airport. SH- Provision of Taxiway Lighting and Apron Flood Lighting Tender ID: 2021_AAI_99845_2
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Balaji Engineering | 4096642.30 | L1
| 2 | Manish Electricals | 4529186.00 | L2
| 3 | Vardhman Airport Solutions Pvt Ltd | 4640282.92 | L3
| 4 | Taral Electricals | 4644733.52 | L4
| 5 | Techno Electricals | 4783713.30 | L5
| 6 | CREATIVE TRADING CO | 5070004.90 | L6
| 7 | S. N. ELECTRIC & MAINTENANCE PRIVATE LIMITED | 5171830.90 | L7
| 8 | jaydeep agency corporation | 5274056.30 | L8
| 9 | DElite System Engineering (India) Pvt. Ltd. | 6898673.40 | L9