## BoQ1
Government eProcurement System Created By: KAMBLE TANAJI Created Date/Time: 17-Jan-2022 04:18 PM Tender Title: Construction of Integrated of cargo terminal at Pune Airport SH Electrical Works Tender ID: 2021_AAI_99850_1
Tender Inviting Authority: Asst. General Manager (Engg-Elect), Pune Airport
Name of Work: Construction of Integrated of cargo terminal at Pune Airport (SH: Electrical Works)
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | RB MULTITECH(GSTN-24COFPP5237R1ZA) |  | Taral Electricals(GSTN-24ACMPR0280M1Z9) |  | Manish Electricals(GSTN-22ABLPM9012E1ZY) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5) |  | Ekveera Electrical Works & Services(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Wiring for light pont/ fanpoint/ exhaust fan point/ call bell point with 1.5 Sq. mm FRLS PVC insulated, copper conductor single core cable in surface / recessed steel conduit , with modular type switch, modular plate, suitable size G.I. .box and earthing the point with 1.5 sq.mm FR PVC insulated copper conductor single core cable etc as required. Group C | 60.00 | Point |  | 632.00 | 37920.00 | 1520.00 | 91200.00 | 1100.00 | 66000.00 | 1050.00 | 63000.00 | 1450.00 | 87000.00 | 37920.00 | RB MULTITECH
2.00 | Wiring for light / power plug with 2 x 4 Sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit alongwith 1 No. 4 sq.mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 350.00 | Meter |  | 230.00 | 80500.00 | 213.00 | 74550.00 | 210.00 | 73500.00 | 245.00 | 85750.00 | 290.00 | 101500.00 | 73500.00 | Manish Electricals
3.00 | Wiring for cicuit/submain wiring along with earth wire with following size of FRLS PVC insulated, copper conductor, single core cable in surface /recessed steel conduit as required. 2 x 2.5 Sqmm +1 x 2.5 Sqmm earth wire | 400.00 | Meter |  | 207.00 | 82800.00 | 284.00 | 113600.00 | 185.00 | 74000.00 | 208.00 | 83200.00 | 238.00 | 95200.00 | 74000.00 | Manish Electricals
4.00 | Supplying and fixing suitable size Gl box with modular plate and cover in Front on surface or in recess, including providing and fixing 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connection etc. as required. | 44.00 | Each |  | 690.00 | 30360.00 | 414.00 | 18216.00 | 350.00 | 15400.00 | 715.00 | 31460.00 | 540.00 | 23760.00 | 15400.00 | Manish Electricals
5.00 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. for Telephone & TV. 25 mm | 600.00 | Meter |  | 103.00 | 61800.00 | 203.00 | 121800.00 | 45.00 | 27000.00 | 135.00 | 81000.00 | 145.00 | 87000.00 | 27000.00 | Manish Electricals
6.00 | Supplying and drawing 02 pair 0.5 mm dia FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. | 60.00 | Meter |  | 28.00 | 1680.00 | 18.00 | 1080.00 | 60.00 | 3600.00 | 22.00 | 1320.00 | 32.00 | 1920.00 | 1080.00 | Taral Electricals
7.00 | Supplying and drawing 20 pair 0.63 mm dia jelly filled copper conductor armored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. | 200.00 | Meter |  | 80.00 | 16000.00 | 189.00 | 37800.00 | 210.00 | 42000.00 | 345.00 | 69000.00 | 320.00 | 64000.00 | 16000.00 | RB MULTITECH
8.00 | Supplying and drawing co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ recessed steel/ PVC conduit as required. | 60.00 | Meter |  | 28.00 | 1680.00 | 38.00 | 2280.00 | 35.00 | 2100.00 | 58.00 | 3480.00 | 45.00 | 2700.00 | 1680.00 | RB MULTITECH
9.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. Telephone socket outlet | 4.00 | Each |  | 230.00 | 920.00 | 131.00 | 524.00 | 150.00 | 600.00 | 150.00 | 600.00 | 270.00 | 1080.00 | 524.00 | Taral Electricals
10.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. TV antenna socket outlet | 4.00 | Each |  | 230.00 | 920.00 | 120.00 | 480.00 | 40.00 | 160.00 | 155.00 | 620.00 | 230.00 | 920.00 | 160.00 | Manish Electricals
11.00 | Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, 50Hz AC supply complete as required.. | 4.00 | Each |  | 172.00 | 688.00 | 178.00 | 712.00 | 80.00 | 320.00 | 270.00 | 1080.00 | 540.00 | 2160.00 | 320.00 | Manish Electricals
12.00 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc. as required. 75 mm X 75 mm X 60 mm deep | 10.00 | Each |  | 172.00 | 1720.00 | 530.00 | 5300.00 | 54.00 | 540.00 | 90.00 | 900.00 | 450.00 | 4500.00 | 540.00 | Manish Electricals
13.00 | Supplying and fixing following way horizontal type TP &N MCB distribution board of sheet steel, 415 volts, on surface/ recess, terminal connectors for all incoming and outgoing circuits with suitable size FRLS PVC insulated copper conductor up to terminal blocks, earth bar, din bar, detachable gland plate,with cable end box interconnections, powder painted, including earthing etc.as required.(But without MCB/RCCB/Isolator). 6 way (4+18) double door | 8.00 | Each |  | 4600.00 | 36800.00 | 3420.00 | 27360.00 | 6500.00 | 52000.00 | 3550.00 | 28400.00 | 5400.00 | 43200.00 | 27360.00 | Taral Electricals
14.00 | Supplying and fixing following rating MCB suitable for inductive load in the existing MCB DB Complete with connections, testing and commissioning etc. as required. Four pole, 415 Volts, 10kA, 'C' curve63 Amps | 8.00 | Each |  | 1610.00 | 12880.00 | 1446.00 | 11568.00 | 1100.00 | 8800.00 | 1500.00 | 12000.00 | 1600.00 | 12800.00 | 8800.00 | Manish Electricals
15.00 | Supplying and fixing 6 Amps. to 32 Amps. rating, 240 Volts, 'C' Series, 10kA, SP MCB in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 304.00 | Each |  | 103.00 | 31312.00 | 160.00 | 48640.00 | 180.00 | 54720.00 | 165.00 | 50160.00 | 230.00 | 69920.00 | 31312.00 | RB MULTITECH
16.00 | Supplying and drawing following sizes of FR PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required. 3 x 1.5 sqmm | 100.00 | Mtr |  | 51.00 | 5100.00 | 67.00 | 6700.00 | 125.00 | 12500.00 | 80.00 | 8000.00 | 76.00 | 7600.00 | 5100.00 | RB MULTITECH
17.00 | Supplying and drawing following sizes of FR PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required. 3 x 2.5 sqmm | 100.00 | Mtr |  | 80.00 | 8000.00 | 105.00 | 10500.00 | 210.00 | 21000.00 | 140.00 | 14000.00 | 94.00 | 9400.00 | 8000.00 | RB MULTITECH
18.00 | Supplying and drawing following sizes of FR PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required. 3 x 4.0 sqmm | 100.00 | Mtr |  | 115.00 | 11500.00 | 148.00 | 14800.00 | 270.00 | 27000.00 | 170.00 | 17000.00 | 115.00 | 11500.00 | 11500.00 | RB MULTITECH, Ekveera Electrical Works & Services
19.00 | Design, supply, installation, testing and commissioning of 3200 Lumen, 6500K, efficacy >110 lumen/watt, power factor >0.95, IP20, CRI >80, burning hours>50000 hours, surface mounted LED type 2'X2' LED luminaire with high transmitive diffuser, 05 years warranty suitable for indoor commercial application, made out of metalic CRCA powder coated body, required heat sink, mounting arrangement complete with LEDs driver, surge protection system and compliance with LM 80 & LM 79 s etc. complete as required. Make- Philips, Model No.- SM365C LED32-6500 PSU OD GR or Equivalent. | 80.00 | Each |  | 3392.00 | 271360.00 | 4435.00 | 354800.00 | 4500.00 | 360000.00 | 2100.00 | 168000.00 | 3600.00 | 288000.00 | 168000.00 | Awasthi Electric Works
20.00 | Design, supply, installation, testing and commissioning of 6500 Lumen, 5700K, efficacy >110 lumen/watt, power factor >0.95 , IP66, CRI >80, burning hours>50000 hours pole mounting LED type streetlight fitting with 05 years warranty, made out of pressure die-cast housing and heat sink, mounting clamps complete with LEDs driver, surge protection system and compliance with LM 80 & LM 79 s etc. complete as required. Make- Philips, Model No.- BRP062 LED65 CW SLA S1 PSU or Equivalent. | 25.00 | Each |  | 3507.00 | 87675.00 | 3762.00 | 94050.00 | 5200.00 | 130000.00 | 2950.00 | 73750.00 | 3200.00 | 80000.00 | 73750.00 | Awasthi Electric Works
21.00 | Design, supply, installation, testing and commissioning of 10000 Lumen, 6500K, efficacy >110 lumen/watt, power factor >0.95 , IP66, CRI >80, burning hours>50000 hours highbay LED type light fitting with 05 years warranty, aluminum die-cast housing & toughened glass suitable for ceiling (Surface /Suspended) mount, wide beam, mounting/suspending arrangement complete with LEDs driver, surge protection system and compliance with LM 80 & LM 79 etc. complete as required. Make- Philips, Model No.- BY325P LED100S CW PSU GR FG NB XTFCL V1 or Equivalent. | 15.00 | Each |  | 5980.00 | 89700.00 | 7296.00 | 109440.00 | 11000.00 | 165000.00 | 4900.00 | 73500.00 | 5200.00 | 78000.00 | 73500.00 | Awasthi Electric Works
22.00 | Supply and fixing of 300mm swep, 1300 RPM, MS blade exhaust fan in the existing opening, including making the hole to suit the size of the above fan, making good the damage, connections, testing, commissioning etc. as required | 2.00 | Each |  | 2300.00 | 4600.00 | 3089.00 | 6178.00 | 2500.00 | 5000.00 | 2190.00 | 4380.00 | 4500.00 | 9000.00 | 4380.00 | Awasthi Electric Works
23.00 | Supply, installation, testing and commissioning of energy effiecient, 400 mm sweep, 1400 RPM, rotating wall fan suitable for operation on 230 V, 50 Hz, Single phase, A.C supply etc. complete as required. | 10.00 | Each |  | 2300.00 | 23000.00 | 2109.00 | 21090.00 | 7500.00 | 75000.00 | 1875.00 | 18750.00 | 3600.00 | 36000.00 | 18750.00 | Awasthi Electric Works
24.00 | Supply, installation, testing and commissioning of wall mounted touch-free plastic hand dryer suitable to work on 230 V, 50 Hz AC supply etc. complete as required. | 2.00 | Each |  | 3450.00 | 6900.00 | 47255.00 | 94510.00 | 9000.00 | 18000.00 | 9500.00 | 19000.00 | 9000.00 | 18000.00 | 6900.00 | RB MULTITECH
25.00 | Supply, installation, testing and commissioning of ABS casing automatic hand sanitizer having capacity 1100 ml, sensing range 08cm etc. complete as required. Make -Euronics, Model No. EST02N or Equivalent | 2.00 | Each |  | 4025.00 | 8050.00 | 2744.00 | 5488.00 | 15600.00 | 31200.00 | 3600.00 | 7200.00 | 4500.00 | 9000.00 | 5488.00 | Taral Electricals
26.00 | Supply, installation, testing and commissioning of automatic pest-o flash insect and mosquito killer consisting of 02 nos. UV tubes covering 500 sqft. Area suitable for operation on 230V, 1-phase, 50Hz AC supply etc. complete as required. Make: Orchids, Model: OR-PCI-01 or equivalent. | 2.00 | Each |  | 6900.00 | 13800.00 | 7695.00 | 15390.00 | 7500.00 | 15000.00 | 8125.00 | 16250.00 | 8100.00 | 16200.00 | 13800.00 | RB MULTITECH
27.00 | Supply, installation, testing and commissioning of 1-phase, class-1, 5-20A rated current energy meter with C20A, Isc=10kA SP MCB, MCB channel in corrosion free, rust free IP 65 meter box including interconnection with suitable wires complete as required. | 10.00 | Each |  | 3450.00 | 34500.00 | 3192.00 | 31920.00 | 1250.00 | 12500.00 | 1800.00 | 18000.00 | 2300.00 | 23000.00 | 12500.00 | Manish Electricals
28.00 | Supplying and fixing 20 A, 240 V, SPN Industrial type socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 A "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket outlet and complete with connections, testing and commissioning etc. as required. | 4.00 | Each |  | 1150.00 | 4600.00 | 1995.00 | 7980.00 | 900.00 | 3600.00 | 1210.00 | 4840.00 | 1600.00 | 6400.00 | 3600.00 | Manish Electricals
29.00 | Supply of 3 W LED type Rechargeable Lantern with Long Backup having Li-ion battery capacity 2000mAH suitable to operate on 240 V single phase , 50 Hz ac supply etc. complete as required. Make-Havells, Model No. GALAXY NEO LANTERN or Equivalent. | 2.00 | Each |  | 1840.00 | 3680.00 | 1425.00 | 2850.00 | 1200.00 | 2400.00 | 1650.00 | 3300.00 | 2300.00 | 4600.00 | 2400.00 | Manish Electricals
30.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. in the existing trench/on ground complete as required. 63 mm dia (OD-63 mm & ID-51 mm nominal) | 1100.00 | Mtr |  | 60.00 | 66000.00 | 82.00 | 90200.00 | 210.00 | 231000.00 | 130.00 | 143000.00 | 126.00 | 138600.00 | 66000.00 | RB MULTITECH
31.00 | Supply and Laying of one number PVC insulated and PVC sheathed / XLPE of 1.1 KV grade 3.5C x 120 Sqmm. aluminium conductor armoured power cable along with 6SWG dia G.I.earth wire including end connection of earth wire in the existing HDPE pipe/cable tray/duct complete as required. | 360.00 | Mtr. |  | 621.00 | 223560.00 | 616.00 | 221760.00 | 586.00 | 210960.00 | 665.00 | 239400.00 | 770.00 | 277200.00 | 210960.00 | Manish Electricals
32.00 | Supply and Laying of one number PVC insulated and PVC sheathed / XLPE of 1.1 KV grade 4C x 25 Sqmm. aluminium conductor armoured power cable along with 6SWG dia G.I.earth wire including end connection of earth wire in the existing HDPE pipe/cable tray/duct/on wall complete as required. | 200.00 | Mtr |  | 178.00 | 35600.00 | 214.00 | 42800.00 | 190.00 | 38000.00 | 255.00 | 51000.00 | 295.00 | 59000.00 | 35600.00 | RB MULTITECH
33.00 | Supply installation testing and commisioning of 7 M hot dip galvanised Octagonal/Tubular streetlight pole with 70 mm top dia., 130 mm bottom dia., 3mm thick with suitable foundation,base plate, foundation bolts, fastener as recommended by OEM including 01 mtr single arm pipe type bracket suitable for street light specified at BOQ item no.16, provision of junction box and cable loop-in loop-out arrangement, 04 nos. terminal block, din MCB channel etc. complete as required. | 25.00 | Each |  | 9775.00 | 244375.00 | 20087.00 | 502175.00 | 16500.00 | 412500.00 | 15900.00 | 397500.00 | 23000.00 | 575000.00 | 244375.00 | RB MULTITECH
34.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 120 sq. mm (45mm) | 4.00 | Each |  | 287.00 | 1148.00 | 673.00 | 2692.00 | 1000.00 | 4000.00 | 550.00 | 2200.00 | 540.00 | 2160.00 | 1148.00 | RB MULTITECH
35.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4 X 25 sq. mm (28mm) | 16.00 | Each |  | 115.00 | 1840.00 | 467.00 | 7472.00 | 500.00 | 8000.00 | 220.00 | 3520.00 | 410.00 | 6560.00 | 1840.00 | RB MULTITECH
36.00 | Supply and Laying of one number PVC insulated and PVC sheathed / XLPE of 1.1 KV grade 4C x 16 Sqmm. aluminium conductor armoured power cable along with 6SWG dia G.I.earth wire in including end connection of earth wire the existing HDPE pipe/on wall complete as required. | 400.00 | Meter |  | 138.00 | 55200.00 | 156.00 | 62400.00 | 25.00 | 10000.00 | 190.00 | 76000.00 | 225.00 | 90000.00 | 10000.00 | Manish Electricals
37.00 | Supplying and making end termination with brass compressiongland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4 X 16 sq. mm (28mm) | 60.00 | Each |  | 57.00 | 3420.00 | 473.00 | 28380.00 | 500.00 | 30000.00 | 150.00 | 9000.00 | 360.00 | 21600.00 | 3420.00 | RB MULTITECH
38.00 | Supply and Laying of one number PVC insulated and PVC sheathed / XLPE of 1.1 KV grade 4C x 35 Sqmm. aluminium conductor armoured power cable along with 6SWG dia G.I.earth wire including end connection of earth wire in the existing HDPE pipe/on wall complete as required. | 150.00 | Meter |  | 253.00 | 37950.00 | 271.00 | 40650.00 | 20.00 | 3000.00 | 340.00 | 51000.00 | 360.00 | 54000.00 | 3000.00 | Manish Electricals
39.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4 X 35 sq. mm (32mm) | 4.00 | Each |  | 172.00 | 688.00 | 503.00 | 2012.00 | 500.00 | 2000.00 | 250.00 | 1000.00 | 430.00 | 1720.00 | 688.00 | RB MULTITECH
40.00 | Supply and Laying of one number PVC insulated and PVC sheathed / XLPE of 1.1 KV grade 2C X 16 Sqmm. aluminium conductor armoured power cable in the existing HDPE pipe/on wall/pole to pole etc. complete as required. | 180.00 | Each |  | 103.00 | 18540.00 | 114.00 | 20520.00 | 90.00 | 16200.00 | 300.00 | 54000.00 | 206.00 | 37080.00 | 16200.00 | Manish Electricals
41.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 2 X 16 sq. mm (22mm) | 20.00 | Each |  | 115.00 | 2300.00 | 331.00 | 6620.00 | 300.00 | 6000.00 | 190.00 | 3800.00 | 320.00 | 6400.00 | 2300.00 | RB MULTITECH
42.00 | Supply, Installation, Testing and commissioning of Platform type Electronic Weighing Scale operated on 230 V AC,50 Hz +/- 10% along with calibration reports, stamping documents, inbuilt printing facility, RS-232 port, MS frame, SS/MSC load platter, remote display etc. and all its technical specifications as per OEM recommendation consisting of following Capacities Capacity- 2000kg, Accuracy 100-500gm, Platform size 1000mmX1200mm Make: Essae Model: DS-215HD or equivalent. | 4.00 | Each |  | 12075.00 | 48300.00 | 144283.00 | 577132.00 | 16000.00 | 64000.00 | 67000.00 | 268000.00 | 32000.00 | 128000.00 | 48300.00 | RB MULTITECH
43.00 | Supply, Installation, Testing and commissioning of Platform type Electronic Weighing Scale operated on 230 V AC,50 Hz +/- 10% along with calibration reports, stamping documents, printing facility, RS-232 port, SS load platter, remote display etc. and all its technical specifications as per OEM recommendation consisting of following Capacities Capacity- 15kg, Accuracy 2.0 gm, Platform size 280mmX340mm Make: Essae Model: SI-810PR or equivalent. | 2.00 | Each |  | 9200.00 | 18400.00 | 61081.00 | 122162.00 | 9000.00 | 18000.00 | 24500.00 | 49000.00 | 16000.00 | 32000.00 | 18000.00 | Manish Electricals
44.00 | Supply and fixing of 600mm swep, 1440 RPM, 180W metal blade metal body industrial wall fan suitable for 240V, 1-ph 50HZ AC supply on wall/ metallic pole including connections, testing, commissioning etc. complete as required | 5.00 | Each |  | 7475.00 | 37375.00 | 6783.00 | 33915.00 | 16500.00 | 82500.00 | 6200.00 | 31000.00 | 8100.00 | 40500.00 | 31000.00 | Awasthi Electric Works
45.00 | Supplying and fixing 16 A, 415 V, 3-phse Industrial type socket outlet, with neutral and earth, metal enclosed plug top alongwith 16 A "C" curve, FP MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket outlet and complete with connections, testing and commissioning etc. as required. | 2.00 | Each |  | 1840.00 | 3680.00 | 4560.00 | 9120.00 | 1200.00 | 2400.00 | 4950.00 | 9900.00 | 5400.00 | 10800.00 | 2400.00 | Manish Electricals
46.00 | Supply, Installation, Testing and Commissioning of cubicle type of suitable size LT panel,as per IEC 61439-1 & IEC 61439-2, suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, shall be mounted on 60 cm height cement concrete foundations over suitable height MS angle base frame i/c grouting the stand with concrete mortar(As per standard or directed by EIC) nut bolts etc as required, and shall be fabricated in compartmentalized 4b modular design IP 54 from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having busbar with SMC bus bar supports, entire panel shall have a common GI earth bar with 2 Nos. earth stud, solid / flexible connections from main bus bar to switchgears and from switchgear output to cable termination block in cable alley with required size of AL conductors / bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half as per specifications. Mechanical interlock betwee incomers and buscoupler to be provided. Incomer-2 nos.: 250A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c rotary magnetic handle, spreader link, R,Y,B indication lamp- 1 Set, ON, OFF, TRIP indication lamp- Each 1 no., 2A SP 10kA control MCB, multifunction meter with suitable ratio CTs of class 1.0 accuracy, 3-ph energy meter of class 1.0 accuracy. Bus-coupler: 250A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c rotary magnetic handle, spreader link, ON, OFF, TRIP indication lamp- Each 1 no., 2A SP 10kA control MCB Outgoing: (a) 12 nos. 63A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c rotary magnetic handle, spreader link, ON, OFF, TRIP indication lamp- Each 1 no., (b)FP C32A MCB -02 nos. (c) SP C32A MCB- 06 nos. Busbar: TPN Aluminium alloy bus bars for high conductivity - 250A Rating, Isc=36kA for 1 sec | 1.00 | Each |  | 402500.00 | 402500.00 | 673997.00 | 673997.00 | 225000.00 | 225000.00 | 575000.00 | 575000.00 | 180000.00 | 180000.00 | 180000.00 | Ekveera Electrical Works & Services
47.00 | Supply, Installation, Testing and Commissioning of cubicle type IP 54 LT panel with slanting top rain shed suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, shall be mounted on 60 cm height cement concrete foundations over suitable height MS angle base frame i/c grouting the stand with concrete mortar(As per standard or directed by EIC) nut bolts etc as required, and shall be fabricated from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having busbar with SMC bus bar supports, entire panel shall have a common GI earth bar with 2 Nos. earth stud, solid / flexible connections from main bus bar to switchgears and from switchgear output to cable termination block in cable alley with required size of AL conductors / bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable gland plates in two half as per specifications. Incomer: 63A FP 36kA MCCB (Thermal Magnetic release with O/L, S/C & E/F protection) Ics=100%Icu i/c rotary magnetic handle, spreader link, R,Y,B indication lamp- 1 Set, ON, OFF, TRIP indication lamp- Each 1 no., 2A SP 10kA control MCB, multifunction meter with suitable ratio CTs of class 1.0 accuracy Outgoing: (a)FP C32A MCB -01 nos. (b) SP C32A MCB- 10 nos. Busbar: TPN Aluminium alloy bus bars for high conductivity - 200A Rating, Isc=36kA for 1 sec | 2.00 | Each |  | 34500.00 | 69000.00 | 132760.00 | 265520.00 | 78000.00 | 156000.00 | 82500.00 | 165000.00 | 63000.00 | 126000.00 | 69000.00 | RB MULTITECH
48.00 | Supply, installation, Testing and commissioning of exterior facia signboard fabricated with 3mm ACP of Eurobond /Alucobond /Renobond /Alubond /Alstone make, computer cut trilingual matter i.e. logo, text, symbol, background color etc. as instructed/approved by Engineer-in-charge, 3mm thick inner side poly carbonate sheet so as the lettering will glow white evenly by providing suitable LED modules with driver. It shall be fixed on wall/roof/concrete surface by providing suitable size GI pipe, clamp, base plate etc., The boxing will be formed after making U grove on back side of ACP and it shall be folded with folding jig, press flat to ensure straight line. The corners at the edges shall be sealed with suitable outdoor type sealant. There shall be aluminium frame of 2" X 1" of 16 SWG rectangular pipe inside the boxing to screw the structure and make it rigid. Rear side/centre opening shall be provided on the boxing to carry out easy maintenance of sign board etc. complete as required. | 10.00 | Sqm |  | 8050.00 | 80500.00 | 15447.00 | 154470.00 | 12000.00 | 120000.00 | 48000.00 | 480000.00 | 1800.00 | 18000.00 | 18000.00 | Ekveera Electrical Works & Services
49.00 | Supply installation testing commissioning of corrosion resistant, stainless chrome body, non-radioactive, fully autonomous Advanced Early Streamer Emission Air Terminal (ESEAT) (make and model: Cosmoss-40 or equivalent) lightning protection system suitable for both negative and positive polarized discharge with CPRI tested average gain in triggering time (ΔTs) 63µs complying with NFC17-102 version 2011, protection radius 107 mtr including six digit digital discharge event counter in weather proof enclosure, 5mtr mounting mast with supproting rope, fastener, D-clamp, foundation bolt, nut and other accessories etc. It also includes supply installation testing commissioning of maintenance free 03 nos. compound earth electrodes (76mmX1mtr long with 15kg standard backfill compund each) and its interconnection to ESEAT by 70 sqmm flexible copper cable of required length with proper support and provision of test link box etc. complete as required. | 1.00 | Job |  | 73796.00 | 73796.00 | 125400.00 | 125400.00 | 195000.00 | 195000.00 | 155000.00 | 155000.00 | 36000.00 | 36000.00 | 36000.00 | Ekveera Electrical Works & Services
50.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Set |  | 3450.00 | 13800.00 | 8675.00 | 34700.00 | 9000.00 | 36000.00 | 8000.00 | 32000.00 | 14000.00 | 56000.00 | 13800.00 | RB MULTITECH
51.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Meter |  | 402.00 | 8040.00 | 195.00 | 3900.00 | 625.00 | 12500.00 | 650.00 | 13000.00 | 230.00 | 4600.00 | 3900.00 | Taral Electricals
52.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 30.00 | Meter |  | 103.00 | 3090.00 | 166.00 | 4980.00 | 425.00 | 12750.00 | 140.00 | 4200.00 | 180.00 | 5400.00 | 3090.00 | RB MULTITECH
53.00 | Supply and laying of FRP cable tray with cover 3-6mm thick, 100mm width in ground including required fixing arrangement with proper finish etc. complete as required. Make: Aeron or equivalent. | 70.00 | Meter |  | 402.00 | 28140.00 | 986.00 | 69020.00 | 325.00 | 22750.00 | 560.00 | 39200.00 | 230.00 | 16100.00 | 16100.00 | Ekveera Electrical Works & Services
54.00 | Laying of cable for IT system like CAT-6 cable/CCTV camera cable etc. in existing cable tray/conduit pipe etc. as required. | 500.00 | Meter |  | 11.00 | 5500.00 | 14.00 | 7000.00 | 20.00 | 10000.00 | 15.00 | 7500.00 | 36.00 | 18000.00 | 5500.00 | RB MULTITECH
55.00 | Providing, Fixing,Testing and commissioning ISI marked portable type fire extinguishers of CO2 type 4.5 kg capacity as per IS‐ 15683 complete as required. | 6.00 | Each |  | 5175.00 | 31050.00 | 5415.00 | 32490.00 | 11500.00 | 69000.00 | 7800.00 | 46800.00 | 7200.00 | 43200.00 | 31050.00 | RB MULTITECH
56.00 | Providing, Fixing,Testing and commissioning ISI marked portable type fire extinguishers of 6 Kg capacity ABC Dry Powder type as per IS‐ 15683 complete as required. | 5.00 | Each |  | 1296.00 | 6480.00 | 1824.00 | 9120.00 | 9500.00 | 47500.00 | 4200.00 | 21000.00 | 18000.00 | 90000.00 | 6480.00 | RB MULTITECH
57.00 | Supply & installation of 4 Nos. mild steel sand buckets of 9 litre capacity painted "Red Color" with nomenclature "FIRE" white in english and black in hindi filled with sand complete with stand & canopy duly painted "Red Color" of suitable height to hang 4 Buckets as required. | 3.00 | Each |  | 2310.00 | 6930.00 | 13680.00 | 41040.00 | 7500.00 | 22500.00 | 9500.00 | 28500.00 | 1650.00 | 4950.00 | 4950.00 | Ekveera Electrical Works & Services
58.00 | Providing laying, testing & commissioning of 'C' class heavy duty MS Pipe conforming to IS 1239/3589 i/c fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. in ground including welding, excavation & providing cement concrete blocks as supports, anticorrosive treatment with coaltar/asphalt tape as per IS 10221, refilling the trench etc. of following sizes complete as required. 150 mm. Dia | 50.00 | Meter |  | 2300.00 | 115000.00 | 3675.00 | 183750.00 | 1850.00 | 92500.00 | 1950.00 | 97500.00 | 450.00 | 22500.00 | 22500.00 | Ekveera Electrical Works & Services
59.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required. 150 mm dia | 100.00 | Meter |  | 2070.00 | 207000.00 | 2940.00 | 294000.00 | 1450.00 | 145000.00 | 1950.00 | 195000.00 | 390.00 | 39000.00 | 39000.00 | Ekveera Electrical Works & Services
60.00 | Supplying, fixing, testing and commissioning of 150mm dia butterfly valve of PN 1.6 rating with bronze /gunmetal seat duly ISI marked conforming to IS 13095 and 4-way fire brigade connection of cast iron body with gun metal male instantaneous inlet couplings complete with cap, chain as reqd. conforming to IS 904 for 150mm dia MS pipe connection including nuts, bolts, washers, gaskets, flanges, bend etc. as required. | 1.00 | Each |  | 23320.00 | 23320.00 | 4725.00 | 4725.00 | 9500.00 | 9500.00 | 19250.00 | 19250.00 | 4500.00 | 4500.00 | 4500.00 | Ekveera Electrical Works & Services
61.00 | Supply installation testing commissioning of 1.0 (approx.) meter high from ground 'C' class heavy duty 80mm dia MS pipe painted with two or more coats of synthetic enamel paint of required shade conforming to IS 3589/IS 1239 with suitable clamp/support frame, 80mm dia butterfly valve of PN 1.6 rating with bronze/gunmetal seat duly ISI marked complete conforming to IS 13095, single headed gunmetal external yard hydrant valve with 1 No. 63 mm dia instantaneous FM Gunmetal coupling and cast iron wheel, ISI marked, conforming to IS 5290 (type A) with blank Gunmetal cap and chain including Welding, fittings like elbows, tees, bend, flanges, tapers, nuts, bolts, gaskets, washer etc. complete as required. | 3.00 | Each |  | 14401.00 | 43203.00 | 9975.00 | 29925.00 | 1250.00 | 3750.00 | 14900.00 | 44700.00 | 4100.00 | 12300.00 | 3750.00 | Manish Electricals
62.00 | Supply installation testing commissioning of 900mm (L) X 760mm(H) X 400mm(W) Hose cabinet duly painted with red synthetic enamel paint, made of 2mm thick MS sheet with 6mm thick glazed glass doors, necessary locking arrangement, suitable foundation, associated breakable glass door red color hose key enclosure etc. It also includes supply fixing of 63 mm dia gun metal short branch pipe with 20 mm nominal internal diameter size nozzle conforming to IS 903 and 02 nos. 63 mm dia, 15 m long RRL non percolating hose pipe with 63 mm dia male and female gunmetal couplings duly bound with GI wire, rivets etc. conforming to IS 636 (type-A) for which the short branch pipe shall be suitable for instantaneous connection etc. complete as required. | 3.00 | Each |  | 46000.00 | 138000.00 | 21000.00 | 63000.00 | 17500.00 | 52500.00 | 17900.00 | 53700.00 | 2700.00 | 8100.00 | 8100.00 | Ekveera Electrical Works & Services
63.00 | Supply,Installation,testing and commisioning of 3 loop addressable fire alarm panel of with 6X40 characters,blue LCD display,programming throught PC or keypad,160 fire zone,RS-485 port for peripheral connection, 2-programable output sounders i/c loop cards & accessories, 24V DC supply Make: Morley Honeywell, model ZX5Se or equivalent | 1.00 | Each |  | 207000.00 | 207000.00 | 162755.00 | 162755.00 | 125000.00 | 125000.00 | 245000.00 | 245000.00 | 18000.00 | 18000.00 | 18000.00 | Ekveera Electrical Works & Services
64.00 | Supply,Installation,testing and commisioning of repeater panel complete with nine LED indicators provide a quick summary of the general system status for the user upto 100 recent events; this also aids commissioning, silence, mute, reset, accept, evacute and test controls, 24V DC supply required for i/c communication cards & accessories. Make Morley Honeywell model ZXr-A or equivalent. | 1.00 | Each |  | 49680.00 | 49680.00 | 50400.00 | 50400.00 | 54000.00 | 54000.00 | 85000.00 | 85000.00 | 14000.00 | 14000.00 | 14000.00 | Ekveera Electrical Works & Services
65.00 | Supply,Installation,testing and commisioning of autodialer for Morley Honeywell panels with 2 triger controller 32-bit processer,LCD keypad,16 text SMS option, 20 sec recording time with 10 phone numbers programable options i/c all accessories. | 1.00 | Each |  | 19397.00 | 19397.00 | 8610.00 | 8610.00 | 21000.00 | 21000.00 | 16700.00 | 16700.00 | 27000.00 | 27000.00 | 8610.00 | Taral Electricals
66.00 | Supplying & laying of 2Cx1.5 sqmm fire survival armoured cable, 600/1000V rated with annealed copper conductor having glass mica fire barrier tape covered by an extruded layer of XLPE insulation and FRLS inner seathed, GI wire strip armouring & FRLS outer sheath complete as required. | 300.00 | Meter |  | 230.00 | 69000.00 | 95.00 | 28500.00 | 125.00 | 37500.00 | 245.00 | 73500.00 | 270.00 | 81000.00 | 28500.00 | Taral Electricals
67.00 | Design, supplying, installation, testing & commissioning of addressable smoke detector with builtin LED and mounting base complete with all connections etc. as required | 40.00 | Each |  | 1771.00 | 70840.00 | 1838.00 | 73520.00 | 1850.00 | 74000.00 | 2350.00 | 94000.00 | 2700.00 | 108000.00 | 70840.00 | RB MULTITECH
68.00 | Supplying, installation, testing & commissioning of addressable manual call box of ABS type in surface/recess with stainless steel chain & hammer assembly complete with glass and push button etc. as required | 4.00 | Each |  | 415.00 | 1660.00 | 2363.00 | 9452.00 | 2350.00 | 9400.00 | 3600.00 | 14400.00 | 1400.00 | 5600.00 | 1660.00 | RB MULTITECH
69.00 | Supply installation testing commissioning of fire alarm addressable control modue with 02 nos. fire alarm hooter cum flasher including programming, provision of 24V DC supply, interconnection etc. complete as required but excluding supply of interconnecting wire/cable. | 2.00 | Each |  | 7475.00 | 14950.00 | 5880.00 | 11760.00 | 3200.00 | 6400.00 | 4130.00 | 8260.00 | 7200.00 | 14400.00 | 6400.00 | Manish Electricals
| Total in Figures |  |  |  |  | 3456697.00 |  | 5442850.00 |  | 3997050.00 |  | 4861470.00 |  | 3627630.00
Lowest Amount Quoted BY: RB MULTITECH(3456697.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of Integrated of cargo terminal at Pune Airport SH Electrical Works Tender ID: 2021_AAI_99850_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | RB MULTITECH | 3456697.00 | L1
| 2 | Ekveera Electrical Works & Services | 3627630.00 | L2
| 3 | Manish Electricals | 3997050.00 | L3
| 4 | Awasthi Electric Works | 4861470.00 | L4
| 5 | Taral Electricals | 5442850.00 | L5