## BoQ1
Government eProcurement System Created By: Riddhiman Dey Created Date/Time: 13-Nov-2021 12:28 PM Tender Title: Providing and Erection of 7M height Street Light Poles along with 60W LED luminaries besides the proposed Patrolling roads at Sector I and II, Falta Special Economic Zone (FSEZ), Falta, West Bengal Tender ID: 2021_WAPCO_85019_1
Tender Inviting Authority: WAPCOS LIMITED
Name of Work: Providing & Erection of 7M height Street Light Poles along with 60W LED luminaries besides the proposed Patrolling roads at Sector I & II, Falta Special Economic Zone (FSEZ), Falta, West Bengal.
Contract No: WAP/D&RE/KOL/TURGA/FSEZ/PMC/2021-22/07
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SAHIL CONSTRUCTION(GSTN-NA) |  | K. P. Construction(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply and delivery at site of 2 Core 6 Sq mm PVC/XLPE insulated armoured Al conductor cable A2XWY/A2XFY of 1100V grade and conforming to IS:7098 (Part-I) 1988. (Make:- Polycab/Finolex or any other make as approved by EIC). | 100.00 | Meter |  | 93.00 | 9300.00 | 92.00 | 9200.00 | 9200.00 | K. P. Construction
2.00 | Laying and fixing of one number (For each Main Switch) PVC/XLPE insulated and PVC/XLPE power cable of 1.1 KV grade of 2 Core 6 Sq mm on wall surface as required to complete the work (clamped with 2mm thick saddle). | 60.00 | Meter |  | 35.00 | 2100.00 | 32.00 | 1920.00 | 1920.00 | K. P. Construction
3.00 | Laying of one number (For each Main Switch) PVC/XLPE insulated and PVC/XLPE power cable of 1.1 KV grade of 2 Core 6 Sq mm size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required to complete the work. | 40.00 | Meter |  | 283.00 | 11320.00 | 295.00 | 11800.00 | 11320.00 | SAHIL CONSTRUCTION
4.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 2 Core 6 Sq mm of PVC/XLPE insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 10.00 | Each |  | 173.00 | 1730.00 | 180.00 | 1800.00 | 1730.00 | SAHIL CONSTRUCTION
5.00 | Supplying and Fixing 240V DP with porcelain cutout and fuse on L&N Sheet steel Main Switches on flat iron frame on wall etc. as required to complete the work (Make:- Havells/ Standard/Anchor or any other make as approved by EIC). | 10.00 | Set |  | 1142.00 | 11420.00 | 1203.00 | 12030.00 | 11420.00 | SAHIL CONSTRUCTION
6.00 | Supply and delivery at site of 2 Core 4 Sq mm PVC/XLPE insulated armoured Al conductor cable A2XWY/A2XFY of 1100V grade and conforming to IS:7098 (Part-I) 1988 (Make:- Polycab/Finolex or any other make as approved by EIC). | 2300.00 | Meter |  | 78.00 | 179400.00 | 79.00 | 181700.00 | 179400.00 | SAHIL CONSTRUCTION
7.00 | Laying of one number (For each Main Switch) PVC/XLPE insulated and PVC/XLPE power cable of 1.1 KV grade of 2 Core 4 Sq mm size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required to complete the work with fixing of cable trench marker. | 2100.00 | Meter |  | 283.00 | 594300.00 | 296.00 | 621600.00 | 594300.00 | SAHIL CONSTRUCTION
8.00 | Supplying and fixing compression type gland complete with brass gland, brass ring & rubber ring for dust & moisture-proof entry of XLPE/PVC armoured cables (2 Core 4 Sq mm). | 10.00 | Set |  | 53.00 | 530.00 | 55.00 | 550.00 | 530.00 | SAHIL CONSTRUCTION
9.00 | Finishing the end of 2 Core 4 Sq mm XLPE armoured cables by crimping method incl. supplying and fixing solder less socket (Dowels make), tapes, anticorrosive paste & jointing materials. | 10.00 | Set |  | 28.00 | 280.00 | 27.00 | 270.00 | 270.00 | K. P. Construction
10.00 | Supplying of MS Aluminium painted 7 Mtr. long (Swaged Type) Steel tubular pole as per IS: 2713/1986 Part-I-II (Conforming to 410-SP-01) with MS Base Plate (250x250x5 mm) (welded) & junction box unction box for interconnection etc. at bottom as required. (Make:- Electro Poles or any other reputed make as approved by EIC). | 140.00 | Each |  | 4385.00 | 613900.00 | 4210.00 | 589400.00 | 589400.00 | K. P. Construction
11.00 | Excavation of soil for Erection of Steel tubular Pole and filling & ramming. | 86.00 | Cu. Mtr |  | 193.00 | 16598.00 | 195.00 | 16770.00 | 16598.00 | SAHIL CONSTRUCTION
12.00 | Erection of Single Steel tubular pole of 7 Mtr. length with sole plate & Cap etc. in CC foundation (0.6x0.6x1.70mt.) as per drawing having 600x600x450 mm thick CC (4:2:1) base block below sole plate/pole with hard jhama metal including CC (6:3:1) muffing 0.30 mts. dia and 0.30 mts above ground level including 3 mm thick neat cemented finish and GI earth bolt after making drilled holes etc. on pole & carriage of pole from Store to work-site including filling up the excavated earth pit with shifted soil and ramming properly. | 140.00 | Set |  | 2527.00 | 353780.00 | 2655.00 | 371700.00 | 353780.00 | SAHIL CONSTRUCTION
13.00 | Distribution wiring for steel light on pole for street light fitting with 2x1/1.40 PVC insulated and sheathed copper wire (single core) in 15 mm dia GI Pipe (ISI-Medium) control switch, incl. fitting and fixing the light fitting by providing 32 mm/suitable dia GI Pipe bracket of lengh 1.05 mts, on pole incl. S&F sutable MS flat clamps with bolts, nuts etc. as required and painting. | 140.00 | Set |  | 1006.00 | 140840.00 | 939.00 | 131460.00 | 131460.00 | K. P. Construction
14.00 | Supply, Delivery, Installation & Testing of 60W LED Street light Class 1 Electrical Protection, Decorative, Modern style & Superior aesthetic look Pressure die-cast Aluminum (LM6 alloy) housing, Dark Grey, LED fittings with inbuilt 4kV surge protection, Long life, Environment friendly, Energy efficient, 5700K, IP 66/IK08 protection LED light fitting complete with all accessories, Toughened and Shatter proof quality built-in lens & cover, replaceable driver, control units, surge protection device, mechanical parts etc. Technical Specification :- System Lumen - 6600 lm Wattage - 60 W Luminous Efficiency - 110 lm/W CRI - 70 Life - minimum 50000 Hrs @ Ta 35 deg C IP rating - 66 IK rating - 08 Operating Voltage range - 120 to 270 V High Voltage Cutoff - 325 (+/- 15V) Phase to Phase Protection - 440V (8 hrs.) Auto Restart - Yes Dimensions L x W x H - 473 x 165 x 80 mm (Make:- As approved by Client/EIC) | 140.00 | Set |  | 5262.00 | 736680.00 | 5180.00 | 725200.00 | 725200.00 | K. P. Construction
15.00 | Earthing with 50 mm dia GI pipe 3.64 mm thick x 3.04 Mts. long and 1 x 4 SWG GI (Hot Dip) wire (4 Mts. long), 13 mm dia x 80 mm long GI bolts, double nuts, double washers incl. S & F 15 mm dia GI pipe protection (1 Mts. long) to be filled with bitumen partly under the ground level and partly above ground level driven to an average depth of 3.65 Mts. below the ground level by TATA-Medium GI pipe. | 20.00 | Each |  | 1362.00 | 27240.00 | 1434.00 | 28680.00 | 27240.00 | SAHIL CONSTRUCTION
16.00 | Excavation of soil for installation of Earth Electrode and filling & ramming. | 42.00 | Cu. Mtr |  | 193.00 | 8106.00 | 194.00 | 8148.00 | 8106.00 | SAHIL CONSTRUCTION
17.00 | Connecting the equipments (LED light fixtures) to earth busbar including S & F GI (Hot Dip) wire of 8 SWG size on wall/along the cables with staples buried inside wall/floor as required and making connection to equipments with bolts, nuts, washers, cable lugs etc. as required and mending good damages. | 2400.00 | Meter |  | 10.00 | 24000.00 | 9.00 | 21600.00 | 21600.00 | K. P. Construction
| Total in Figures |  |  |  |  | 2731524.00 |  | 2733828.00
Lowest Amount Quoted BY: SAHIL CONSTRUCTION(2731524.00)

## BOQ Summary
BOQ Summary Details Tender Title: Providing and Erection of 7M height Street Light Poles along with 60W LED luminaries besides the proposed Patrolling roads at Sector I and II, Falta Special Economic Zone (FSEZ), Falta, West Bengal Tender ID: 2021_WAPCO_85019_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SAHIL CONSTRUCTION | 2731524.00 | L1
| 2 | K. P. Construction | 2733828.00 | L2