## BoQ1
Government eProcurement System Created By: BIJU K G Created Date/Time: 28-Feb-2022 05:56 PM Tender Title: Provision for Outdoor Feeder Pillar and associated cable laying works for existing Terminal Building at Tuticorin Airport Tender ID: 2022_AAI_101911_1
Tender Inviting Authority: Airports Authority of India, Tuticorin Airport, Tuticorin - 628103.
Name of Work: Provision for Outdoor Feeder Pillar and associated cable laying works for existing Terminal Building at Tuticorin Airport.
Tender ID: 2021_AAI_101911_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Shantha ELectricals and Engineers Pvt Ltd(GSTN-29AARCS2866G1ZP) |  | BR Power Control and Automation Services(GSTN-06AREPS4024K1ZP) |  | LINSTA SERVICES(GSTN-32BMKPS6907H1ZS) |  | DElite System Engineering (India) Pvt. Ltd.(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of outdoor LT feeder pillar panel with double door arrangement, outer cover made up of 14 SWG and inner front, top covers and all partitions made up of 14 SWG CRCA sheet steel, with degree of protection not less than IP54, i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, door dust tight, vermin proof, totally enclosed, cubicle type, floor mounting, free standing, including providing and fixing 300 A Aluminium Bus bar with all accessories suitable for operation at 415 V, 3 phase, 4 wire, 50 Hz, A.C. power supply system complete with all accessories, interconnection, mechanical interlocking arrangement, connection, earthing, painting, grouting, providing pedestal, cable Entry provision wih all necessary accessories etc. as required and comprising the following : INCOMER 250 A, 36 kA, 4P MCCB with Microprocessor based releases as incomer with R,Y,B,ON,OFF, Trip indication lamps, resin cast CT's with 3 phase multifunction meter with RS 485 (for V, A, kWH, kW, PF, Hz, kVA & THD - L&T WL 5010 or equivalent)- 2 sets as incomer suitable for terminating incomers of 3.5 core 300 sq.mm with suitable spreader links. BUS-COUPLER 250 A, 36 kA, 4P MCCB bus coupler microprocessor based releases with R,Y,B,ON,OFF indication lamps- 1 set as bus coupler. OUTGOINGS a) 160 A, 25KA, 4P MCCB with microprocessor based releases with resin cast CTs, digital Ammeter, ON, OFF, Trip indication lamps as outgoing - 2 set as outgoing. b) 125 A, 25KA, 4P MCCB with microprocessor based releases with resin cast CTs, digital Ammeter, ON, OFF, Trip indication lamps as outgoing - 2 sets as outgoing. c) 100 A, 25KA, 4P MCCB with microprocessor based releases with resin cast CTs, digital Ammeter, ON, OFF, Trip indication lamps as outgoing - 2 sets as outgoing. d) 63A, 25KA, 4P MCCB with microprocessor based releases with resin cast CTs, digital Ammeter, ON, OFF, Trip indication lamps as outgoing - 8 sets as outgoing. e) 32A, 25KA, 4P MCCB with microprocessor based releases with resin cast CTs, digital Ammeter, ON, OFF, Trip indication lamps as outgoing - 8 sets as outgoing. | 1.00 | Job |  | 1450000.00 | 1450000.00 | 749123.00 | 749123.00 | 890000.00 | 890000.00 | 1200000.00 | 1200000.00 | 749123.00 | BR Power Control and Automation Services
2.00 | Supplying of following sizes of 1.1 KV grade, XLPE insulated, Aluminium conductor armoured Power Cable conforming to IS 7098 Part-I 1985 with upto date amendments complete as required as per specifications. 3.5 core, 300 sq.mm | 240.00 | Metre |  | 1250.00 | 300000.00 | 1779.00 | 426960.00 | 1800.00 | 432000.00 | 1499.00 | 359760.00 | 300000.00 | Shantha ELectricals and Engineers Pvt Ltd
3.00 | Supplying of following sizes of 1.1 KV grade, XLPE insulated, Aluminium conductor armoured Power Cable conforming to IS 7098 Part-I 1985 with upto date amendments complete as required as per specifications. 3.5 core, 35 sq.mm | 35.00 | Metre |  | 250.00 | 8750.00 | 277.00 | 9695.00 | 290.00 | 10150.00 | 229.00 | 8015.00 | 8015.00 | DElite System Engineering (India) Pvt. Ltd.
4.00 | Supplying of following sizes of 1.1 KV grade, XLPE insulated, copper conductor armoured Power Cable conforming to IS 7098 Part-I 1985 with upto date amendments complete as required as per specifications. 4 core, 10 sq.mm | 40.00 | Metre |  | 520.00 | 20800.00 | 610.00 | 24400.00 | 620.00 | 24800.00 | 499.00 | 19960.00 | 19960.00 | DElite System Engineering (India) Pvt. Ltd.
5.00 | Supplying of following sizes of 1.1 KV grade, XLPE insulated, copper conductor armoured Power Cable conforming to IS 7098 Part-I 1985 with upto date amendments complete as required as per specifications. 4 core, 6 sq.mm | 350.00 | Metre |  | 345.00 | 120750.00 | 405.00 | 141750.00 | 410.00 | 143500.00 | 299.00 | 104650.00 | 104650.00 | DElite System Engineering (India) Pvt. Ltd.
6.00 | Providing and laying of 150mm dia B class G.I pipe below 0.5 mtr, across road including cutting bituminous road and refilling with concrete to the original finish etc. complete as required. | 24.00 | Metre |  | 5100.00 | 122400.00 | 5228.00 | 125472.00 | 2200.00 | 52800.00 | 3000.00 | 72000.00 | 52800.00 | LINSTA SERVICES
7.00 | Supply and installing following size of perforated Hot Dipped Galvanised Iron cable tray cable tray with perforation not more than 17.5%, including all accessories like connectors, bends, nuts, bolts etc as required and duly supported with GI coated MS angles/SS fasteners on wall and cement concrete on terrace etc as required. 300 mm width x 50 mm depth x 1.6 mm thickness | 10.00 | Metre |  | 1600.00 | 16000.00 | 1716.00 | 17160.00 | 850.00 | 8500.00 | 1500.00 | 15000.00 | 8500.00 | LINSTA SERVICES
8.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 185 sq. mm and upto 400 sq. mm | 30.00 | Metre |  | 110.00 | 3300.00 | 151.00 | 4530.00 | 150.00 | 4500.00 | 199.00 | 5970.00 | 3300.00 | Shantha ELectricals and Engineers Pvt Ltd
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/ HDPE/ PVC pipe as required. Upto 35 sq.mm | 420.00 | Metre |  | 90.00 | 37800.00 | 69.00 | 28980.00 | 60.00 | 25200.00 | 50.00 | 21000.00 | 21000.00 | DElite System Engineering (India) Pvt. Ltd.
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/ HDPE pipe as required. Above 35 sq. mm and upto 95 sq. mm | 20.00 | Metre |  | 80.00 | 1600.00 | 94.00 | 1880.00 | 80.00 | 1600.00 | 50.00 | 1000.00 | 1000.00 | DElite System Engineering (India) Pvt. Ltd.
11.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/ HDPE pipe as required. Above 185 sq. mm and upto 400 sq. mm | 420.00 | Metre |  | 180.00 | 75600.00 | 151.00 | 63420.00 | 100.00 | 42000.00 | 199.00 | 83580.00 | 42000.00 | LINSTA SERVICES
12.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface/ tray as required. Upto 35 sq. mm | 10.00 | Metre |  | 70.00 | 700.00 | 75.00 | 750.00 | 80.00 | 800.00 | 50.00 | 500.00 | 500.00 | DElite System Engineering (India) Pvt. Ltd.
13.00 | Retrieval of cables of XLPE insulated / PVC sheathed cables of size upto 95 sq.mm from ground by excavation in soft soil, depth upto 1.2 m including getting out the excavated soil, refilling with sand and or good soil after retrieving the cable/ pipe etc. and disposal of surplus excavated soil as directed, within a lead of 50 meter without ramming and watering. | 65.00 | Metre |  | 250.00 | 16250.00 | 314.00 | 20410.00 | 120.00 | 7800.00 | 299.00 | 19435.00 | 7800.00 | LINSTA SERVICES
14.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. OD-120 mm & ID-103 mm nominal | 300.00 | Metre |  | 325.00 | 97500.00 | 282.00 | 84600.00 | 220.00 | 66000.00 | 350.00 | 105000.00 | 66000.00 | LINSTA SERVICES
15.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. OD-63 mm & ID-51 mm nominal | 50.00 | Metre |  | 235.00 | 11750.00 | 224.00 | 11200.00 | 130.00 | 6500.00 | 300.00 | 15000.00 | 6500.00 | LINSTA SERVICES
16.00 | Dismantling of existing 2 nos. LT panel installed inside the terminal building and relocating the same to electrical store outside power house as per direction of Engineer-in-charge, removing the cable from the existing Panels, making it suitable for terminating the cables to the new panel without affecting airport operations etc complete as required. | 1.00 | Job |  | 15000.00 | 15000.00 | 10060.00 | 10060.00 | 2500.00 | 2500.00 | 20000.00 | 20000.00 | 2500.00 | LINSTA SERVICES
17.00 | Supplying and making end termination with brass single compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/ XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 core x 300 sq.mm | 4.00 | Set |  | 2200.00 | 8800.00 | 2447.00 | 9788.00 | 1750.00 | 7000.00 | 900.00 | 3600.00 | 3600.00 | DElite System Engineering (India) Pvt. Ltd.
18.00 | Supplying and making end termination with brass single compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/ XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 core x 95 sq.mm | 1.00 | Set |  | 1500.00 | 1500.00 | 1615.00 | 1615.00 | 1000.00 | 1000.00 | 900.00 | 900.00 | 900.00 | DElite System Engineering (India) Pvt. Ltd.
19.00 | Supplying and making end termination with brass single compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/ XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 core x 70 sq.mm | 2.00 | Set |  | 1200.00 | 2400.00 | 1190.00 | 2380.00 | 850.00 | 1700.00 | 900.00 | 1800.00 | 1700.00 | LINSTA SERVICES
20.00 | Supplying and making end termination with brass single compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/ XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 core x 50 sq.mm | 1.00 | Set |  | 900.00 | 900.00 | 934.00 | 934.00 | 750.00 | 750.00 | 900.00 | 900.00 | 750.00 | LINSTA SERVICES
21.00 | Supplying and making end termination with brass single compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed/ XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 core x 35 sq.mm | 2.00 | Set |  | 700.00 | 1400.00 | 708.00 | 1416.00 | 600.00 | 1200.00 | 750.00 | 1500.00 | 1200.00 | LINSTA SERVICES
22.00 | Supplying and making end termination with brass single compression gland and copper lugs for following size of PVC insulated and PVC sheathed/ XLPE copper conductor cable of 1.1 KV grade as required. 4 core x 10 sq.mm | 2.00 | Set |  | 500.00 | 1000.00 | 1190.00 | 2380.00 | 450.00 | 900.00 | 500.00 | 1000.00 | 900.00 | LINSTA SERVICES
23.00 | Supplying and making end termination with brass single compression gland and copper lugs for following size of PVC insulated and PVC sheathed/ XLPE copper conductor cable of 1.1 KV grade as required. 4 core x 6 sq.mm | 14.00 | Set |  | 350.00 | 4900.00 | 1059.00 | 14826.00 | 400.00 | 5600.00 | 500.00 | 7000.00 | 4900.00 | Shantha ELectricals and Engineers Pvt Ltd
24.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size 3.5 core PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required for the following size: 25 sq.mm to 50 sq.mm | 3.00 | Set |  | 3500.00 | 10500.00 | 3170.00 | 9510.00 | 3000.00 | 9000.00 | 4000.00 | 12000.00 | 9000.00 | LINSTA SERVICES
25.00 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. 32 mm | 40.00 | Metre |  | 55.00 | 2200.00 | 158.00 | 6320.00 | 130.00 | 5200.00 | 200.00 | 8000.00 | 2200.00 | Shantha ELectricals and Engineers Pvt Ltd
26.00 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. 25 mm | 350.00 | Metre |  | 40.00 | 14000.00 | 147.00 | 51450.00 | 110.00 | 38500.00 | 150.00 | 52500.00 | 14000.00 | Shantha ELectricals and Engineers Pvt Ltd
27.00 | Supplying and fixing following way, three pole and neutral, MCB distribution board, of IP 43, double door type, 415 volts, on surface/ recess, complete with tinned copper busbars, neutral link, earth bar, din bar, detachable gland plate, interconnections, phosphatized and powder painted including earthing etc.as required (but without MCB/RCCB/Isolator). 12 way (8 + 36), Metal door, vertical type | 1.00 | Job |  | 15000.00 | 15000.00 | 18528.00 | 18528.00 | 16100.00 | 16100.00 | 15000.00 | 15000.00 | 15000.00 | DElite System Engineering (India) Pvt. Ltd., Shantha ELectricals and Engineers Pvt Ltd
28.00 | Supplying and fixing following way, three pole and neutral, MCB distribution board, of IP 43, double door type, 415 volts, on surface/ recess, complete with tinned copper busbars, neutral link, earth bar, din bar, detachable gland plate, interconnections, phosphatized and powder painted including earthing etc.as required (but without MCB/RCCB/Isolator). 8 way (8 + 24), Metal door, vertical type | 1.00 | Job |  | 10500.00 | 10500.00 | 14231.00 | 14231.00 | 13400.00 | 13400.00 | 14000.00 | 14000.00 | 10500.00 | Shantha ELectricals and Engineers Pvt Ltd
29.00 | Supplying and fixing 63 Amps FP MCB rating, 415 volts, 'C' curve, miniature circuit breaker in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 1.00 | Job |  | 2900.00 | 2900.00 | 2574.00 | 2574.00 | 1950.00 | 1950.00 | 3000.00 | 3000.00 | 1950.00 | LINSTA SERVICES
30.00 | Supplying and fixing 32 Amps FP MCB rating, 415 volts, 'C' curve, miniature circuit breaker in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 1.00 | Job |  | 1800.00 | 1800.00 | 1798.00 | 1798.00 | 1450.00 | 1450.00 | 2000.00 | 2000.00 | 1450.00 | LINSTA SERVICES
31.00 | Supplying and fixing 32 Amps TP MCB rating, 415 volts, 'C' curve, miniature circuit breaker in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 2.00 | Job |  | 1250.00 | 2500.00 | 1325.00 | 2650.00 | 1450.00 | 2900.00 | 2000.00 | 4000.00 | 2500.00 | Shantha ELectricals and Engineers Pvt Ltd
32.00 | Supplying and fixing 20 Amps TP MCB rating, 415 volts, 'C' curve, miniature circuit breaker in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 2.00 | Job |  | 1250.00 | 2500.00 | 872.00 | 1744.00 | 1450.00 | 2900.00 | 2000.00 | 4000.00 | 1744.00 | BR Power Control and Automation Services
33.00 | Supplying and fixing 6 to 32 Amps SP MCB rating, 415 volts, 'C' curve, miniature circuit breaker in the existing MCB DB complete with connections, testing and commissioning etc. as reqd. | 48.00 | Job |  | 295.00 | 14160.00 | 380.00 | 18240.00 | 220.00 | 10560.00 | 500.00 | 24000.00 | 10560.00 | LINSTA SERVICES
34.00 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer-in-charge:Nominal concrete 1:3:6 or richer mix (i/c equivalent design mix) | 1.00 | Cum |  | 2500.00 | 2500.00 | 7540.00 | 7540.00 | 1500.00 | 1500.00 | 6000.00 | 6000.00 | 1500.00 | LINSTA SERVICES
35.00 | Excavation for foundation in soft soil including dressing of sides and ramming of bottoms, lift upto 1.5 m including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 metres. | 1.00 | Cum |  | 3500.00 | 3500.00 | 22600.00 | 22600.00 | 2500.00 | 2500.00 | 6000.00 | 6000.00 | 2500.00 | LINSTA SERVICES
36.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size). | 1.00 | Cum |  | 6500.00 | 6500.00 | 6400.00 | 6400.00 | 9000.00 | 9000.00 | 9000.00 | 9000.00 | 6400.00 | BR Power Control and Automation Services
37.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe, Tools & plants charges for bore drilling machine etc. with charcoal/ coke and salt as required. | 4.00 | Job |  | 16000.00 | 64000.00 | 12600.00 | 50400.00 | 9500.00 | 38000.00 | 12500.00 | 50000.00 | 38000.00 | LINSTA SERVICES
38.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess or ground for loop earthing along with existing cable as required. | 510.00 | Metre |  | 50.00 | 25500.00 | 34.00 | 17340.00 | 40.00 | 20400.00 | 49.00 | 24990.00 | 17340.00 | BR Power Control and Automation Services
39.00 | Providing and laying earth connections from earth electrode with 6 SWG dia G.I wire in 15 mm dia. G.I pipe from earth electrode as required. | 12.00 | Metre |  | 70.00 | 840.00 | 264.00 | 3168.00 | 150.00 | 1800.00 | 200.00 | 2400.00 | 840.00 | Shantha ELectricals and Engineers Pvt Ltd
40.00 | Providing and fixing 14 SWG copper wire on surface or in recess for loop earthing as required. | 390.00 | Metre |  | 80.00 | 31200.00 | 56.00 | 21840.00 | 60.00 | 23400.00 | 600.00 | 234000.00 | 21840.00 | BR Power Control and Automation Services
| Total in Figures |  |  |  |  | 2529200.00 |  | 2010062.00 |  | 1935360.00 |  | 2538460.00
Lowest Amount Quoted BY: LINSTA SERVICES(1935360.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision for Outdoor Feeder Pillar and associated cable laying works for existing Terminal Building at Tuticorin Airport Tender ID: 2022_AAI_101911_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | LINSTA SERVICES | 1935360.00 | L1
| 2 | BR Power Control and Automation Services | 2010062.00 | L2
| 3 | Shantha ELectricals and Engineers Pvt Ltd | 2529200.00 | L3
| 4 | DElite System Engineering (India) Pvt. Ltd. | 2538460.00 | L4