## BoQ1
Government eProcurement System Created By: SUBHASH KUMAR Created Date/Time: 02-Feb-2022 01:04 PM Tender Title: SITC OF DG SET FOR PAPI AT DARBHANGA AIRPORT Tender ID: 2022_AAI_101969_1
Tender Inviting Authority: Sr. Manager (E-E), AAI, Darbhanga Airport
Name of Work: Provision of Ground Lighting Facilities at Darbhanga Airport.( SH: SITC of DG Set for PAPIs at Darbhanga Airport)
Contract No: 2021_AAI_101969_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Ruhi Electronics(GSTN-10ABYPJ8411H1ZM) |  | Awasthi Electric Works(GSTN-09ABAPA1866D1Z5)
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-A: SITC of DG Set
1.01 | Supply, Installation, Testing and Commissioning of 15kVA ,single Phase, Silent DG Set as per IS:10002/BS:5514,ISO:3046, coupled through flexiable coupling to alternator, comprising of engine 32 BHP or suitable, designed & tested on 50℃ ambient temp. and 15 KVA, 230V alternator mounted on a common base, complete with Fuel tank for 8 hour running capacity, Batteries and leads, hospital grade Silencer, Standard Panel, First fill of lube oil, AVM Pads, Acoustic Enclosure as per CPCB norms. Specification for Genrator Set :- Power Rating KVA/KWe-15/12 . No.of Phase-1 Phase. Output Voltage-230V.Powerfactor-0.8 lagging. Current(1Phase)-65A. Frequency & RPM -50Hz& 1500RPM. Engine Specification:-MoEF Certified Power(BHP) 25. Cooling-Liquied cooled.Aspiration-Turbo charged. No. of cylinder-3 Fuel-High speed Diesel. Alternator Specification:- Alternator Frame-SOL2MI,Elclosure-IP23,Voltage Regulation(Max.)-±1%,Class of Insulation-H class.Total Harmonic Distortion-No load<1.5%,Non Distorting balanced linear load<5%, Maximum Unbalanced Load across Phases-Less then or equal to 25%. Control Panel:- Control Panel is manufactured with 14/16 gauge CRCA sheet and is powder coated for weather-proof and long losting finish. The control panel consists of the following parts: Controller(AMF functionality Inbuilt), Aluminum Bus-bar with suitable capacity of Incoming/Outgoing Terminals,Indicating lampsfor "Load ON" and "Set Running",Instrument fuses duly wired and ferruled,Circuit breakers of suitable rating with Overload and Short Circuit Protection. (a) Unloading Shifting DG set on Foundation. (c ) End termination of cable with Glands, Lugs & PVC tape-1 Job. (d) Testing commissioning with diesel as directed by EIC-1 Job. (e) Electrical safety approval from EIC, Electrical Safety- 1 Job. Defect liability Period of One year. | 1.00 | Job |  | 360000.00 | 360000.00 | 455000.00 | 455000.00 | 360000.00 | Ruhi Electronics
1.02 | SITC of movable Trolley made by mild steel clouwith four stand with three wheels suitable for upto 25KVA DG Set. | 1.00 | Job |  | 121000.00 | 121000.00 | 123500.00 | 123500.00 | 121000.00 | Ruhi Electronics
| Total in Figures |  |  |  |  | 481000.00 |  | 578500.00
Lowest Amount Quoted BY: Ruhi Electronics(481000.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC OF DG SET FOR PAPI AT DARBHANGA AIRPORT Tender ID: 2022_AAI_101969_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Ruhi Electronics | 481000.00 | L1
| 2 | Awasthi Electric Works | 578500.00 | L2