## BoQ1
Government eProcurement System Created By: Saubhik Pan Created Date/Time: 14-Mar-2022 01:00 PM Tender Title: Sub Station augmentation of Power Supply Eastern side of runway (C and E) at NSCBI Airport, Kolkata. (a) Co Hangar Sub station and Plant room. SH Electrical works. (Second Recall) Tender ID: 2022_AAI_102488_1
Tender Inviting Authority: AIRPORTS AUTHORITY OF INDIA
Name of Work: Sub-Station augmentation of Power Supply-Eastern side of runway (C+E) at NSCBI Airport, Kolkata. (a) C/o Hangar Sub-station & Plant room. SH: Electrical works.
Contract No: 2022_AAI_102488_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | K KUMAR RAJA PROJECTS PVT LIMITED(GSTN-37AABCK5644G1ZI) |  | Konstelec Engineers Pvt. Ltd.(GSTN-27AAACK2747D1ZS) |  | shiv electric(GSTN-07AACFS2722H1ZF) |  | EVERCREST PROJECTS PVT LTD(GSTN-24AADCE7826L1ZE)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Sub Head A:- Sub - Station Equipment: Design, Assembling, Supplying, Installation, testing and commissioning of 12 KV rated, 800A, 26.3 KA breaking capacity, 9 panels 2-way communicable VCBs (Incoming - 2 nos., Buscoupler - 1 no., Outgoing - 6 nos.) Switch Board should be fabricated out of 2 mm sheet steel, dust tight, vermin proof, totally enclosed and fully interlocked, IP 42 protection, cubicle type, free standing, floor mounted, extensible on both sides, complete with rack in - rack out mechanism, horizontal draw out, horizontal isolation type breaker as per IS/IEC 62271-1:2017 with necessary amendment up to date, suitable for indoor operation at 11 kV as well as 6 KV, 3 phase, 50 Hz, AC supply, with Bus Bar: 800A, 26.3 KA for 3 sec, 3 phase Copper bus bar- 1 set, 2 Nos Incomer and 1 No. Buscoupler: rating of 800 Amp, VCB & Outgoings - 2 Nos. (for Transformers) 630 amp VCB & 4 Nos. 630 amp (for other feeders) VCB having 12 KV grade, 26.3 kA breaking capacity with motorised spring charge mechanism rated for 230 volt AC, tripping coil and closing coil for 110 V DC as per specifications attached and as directed by Engineer-In-Charge. | 1.00 | Job |  | 6600000.00 | 6600000.00 | 3660000.00 | 3660000.00 | 3750000.00 | 3750000.00 | 3122550.00 | 3122550.00 | 3122550.00 | EVERCREST PROJECTS PVT LTD
2.00 | Design, Supply, installation, testing and commissioning of indoor type 2500 KVA 11 - 6 / 0.415 KV, 3 Phase, 50Hz, Dyn11, KNAN type, copper wound Transformer with Off load tap changing arrangement +5% to -10% of HV in steps of 2.5 percent for variation of HV having cable end box weather proof termination on HV side suitable for 3 Core x 300 Sq.mm. XLPE cable of 11 KV grade on HT side and 4000 Amp Aluminium sandwich bustrunking on LV side complete with all accessories like buchholz relay, oil temperature indication, winding temperature indication, Silica Gel Breather, Conservator tank oil level indicators (MOG, Sight Glass), PRV and alarm & trip etc. i/c first filling of filtered dehydrated K class natural easter oil and confirming to IS: 16659:2017 and losses shall be as energy efficiency level 1 only with an impedance of 6.5 to 7% i/c as per specification attached complete in all respects as required at site. Design ambient to be considered as 50 Deg C. All the balance parameter like temp rise, Basic insulation level, flux density etc. shall be strictly in accordance with IS 2026 Part - 1 only. Provision of On-line Health Monitoring system with OTI, WTI, Voltage, Current, Percentage loading, Buchholz & PRV relay status with historical data saving as per specifications attached and as directed by Engineer-In-Charge. | 2.00 | Jobs |  | 5940000.00 | 11880000.00 | 4450000.00 | 8900000.00 | 4050000.00 | 8100000.00 | 3952000.00 | 7904000.00 | 7904000.00 | EVERCREST PROJECTS PVT LTD
3.00 | SITC of LT bus duct for 4000 amps. rating, indoor sandwiched type Busduct (fault level of 65 KA) [for connecting 2 nos. transformer secondary side to Incomers of NE#1 MV panel having suitable rated aluminium conductor for three phase and 100% neutral connections with necessary 90 dgree bends, adopter boxes with flanged end as per site requirement and necessary copper flexible (set of TPN) at terminating ends etc. as required, GI housing for heat dissipation in natural environment, complete with 2 nos. 50 x 6 mm Aluminium continuous earthing conductor and having necessary hanging arrangement, elbows, zig zag bridge for phase sequence matching, supports from the ceiling. The housing shall be powder coated etc. as required complete as per site requirement, as per specifications attached and as directed by Engineer-In-Charge. | 24.00 | Mtrs. |  | 60000.00 | 1440000.00 | 69978.00 | 1679472.00 | 40000.00 | 960000.00 | 31326.00 | 751824.00 | 751824.00 | EVERCREST PROJECTS PVT LTD
4.00 | SITC of LT bus duct for 1600 amps. Rating, indoor sandwiched type Bus duct (fault level of 65 KA) [for connecting 2 nos. DG sets outgoing into Incomers of Essential MV panel] having suitable rated aluminium conductor for three phase and 100% neutral connections with necessary 90 degree bends, adopter boxes with flanged end as per site requirement and necessary copper flexible (set of TPN) at terminating ends etc. as required, GI housing for heat dissipation in natural environment, complete with 2 nos. 50 x 6 mm Aluminium continuous earthing conductor and having necessary hanging arrangement, elbows, zig zag bridge for phase sequence matching, supports from the ceiling. The housing shall be powder coated etc. as required complete as per site requirement, as per specifications attached and as directed by Engineer-In-Charge. | 55.00 | Mtrs. |  | 30000.00 | 1650000.00 | 30399.00 | 1671945.00 | 18400.00 | 1012000.00 | 13431.00 | 738705.00 | 738705.00 | EVERCREST PROJECTS PVT LTD
5.00 | Design, fabrication (TTA assembly), Supply, Installation, testing & commissioning of both side extendable, floor mounted type, fully compartmentalized, front operated, back openable, LT cubicle panel suitable for incoming and outgoing power cables entry from bottom and top opening for communication cables, the switchboards shall be of Single front design as specified as per IEC61439-1 & 2 with Internal Arc Containment as per IEC 61641 for 50kA/0.3 s, suitable for Seismic Zone III /IV/ V as per IS 1893 part-1, Form of separation shall be of Form 4B as per IS/ IEC 61439-1&2 with Bus Bars rating of 4000A, 3phase with 100% Electrolytic grade Neutral Aluminium bus bar- 1 set, 2 Nos. Incomer and 1 No. Bus coupler - 4000 Amp 415V (Uimp=8KV), 65KA (Icu @415V=Ics=Icw for 1 sec) 4 Pole EDO (Electrically operated Draw-out) type microprocessor controlled Modular ACB with LSIG release (zone: O/L, S/C, Instantaneous & ground fault), 1 set for 3 nos. ACBs- Electrical interlocking so that only two ACBs can be made ON at a time, These ACB panels shall be single tier only. Outgoings: 2 Nos-2000 Amp; 4 Nos.-1600A; 4Nos.-800A 415V (Uimp=8KV), 65KA (Icu @415V=Ics=Icw for 1 sec) 4 Pole EDO (Electrically operated Draw-out) type microprocessor controlled Modular ACB with LSIG release (zone: O/L, S/C, Instantaneous & ground fault), 10 nos., 630 Amps. 65kA Fault current breaking capacity, 4 pole MCCB with microprocessor controlled with O/C, S/C & E/F protections, 4 nos., 200 Amps. 65kA Fault current breaking capacity, 4 pole MCCB with microprocessor controlled with O/C, S/C & E/F protections, Digital LED MFM with RS-485 for metering records and status of each MCCB to be shown on SCADA Platform, as per specifications attached and as directed by Engineer-In-Charge. 400X400mm separate, visible compartment on both side of the panel to accommodate SPDs backed with MCBs. | 1.00 | Job |  | 10500000.00 | 10500000.00 | 7482614.00 | 7482614.00 | 6000000.00 | 6000000.00 | 5873776.00 | 5873776.00 | 5873776.00 | EVERCREST PROJECTS PVT LTD
6.00 | Design, fabrication (TTA assembly), Supply, Installation, testing & commissioning of both side extendable, floor mounted type, fully compartmentalized, front operated, back openable, LT cubicle panel suitable for incoming and outgoing power cables entry from bottom and top opening for communication cables, the switchboards shall be of Single front design as specified as per IEC61439-1 & 2 with Internal Arc Containment as per IEC 61641 for 50kA/0.3 s, suitable for Seismic Zone III /IV/ V as per IS 1893 part-1, Form of separation shall be of Form 4B as per IS/ IEC 61439-1&2. Bus Bars: 1600A, 3phase with 100% Electrolytic grade Neutral Aluminium bus bar- 1 set. Incomers & Bus coupler: Electrical interlocking so that only two MCCBs can be made ON at a time, 3 nos.- 630 Amps. Outgoings: 2 nos- 200 Amps, 12 nos-100 Amps, 65kA Fault current breaking capacity, 4 pole MCCB with microprocessor controlled with O/C, S/C & E/F protections, CTs and LED indication for phases and OFF,ON & TRIP. Digital LED MFM with RS-485 for metering records and status of each MCCB to be shown on SCADA Platform. 400X400mm separate, visible compartment on both side of the panel to accommodate SPDs backed with MCBs. | 1.00 | Job |  | 2000000.00 | 2000000.00 | 1248945.00 | 1248945.00 | 1000000.00 | 1000000.00 | 1034092.00 | 1034092.00 | 1000000.00 | shiv electric
7.00 | Design, fabrication (TTA assembly), Supply, Installation, testing & commissioning of both side extendable, floor mounted type, fully compartmentalized, front operated, back openable, LT cubicle panel suitable for incoming and outgoing power cables entry from bottom and top opening for communication cables, the switchboards shall be of Single front design as specified as per IEC61439-1 & 2 with Internal Arc Containment as per IEC 61641 for 50kA/0.3 s, suitable for Seismic Zone III /IV/ V as per IS 1893 part-1, Form of separation shall be of Form 4B as per IS/ IEC 61439-1&2 with Bus Bar rating 1600A, 3phase with 100% Electrolytic grade Neutral Aluminium bus bar; Incomers & Bus coupler: 2 Nos Incomer and 1 No. Buscoupler - 1250 Amp 415V(Uimp=12KV), 65KA (Icu @415V=Ics=Icw for 1 sec) 4 Pole EDO (Electrically operated Draw-out) type microprocessor controlled Modular ACB with LSIG release (zone: O/L, S/C, Instantaneous & ground fault) ACB shall be capable of communicating data on Ethernet protocol and on-line parameterization capable. Outgoings: 8 nos.- 250 Amps; 6 nos.- 200 Amps & 12 nos.-100 Amps. 65kA Fault current breaking capacity, 4 pole MCCB with microprocessor controlled with O/C, S/C & E/F protections, CTs and LED indication for phases and OFF,ON & TRIP. Digital LED MFM with RS-485 for metering records and status of each MCCB to be shown on SCADA Platform, as per specifications attached and as directed by Engineer-In-Charge.400X400mm separate, visible compartment on both side of the panel to accommodate SPDs backed with MCBs. | 1.00 | Job |  | 4000000.00 | 4000000.00 | 2606460.00 | 2606460.00 | 2100000.00 | 2100000.00 | 2146676.00 | 2146676.00 | 2100000.00 | shiv electric
8.00 | Design, Supply, Installation, Testing and Commissioning of Surge Protection Devices (Spark Gap based single pole modular Type 1+2 combined arrester with integrated back-up fuse for 230/400 VAC (L-N) applications having maximum short circuit current (RMS) of 100 KA) for each LT panels (2 Nos. for each of the three LT panels) and Spark Gap based single pole modular combined arrester for 230/400 VAC (N-PE) applications as per IEC 61643 as amended upto date as per specifications attached and as directed by Engineer-In-Charge. | 1.00 | Job |  | 580000.00 | 580000.00 | 73800.00 | 73800.00 | 300000.00 | 300000.00 | 56750.00 | 56750.00 | 56750.00 | EVERCREST PROJECTS PVT LTD
9.00 | Supply, installation, testing & commissioning of single phase automatic Float cum boost (30 Amps) battery charger with dropper diode bank suitable for charging SMF VRLA 110V, 120 AH maintenance free battery consisting of 55 cells i/c supply of SMF (Sealed maintenance free) batteries, necessary battery stand and making all connections etc. complete as per specifications attached and as directed by Engineer-In-Charge. | 1.00 | Job |  | 700000.00 | 700000.00 | 537675.00 | 537675.00 | 400000.00 | 400000.00 | 401900.00 | 401900.00 | 400000.00 | shiv electric
10.00 | Supplying and fixing 12 way prewired SPN MCB distribution board of steel sheet for 240 volts on surface / recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. (with MCB) as per specifications attached and as directed by Engineer-In-Charge. | 1.00 | No |  | 8000.00 | 8000.00 | 6280.00 | 6280.00 | 7000.00 | 7000.00 | 4587.00 | 4587.00 | 4587.00 | EVERCREST PROJECTS PVT LTD
11.00 | Design, fabrication, assembly, wiring, supply, erection, testing and commissioning of IGBT based Hybrid Solution of 400 kVAR capacity at NE#1 Panel to achieve >0.95 Lag and TDDI/THDV values within IEEE recommended limits. The system shall be of design as per IS 16636 with degree of protection of enclosures system shall be IP42 in accordance with IEC 60529. The active compensation system should filter harmonics from 2nd to 51st individual harmonic order as well as feature to improve PF correction. Output voltage- 415V, Incomer shall be of 800A MCCB, Auto/Manual operation selection for each capacitor bank, Capacitors shall be as per MPP low loss as per standards with suitable Capacitor Duty Contactor (Utilization Category AC-6b) De-tuned reactor- 14% Copper wound The system should be with compatible with Grid Power OR D.G. Power Supply, as per specifications attached and as directed by Engineer-In-Charge. | 1.00 | Nos. |  | 2600000.00 | 2600000.00 | 1472200.00 | 1472200.00 | 1200000.00 | 1200000.00 | 1207820.00 | 1207820.00 | 1200000.00 | shiv electric
12.00 | DG SET: 2 Nos. Providing, installation, testing and commissioning of silent type Diesel Generator set along with having prime power rating of 750 KVA, 415 volts at 1500 RPM, 0.8 lagging power factor at 415 V suitable for 50 Hz, 3 Phase system & for 0.85 load factor and consisting of a) Diesel Engine: 4 stroke, water cooled, electric start, suitable capacity alternator of 750KVA nominal output at 80% efficiency and 0.9 (lag.) p.f at 45°C, 50% RH & at 1000 meter MSL site condition and conforming to BS 5514, BS 649, IS 10000, capable of taking 10% over loading for one hour after 12 hours of continuous operation. b) Engine mounted microprocessor based instrument panel fitted with and having digital display c) Alternator: Suitable capacity alternator of 750KVA nominal output at 80% efficiency and 0.9 (lag.) p.f , 415 volts at 1500 RPM, 3 phase 50 Hz AC supply with 0.8 lagging power factor at 45°C, 50 % RH & at 1000 Meter MSL. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self-regulated through AVR conforming to IS: 4722 / BS 2613 suitable for tropical conditions and with class - H insulation. d) Starting System: Suitably rated 24V DC starting/ cranking system comprising of starter motors: voltage regulator and arrangement for initial excitation complete with 2 x 12 volt batteries (12 Volt, suitable capacity SMF battery to deliver required cranking ampere) as required and specified by OEM. with Suitable acoustic and weather proof duly painted/ powder coated enclosure with arrangement for fresh air intake for cooling of the engine & alternator, excitation discharging hot air into the atmosphere as per OEM & complying with CPCB norms conforming to upto date amendments as per specifications attached and as directed by Engineer-In-Charge. e) Base Frame & Foundation: Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on suitable cement concrete foundation. Vibration isolation arrangement shall be made as per recommendations of manufacturer.e) Fueling system: Design, manning/ fabrication followed by errection, installation and commissioning of suitable storage type fuelling system (15KL UG fuel tank alongwith Pumps, piping, auto operation panel with level controller along with day tank (990L), necessary NOC from competent authority and suitable explosive license as applicable.f) Exhaust System: Dry exhaust mainfold with hospital exhaust silencer and catalytic convertor with supporting structures in compliance with CPCB guidelines. as per specifications attached and as directed by Engineer-In-Charge. | 2.00 | Jobs |  | 9000000.00 | 18000000.00 | 5212500.00 | 10425000.00 | 6000000.00 | 12000000.00 | 4775341.00 | 9550682.00 | 9550682.00 | EVERCREST PROJECTS PVT LTD
13.00 | Design, Fabrication, Supply, Installation, Testing & Commissioning of cubicle type AMF panel (consisting of SCADA compatible ATS with in-built onload bypass arrangement and 2 nos. ACBs as incomer) for 1 x 750 kVA above DG set in single mode of operation, suitable for 415 V, 3 phase, 4 wire, 50 Hz, AC supply system fabricated in compartmentalized, extendable design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shades having suitable capacity extensible type TPN aluminium alloy bus bars of high conductivity, DMC/SMC bus bar supports, with short circuit withstand capacity of min 31 MVA for 1 Sec. , Incomer 1 (for input from non-essential panel): 1600 Amps 65 kA - 1 no, Four pole horizontal electrical draw out type, microprocessor release, Air Circuit Breaker of above fault breaking capacity (Ics=Icu> 65kA) manually and electrically operated, fitted with interlocked door, automatic safety shutters, mechanical ON/OFF and service/test/isolated position indicators and frame earthing contact conforming to IS 13947-2 : 1993 as amended up-to-date complete with following accessories for ACB, Incoming from non-Essential panel: suitable arrangements to be made for provision of incoming 2R cable and controlling arrangements/ Control wiring with SCADA communication compatible with non-essential panel as required for operation. Incomer 2 (for input from DG): 1600 Amp 65 kA - 1 no, Four pole horizintal electrical drawout type, microprocessor release Air Circuit Braker of above fault breaking capacity (Ics=Icu=Icw upto 433 V) manually/electrically operated, fitted with interlocked door, automatic safety shutters, mechanical ON/OFF and service/test/isolated position indicators and frame earthing contact conforming to IS 13947-2 : 1993 as amended up-to-date complete with following accessories ACB (1 no for outgoing). Suitable provision in panels should be made for connection of Bus trunking at outgoing connections to non-essential panel and electrical as well as mechanical interlocking of both the outgoings, as per specifications attached and as directed by Engineer-In-Charge. | 2.00 | Jobs |  | 8500000.00 | 17000000.00 | 1584250.00 | 3168500.00 | 4600000.00 | 9200000.00 | 5119170.00 | 10238340.00 | 3168500.00 | Konstelec Engineers Pvt. Ltd.
14.00 | Supply of following size HT Cable composed of Circular Aluminium Stranded conductor, conductor screening by extruded semiconducting compound, XLPE insulated, insulation screened with extruded semiconducting compound followed by copper tape, followed by coloured strip R, Y, B for core identifications, lapped together with suitable filler in the interstices, thermoplastic tape, inner sheath of PVC Type 'ST2', Galvanised flat strip armoured and overall PVC type 'ST2' outer sheathed cable confirming to IS 7098 (Part II)-2011 amended upto date. a) 3 core 300 sq.mm 11 KVI grade | 6400.00 | Mtrs. |  | 2000.00 | 12800000.00 | 1370.00 | 8768000.00 | 1865.00 | 11936000.00 | 1505.00 | 9632000.00 | 8768000.00 | Konstelec Engineers Pvt. Ltd.
15.00 | Supply of following size LT Cable composed of Stranded compact sector shaped Aluminium conductor, colour coded, cores laid up, Thermoplastic Tape inner sheathed, XLPE insulated, FRLS, Galvanised flat steel strip armoured and overall PVC type ‘ST2’ outer sheathed cable confirming to IS:7098 (Part I)-1988 amended upto date. a) 3.5 core 400 sq.mm 1.1KV grade | 1000.00 | Mtrs. |  | 2200.00 | 2200000.00 | 1573.00 | 1573000.00 | 1961.00 | 1961000.00 | 1548.00 | 1548000.00 | 1548000.00 | EVERCREST PROJECTS PVT LTD
16.00 | Supply of following size LT Cable composed of Stranded compact sector shaped Aluminium conductor, colour coded, cores laid up, Thermoplastic Tape inner sheathed, XLPE insulated, FRLS, Galvanised flat steel strip armoured and overall PVC type ‘ST2’ outer sheathed cable confirming to IS:7098 (Part I)-1988 amended upto date. b) 3.5 core 300 sq.mm 1.1KV grade | 1550.00 | Mtrs. |  | 1750.00 | 2712500.00 | 1223.00 | 1895650.00 | 1604.00 | 2486200.00 | 1220.00 | 1891000.00 | 1891000.00 | EVERCREST PROJECTS PVT LTD
17.00 | Supply of following size LT Cable composed of Stranded compact sector shaped Aluminium conductor, colour coded, cores laid up, Thermoplastic Tape inner sheathed, XLPE insulated, FRLS, Galvanised flat steel strip armoured and overall PVC type ‘ST2’ outer sheathed cable confirming to IS:7098 (Part I)-1988 amended upto date. c) 3.5 core 120 sq.mm 1.1KV grade | 3480.00 | Mtrs. |  | 760.00 | 2644800.00 | 536.00 | 1865280.00 | 703.00 | 2446440.00 | 544.00 | 1893120.00 | 1865280.00 | Konstelec Engineers Pvt. Ltd.
18.00 | Supply of 12 core 2.5 sq.mm 1.1KV grade PVC insulated Copper conductor cable confirming to IS 8130 amended upto date. | 50.00 | Mtrs. |  | 490.00 | 24500.00 | 410.00 | 20500.00 | 500.00 | 25000.00 | 359.00 | 17950.00 | 17950.00 | EVERCREST PROJECTS PVT LTD
19.00 | Supply of permanently lubricated HDPE pipe of nominal 160 mm outer dia conforming to specifications attached and as directed by Engineer-in - Charge. | 6250.00 | Mtrs. |  | 2200.00 | 13750000.00 | 525.00 | 3281250.00 | 1150.00 | 7187500.00 | 762.00 | 4762500.00 | 3281250.00 | Konstelec Engineers Pvt. Ltd.
20.00 | Laying of following size of permanently lubricated HDPE (High Density Polyethylene) pipe alongwith its necessary accessories like coupler, end plugs etc. below the ground (i/c. Road crossing, Cement concrete Apron Area) at a depth of 1.6 m to 6 m through horizontal directional drilling as per site as required (size upto 160 mm). | 6250.00 | Mtrs. |  | 1200.00 | 7500000.00 | 200.00 | 1250000.00 | 600.00 | 3750000.00 | 660.00 | 4125000.00 | 1250000.00 | Konstelec Engineers Pvt. Ltd.
21.00 | Supplying and installing following size of Hot dip Galvanised / Powder coated ladder type cable trays in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc. as required. (a) 600 mm. wide X 50 mm. wall height GI Ladder type. | 128.00 | Mtrs. |  | 1000.00 | 128000.00 | 1618.00 | 207104.00 | 1200.00 | 153600.00 | 618.00 | 79104.00 | 79104.00 | EVERCREST PROJECTS PVT LTD
22.00 | Supplying and installing following size of Hot dip Galvanised / Powder coated ladder type cable trays in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc. as required. (b) 450 mm. wide X 50 mm. wall height GI Ladder type. | 125.00 | Mtrs. |  | 900.00 | 112500.00 | 1410.00 | 176250.00 | 1075.00 | 134375.00 | 541.00 | 67625.00 | 67625.00 | EVERCREST PROJECTS PVT LTD
23.00 | Supplying and installing following size of Hot dip Galvanised / Powder coated ladder type cable trays in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc. as required. (c) 150 mm. wide X 50 mm. wall height GI perforated type. | 75.00 | Mtrs. |  | 650.00 | 48750.00 | 1150.00 | 86250.00 | 660.00 | 49500.00 | 461.00 | 34575.00 | 34575.00 | EVERCREST PROJECTS PVT LTD
24.00 | Laying of one no. 11 KV grade XLPE cable of size above 120 sq.mm. but not exceeding 300 sq.mm. as follows:- (a) In in the existing in the existing masonry open duct | 80.00 | Mtrs. |  | 130.00 | 10400.00 | 75.00 | 6000.00 | 100.00 | 8000.00 | 80.00 | 6400.00 | 6000.00 | Konstelec Engineers Pvt. Ltd.
25.00 | Laying of one no. 11 KV grade XLPE cable of size above 120 sq.mm. but not exceeding 300 sq.mm. as follows:- (b) In existing RCC/HUME/ METAL/HDPE pipe | 6300.00 | Mtrs. |  | 130.00 | 819000.00 | 75.00 | 472500.00 | 100.00 | 630000.00 | 80.00 | 504000.00 | 472500.00 | Konstelec Engineers Pvt. Ltd.
26.00 | Laying of one no. 11 KV grade XLPE cable of size above 120 sq.mm. but not exceeding 300 sq.mm. as follows:- (c ) In soil by excavation of soil, providing sand cushioning, protective covering including refilling etc. as reqd. | 20.00 | Mtrs. |  | 520.00 | 10400.00 | 200.00 | 4000.00 | 250.00 | 5000.00 | 450.00 | 9000.00 | 4000.00 | Konstelec Engineers Pvt. Ltd.
27.00 | Laying and fixing of 1.1 KV grade XLPE cable of size 120 sq.mm. as follows. (a) In existing cable tray/ open duct | 500.00 | Mtrs. |  | 90.00 | 45000.00 | 45.00 | 22500.00 | 100.00 | 50000.00 | 60.00 | 30000.00 | 22500.00 | Konstelec Engineers Pvt. Ltd.
28.00 | Laying and fixing of 1.1 KV grade XLPE cable of size 120 sq.mm. as follows. (b) In existing GI pipe/Hume/ RCC | 50.00 | Mtrs. |  | 90.00 | 4500.00 | 40.00 | 2000.00 | 100.00 | 5000.00 | 60.00 | 3000.00 | 2000.00 | Konstelec Engineers Pvt. Ltd.
29.00 | Laying and fixing of 1.1 KV grade XLPE cable of size 120 sq.mm. as follows. (c )In soil by excavation of soil, providing sand cushioning, protective covering including refilling etc. as reqd. | 960.00 | Mtrs. |  | 450.00 | 432000.00 | 85.00 | 81600.00 | 250.00 | 240000.00 | 350.00 | 336000.00 | 81600.00 | Konstelec Engineers Pvt. Ltd.
30.00 | Laying and fixing of 1.1 KV grade XLPE cable of size above 120 sq.mm. but not exceeding 400 sq.mm. as follows. (a) In existing cable tray/ open duct. | 1200.00 | Mtrs. |  | 120.00 | 144000.00 | 75.00 | 90000.00 | 100.00 | 120000.00 | 70.00 | 84000.00 | 84000.00 | EVERCREST PROJECTS PVT LTD
31.00 | Laying and fixing of 1.1 KV grade XLPE cable of size above 120 sq.mm. but not exceeding 400 sq.mm. as follows. (b) In existing GI pipe/Hume pipe/ RCC | 50.00 | Mtrs. |  | 120.00 | 6000.00 | 75.00 | 3750.00 | 100.00 | 5000.00 | 70.00 | 3500.00 | 3500.00 | EVERCREST PROJECTS PVT LTD
32.00 | Laying and fixing of 1.1 KV grade XLPE cable of size above 120 sq.mm. but not exceeding 400 sq.mm. as follows. (c ) In soil by excavation of soil, providing sand cushioning, protective covering including refilling etc. as reqd. | 400.00 | Mtrs. |  | 450.00 | 180000.00 | 150.00 | 60000.00 | 250.00 | 100000.00 | 450.00 | 180000.00 | 60000.00 | Konstelec Engineers Pvt. Ltd.
33.00 | Supply & making straight through joint with heat shrinkable jointing kit i/c. all jointing materials, clamps, ferrules etc. as reqd. for 11 KV (E) grade 3 core 300 sq.mm XLPE insulated AI. Cond. cable. | 30.00 | Nos. |  | 13000.00 | 390000.00 | 22437.00 | 673110.00 | 7000.00 | 210000.00 | 11620.00 | 348600.00 | 210000.00 | shiv electric
34.00 | Supply & making indoor end termination with heat shrinkable joining kit i/c. all necessary joining materials, clamps, sockets etc. for 11 KV (E) grade XLPE insulated AI. Cond. Cable of following sizes: (a) 11 KV (E) grade XLPE insulated 3 core 300 sq.mm. AL Cond. Cable etc. as reqd. | 5.00 | Nos. |  | 7000.00 | 35000.00 | 9645.00 | 48225.00 | 5000.00 | 25000.00 | 5790.00 | 28950.00 | 25000.00 | shiv electric
35.00 | Supply & making end termination with brass compression gland i/c. proper socketing etc. reqd. for 1.1 KV grade XLPE insulated 3.5 core 400 sq.mm. AI. Cond. Cable. | 20.00 | Nos. |  | 4500.00 | 90000.00 | 1524.00 | 30480.00 | 1600.00 | 32000.00 | 1550.00 | 31000.00 | 30480.00 | Konstelec Engineers Pvt. Ltd.
36.00 | Supply & making end termination with brass compression gland i/c. proper socketing etc. reqd. for 1.1 KV grade XLPE insulated 3.5 core 300 sq.mm. AI. Cond. Cable. | 15.00 | Nos. |  | 4000.00 | 60000.00 | 1445.00 | 21675.00 | 1500.00 | 22500.00 | 1200.00 | 18000.00 | 18000.00 | EVERCREST PROJECTS PVT LTD
37.00 | Supply & making end termination with brass compression gland i/c. proper socketing etc. reqd. for 1.1 KV grade XLPE insulated 3.5 core 120 sq.mm. AI. Cond. Cable. | 20.00 | Nos. |  | 2500.00 | 50000.00 | 1193.00 | 23860.00 | 1000.00 | 20000.00 | 672.00 | 13440.00 | 13440.00 | EVERCREST PROJECTS PVT LTD
38.00 | Earthing with Cu. Earth plate 600 mm. X 600 mm. X 3 mm. thick i/c. all accessories, providing masonary enclosure on top cover plate having locking arrangement and watering pipe etc. reqd. | 18.00 | Jobs |  | 20000.00 | 360000.00 | 16975.00 | 305550.00 | 14000.00 | 252000.00 | 27849.00 | 501282.00 | 252000.00 | shiv electric
39.00 | Providing & fixing 50 mm. X 5 mm. Cu. Strip in 80 mm. dia. GI (Class - B) pipe from earth electrode etc. as reqd. | 200.00 | Mtrs. |  | 2370.00 | 474000.00 | 1955.00 | 391000.00 | 2800.00 | 560000.00 | 2977.00 | 595400.00 | 391000.00 | Konstelec Engineers Pvt. Ltd.
40.00 | Earthing with GI earth plate 600 X 600 X 6 mm. thick i/c. all accessories providing masonary enclosure on top, cover plate, having locking arrangement, watering pipe etc. as reqd. | 10.00 | Jobs |  | 12000.00 | 120000.00 | 13325.00 | 133250.00 | 7000.00 | 70000.00 | 5852.00 | 58520.00 | 58520.00 | EVERCREST PROJECTS PVT LTD
41.00 | Providing & fixing 25 mm. X 5 mm. thick GI strip in 40 mm. dia. (Class - B) pipe from earth electrode etc. as reqd. | 50.00 | Mtrs. |  | 600.00 | 30000.00 | 179.00 | 8950.00 | 500.00 | 25000.00 | 572.00 | 28600.00 | 8950.00 | Konstelec Engineers Pvt. Ltd.
42.00 | Providing & fixing 25 X 5 mm. thick GI strip on surface or in recess for connection etc. as reqd. | 50.00 | Mtrs. |  | 150.00 | 7500.00 | 119.00 | 5950.00 | 200.00 | 10000.00 | 145.00 | 7250.00 | 5950.00 | Konstelec Engineers Pvt. Ltd.
43.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 meter below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm). | 50.00 | Mtrs. |  | 1200.00 | 60000.00 | 1010.00 | 50500.00 | 1400.00 | 70000.00 | 150.00 | 7500.00 | 7500.00 | EVERCREST PROJECTS PVT LTD
44.00 | Supply and laying of 6" dia. (at least), Class-B, GI pipe for road /drain crossing at a suitable depth for crossing HT & LT UG cable i/c. necessary excavation for laying of pipe, refilling and making good the damages etc. as reqd. | 150.00 | Mtrs. |  | 2500.00 | 375000.00 | 1513.00 | 226950.00 | 1951.00 | 292650.00 | 2161.00 | 324150.00 | 226950.00 | Konstelec Engineers Pvt. Ltd.
45.00 | Providing and making masonary inspection chember of size not less than 1000 X 1000 X 1200 mm. deep (inside) i/c. excavation of soil, 75 mm. flat brick soiling at the bottom 50 mm. base concrete over brick soiling, 250 mm. brick work with cement morter, cement plasteron brick work bottom (only inside surface), providing removable RCC slabs of suitable size on the top of the chember with providing suitable lifting arrangement etc. complete as reqd. | 20.00 | Nos. |  | 15000.00 | 300000.00 | 5500.00 | 110000.00 | 9500.00 | 190000.00 | 19303.00 | 386060.00 | 110000.00 | Konstelec Engineers Pvt. Ltd.
46.00 | Suitable Trolley for maintenance of following type of breakers with adjustable hights, pulley arrangement, locking system and 360 degree rotating wheels. (a) 11kV VCBs | 2.00 | Nos. |  | 70000.00 | 140000.00 | 68250.00 | 136500.00 | 65000.00 | 130000.00 | 65000.00 | 130000.00 | 130000.00 | shiv electric, EVERCREST PROJECTS PVT LTD
47.00 | Suitable Trolly for maintenance of following type of breakers with adjustable hights, pulley arrangement, locking system and 360 degree rotating wheels. (b) 415V ACBs | 2.00 | Nos. |  | 50000.00 | 100000.00 | 57750.00 | 115500.00 | 40000.00 | 80000.00 | 45000.00 | 90000.00 | 80000.00 | shiv electric
48.00 | Installation, Testing and commissioning of Conventional Lightning Protection System as per IS/IEC 62305-3 Standard (LPL-1) with supply of Air Termination Rod, Clamps to Hold Air Termination Rod, Roof Conductor & Roof Conductor Holder, Clamps & Holder, Down Conductor & Down Conductor Holder, Earthing Materials etc. as per specifications attached and as directed by Engineer-In-Charge. | 1.00 | Job |  | 900000.00 | 900000.00 | 10000.00 | 10000.00 | 15000.00 | 15000.00 | 22000.00 | 22000.00 | 10000.00 | Konstelec Engineers Pvt. Ltd.
49.00 | Sub Head B: Ancillary Services: Fire detection and Alarm system Supply installation testing and commissioning of UL Listed and FM approved 2 Loop, networkable type, Analog addressable Fire Alarm system, having the total panel capacity of 252 devices. The panel shall be able to give location of all fire and Fire / fault and Isolation conditions of addressable units via the address codes. The panel shall have the capacity of storing up to 2000 events. Further, the panel must be able to automatically switch ON /OFF respective control module whenever any alarm is triggered. The panel should have inbuilt common Alarm, Fault and monitored sounder output. The panel shall have VGA monochrome LCD display and having maximum 320 (8 x 40) Characters in the display with 24 Zones LED indicators. The panel shall have a built in power supply and battery charger. Battery charger shall be able to charge the system batteries of up to 33AH capacity with 2 no’s 7AH battery as per specifications attached and as directed by Engineer-In-Charge. | 1.00 | Nos. |  | 370000.00 | 370000.00 | 812500.00 | 812500.00 | 220000.00 | 220000.00 | 249500.00 | 249500.00 | 220000.00 | shiv electric
50.00 | Supply installation testing and commissioning of UL Listed & FM approved System Status Display. The panel shall be able to give location of all fire and fault and Isolation conditions of addressable units of main Fire Alarm panel via the address codes. The panel shall have a LCD display and having maximum 160 (4 x 40) Characters in the display. | 1.00 | No. |  | 90500.00 | 90500.00 | 330000.00 | 330000.00 | 75000.00 | 75000.00 | 68900.00 | 68900.00 | 68900.00 | EVERCREST PROJECTS PVT LTD
51.00 | Supply installation testing and commissioning of UL listed and FM approved intelligent Addressable microprocessor based, photoelectric smoke & heat type multi criteria with base. | 60.00 | Nos. |  | 3500.00 | 210000.00 | 7930.00 | 475800.00 | 3200.00 | 192000.00 | 2580.00 | 154800.00 | 154800.00 | EVERCREST PROJECTS PVT LTD
52.00 | Supply installation testing and commissioning of UL listed & FM approved Intelligent Addressable microprocessor based, rate of rise and fixed temperature Heat detector with Standard base. | 4.00 | Nos. |  | 3500.00 | 14000.00 | 5515.00 | 22060.00 | 3068.00 | 12272.00 | 2394.00 | 9576.00 | 9576.00 | EVERCREST PROJECTS PVT LTD
53.00 | Supply ,installation, testing and commissioning of Manual Call Point with module [of same protocol of FDA Panel] as per site requirement. | 3.00 | Nos. |  | 3400.00 | 10200.00 | 8035.00 | 24105.00 | 2900.00 | 8700.00 | 2388.00 | 7164.00 | 7164.00 | EVERCREST PROJECTS PVT LTD
54.00 | Supply installation testing and commissioning of Electronics Hooter with module [of same protocol of FDA Panel] as per site requirement | 3.00 | Nos. |  | 4800.00 | 14400.00 | 8875.00 | 26625.00 | 4600.00 | 13800.00 | 4600.00 | 13800.00 | 13800.00 | shiv electric, EVERCREST PROJECTS PVT LTD
55.00 | Supply installation testing and commissioning of UL listed & FM approved Line Isolator for isolating the section of circuit in case of short in the addressable Loop wiring. | 4.00 | Nos. |  | 3400.00 | 13600.00 | 7825.00 | 31300.00 | 1415.00 | 5660.00 | 2500.00 | 10000.00 | 5660.00 | shiv electric
56.00 | Supply installation testing and commissioning of UL listed & FM approved Intelligent addressable output module with SPDT contacts having facility to Active sounders, AHU Trippings etc. with the contact rating of 30VDC @ 4 Amp and additionally single lnput for monitoring purpose. | 8.00 | Nos. |  | 4100.00 | 32800.00 | 10450.00 | 83600.00 | 3200.00 | 25600.00 | 2850.00 | 22800.00 | 22800.00 | EVERCREST PROJECTS PVT LTD
57.00 | Supply installation testing and commissioning of 24 V DC SMPS Power Supply. | 1.00 | Nos. |  | 5500.00 | 5500.00 | 3125.00 | 3125.00 | 2600.00 | 2600.00 | 1000.00 | 1000.00 | 1000.00 | EVERCREST PROJECTS PVT LTD
58.00 | Supply installation of Detector Mounting 4" x 4" MS Junction Box with Backlight Cover. | 76.00 | Nos. |  | 400.00 | 30400.00 | 625.00 | 47500.00 | 110.00 | 8360.00 | 230.00 | 17480.00 | 8360.00 | shiv electric
59.00 | Supply installation of Cable Terminal Junction box as per requirement. | 1.00 | Nos. |  | 1300.00 | 1300.00 | 3125.00 | 3125.00 | 890.00 | 890.00 | 230.00 | 230.00 | 230.00 | EVERCREST PROJECTS PVT LTD
60.00 | Supply and laying of 2 core x 1.5 sq. mm copper FRLS Armoured cable with necessary fittings etc. | 600.00 | Mtrs. |  | 170.00 | 102000.00 | 79.00 | 47400.00 | 150.00 | 90000.00 | 168.00 | 100800.00 | 47400.00 | Konstelec Engineers Pvt. Ltd.
61.00 | Supply and laying of 4 core x 1.5 sq. mm copper FRLS Armoured cable with necessary fittings etc. | 50.00 | Mtrs. |  | 210.00 | 10500.00 | 124.00 | 6200.00 | 250.00 | 12500.00 | 249.00 | 12450.00 | 6200.00 | Konstelec Engineers Pvt. Ltd.
62.00 | Supply and laying 25 MM Medium Grade G.I Conduit with fittings FOR SURFACE AREA. | 25.00 | Mtrs. |  | 190.00 | 4750.00 | 161.00 | 4025.00 | 190.00 | 4750.00 | 240.00 | 6000.00 | 4025.00 | Konstelec Engineers Pvt. Ltd.
63.00 | Supply installation of 50MM G.I. Cable Tray alongwith fitting accessories. | 30.00 | Mtrs. |  | 500.00 | 15000.00 | 733.00 | 21990.00 | 295.00 | 8850.00 | 385.00 | 11550.00 | 8850.00 | shiv electric
64.00 | Supply installation testing and commissioning of Fire Extinguishers Supply of CO2 type Fire Extinguisher duly IS: 15683 & 2878 marked of following capacity made out of new high pressure seamless steel cylinder duly IS: 7285 marked, fitted with wheel type valve duly IS: 3224 marked internal discharge tube, discharge hose, fully charged with liquified CO2 gas complete as required in site. (a) 4.5 Kg with Wall hanging Arrangement | 3.00 | Nos. |  | 8000.00 | 24000.00 | 5975.00 | 17925.00 | 7000.00 | 21000.00 | 4500.00 | 13500.00 | 13500.00 | EVERCREST PROJECTS PVT LTD
65.00 | Supply of CO2 type Fire Extinguisher duly IS: 15683 & 2878 marked of following capacity made out of new high pressure seamless steel cylinder duly IS: 7285 marked, fitted with wheel type valve duly IS: 3224 marked internal discharge tube, discharge hose, fully charged with liquified CO2 gas complete as required in site. (b) 6.5 Kg with Trolley Arrangement | 2.00 | Nos. |  | 11500.00 | 23000.00 | 7025.00 | 14050.00 | 9500.00 | 19000.00 | 6800.00 | 13600.00 | 13600.00 | EVERCREST PROJECTS PVT LTD
66.00 | Supply of CO2 type Fire Extinguisher duly IS: 15683 & 2878 marked of following capacity made out of new high pressure seamless steel cylinder duly IS: 7285 marked, fitted with wheel type valve duly IS: 3224 marked internal discharge tube, discharge hose, fully charged with liquefied CO2 gas complete as required in site. (c ) 9 Kg with Trolley Arrangement | 9.00 | Nos. |  | 13500.00 | 121500.00 | 9125.00 | 82125.00 | 13000.00 | 117000.00 | 8300.00 | 74700.00 | 74700.00 | EVERCREST PROJECTS PVT LTD
67.00 | Supply of CO2 MS Fire bucket of standard 9 Ltr. Capacity ( painted Red outside & written FIRE in Black) alongwith hanging MS Stand as per site requirement. | 20.00 | Nos. |  | 4800.00 | 96000.00 | 3875.00 | 77500.00 | 300.00 | 6000.00 | 1650.00 | 33000.00 | 6000.00 | shiv electric
68.00 | Supply of Mechanical Foam type Fire Extinguisher following capacity duly IS: 15683 marked with Fire rating: 2A & 21B, Squeeze grip type valve, PVC Hose with metallic Nozzle & initial refill consisting of 120 gms. CO2 gas Cartridge duly IS: 4947 marked and AFFF Compound duly IS: 4989 Part-II complete as required in site. (a) 9 Ltr. capacity with Wall hanging Arrangement | 3.00 | Nos. |  | 4300.00 | 12900.00 | 2300.00 | 6900.00 | 2600.00 | 7800.00 | 2600.00 | 7800.00 | 6900.00 | Konstelec Engineers Pvt. Ltd.
69.00 | Supply of Dry Chemical Powder type Fire Extinguisher following capacity duly IS: 15683 marked with Fire rating: 21B, Squeeze grip type valve, PVC Hose with metallic Nozzle & initial refill consisting of 120 gms. CO2 gas Cartridge duly IS: 4947 marked and Dry Powder duly IS: 4308 marked complete as required in site. (a) 6 Kg. capacity with Wall hanging Arrangement | 5.00 | Nos. |  | 6700.00 | 33500.00 | 3350.00 | 16750.00 | 2200.00 | 11000.00 | 2600.00 | 13000.00 | 11000.00 | shiv electric
70.00 | Supply and Fixing of "ABC Powder Type Fire Extinguishers" shall confirm IS : 15683 & IS : 14609 with initial fill & all mounting accessories etc. complete. (a) 4.5 Kg with Wall hanging Arrangement | 5.00 | Nos. |  | 3000.00 | 15000.00 | 3350.00 | 16750.00 | 1770.00 | 8850.00 | 1635.00 | 8175.00 | 8175.00 | EVERCREST PROJECTS PVT LTD
71.00 | SITC of highly energy efficient, five star rating as per BEE Table3, hi-wall mounted split air-conditioner of following nominal capacity with inverter rotary compressor fully copper heat exchanger with hydrophylic aluminium finsand heavy duty suitable condenser fan along with necessary copper refrigerant piping upto 5 mtrs. with green refrigent and water drain piping upto 3 mtrs. as required, as mentioned below and the technical specifications attached and as directed by Engineer-In-Charge.: (a) 1.5 TR nominal capacity, 45000 Kcal. | 5.00 | job |  | 60000.00 | 300000.00 | 73000.00 | 365000.00 | 42000.00 | 210000.00 | 40760.00 | 203800.00 | 203800.00 | EVERCREST PROJECTS PVT LTD
72.00 | SITC of highly energy efficient, five star rating as per BEE Table3, hi-wall mounted split air-conditioner of following nominal capacity with inverter rotary compressor fully copper heat exchanger with hydrophylic aluminium finsand heavy duty suitable condenser fan along with necessary copper refrigerant piping upto 5 mtrs. with green refrigent and water drain piping upto 3 mtrs. as required, as mentioned below and the technical specifications attached and as directed by Engineer-In-Charge.: (b) 2 TR nominal capacity, 60,000 Kcal. | 6.00 | job |  | 67000.00 | 402000.00 | 88750.00 | 532500.00 | 60000.00 | 360000.00 | 51494.00 | 308964.00 | 308964.00 | EVERCREST PROJECTS PVT LTD
73.00 | Supply, Installation, Testing and commissioning of RO + UV based 80Ltr. Storage, Indoor fully integrated stainless steel body Water cooler cum purifier and Iron Remover (10” Ironil) with Cooling capacity – 60 Ltrs /hrs. and RO Water Flow Rate – 50 Ltr./hrs. as per specifications attached and as directed by Engineer-In-Charge. | 2.00 | job |  | 83000.00 | 166000.00 | 54500.00 | 109000.00 | 90000.00 | 180000.00 | 65907.00 | 131814.00 | 109000.00 | Konstelec Engineers Pvt. Ltd.
74.00 | PPE: Supply of Rubber hand gloves suitable for 11 kV rated switchgears (1 set shall be comprise of two nos.) | 4.00 | sets |  | 1000.00 | 4000.00 | 1050.00 | 4200.00 | 500.00 | 2000.00 | 450.00 | 1800.00 | 1800.00 | EVERCREST PROJECTS PVT LTD
75.00 | Supply and fixing of pastable, antiskid, fire retardant, alkali and acid resistant nominal 2 mm +/- 10% thick, ISI marked Elastomeric Insulation Sheet of 3.3 KV, 50 Hz grade and conforming to IS 15652 : 2006; including all sundry materials e.g. adhesive, cutting, filling, cleaning, chipping, minor civil work etc. complete as required. | 90.00 | sq.m. |  | 1500.00 | 135000.00 | 1040.00 | 93600.00 | 900.00 | 81000.00 | 625.00 | 56250.00 | 56250.00 | EVERCREST PROJECTS PVT LTD
76.00 | Supply and fixing of pastable, antiskid, fire retardant, alkali and acid resistant nominal 2.5 mm +/- 10% thick, ISI marked Elastomeric Insulation sheet of 11 KV, grade and conforming to IS 15652 : 2006, including all sundry materials e.g. adhesive, resin and cutting, filling, cleaning, chipping, minor civil work etc. complete as required. | 30.00 | sq.m. |  | 1800.00 | 54000.00 | 1250.00 | 37500.00 | 1000.00 | 30000.00 | 775.00 | 23250.00 | 23250.00 | EVERCREST PROJECTS PVT LTD
77.00 | Supply & fixing of glass framed shock treatment chart (A2 size) both in Hindi & English for treating person suffering due to electric shock mounted on wall hooks. | 4.00 | Sets |  | 1000.00 | 4000.00 | 1150.00 | 4600.00 | 500.00 | 2000.00 | 1050.00 | 4200.00 | 2000.00 | shiv electric
78.00 | Providing and fixing of H.T. danger notice plate of 250 mm x 200mm, made of mild steel sheet at least 2mm thick and vitreous enamelled white on both sides and with inscription in single red colour on front side as required. | 10.00 | Sets |  | 600.00 | 6000.00 | 1150.00 | 11500.00 | 500.00 | 5000.00 | 300.00 | 3000.00 | 3000.00 | EVERCREST PROJECTS PVT LTD
79.00 | Supply of Automatic vending machine for Hand Sanitization with 10L sanitizer. | 2.00 | Sets |  | 12000.00 | 24000.00 | 8500.00 | 17000.00 | 15000.00 | 30000.00 | 9500.00 | 19000.00 | 17000.00 | Konstelec Engineers Pvt. Ltd.
80.00 | Safety Equipments / items: Providing & fixing a set of 9.5 Liter capacity GI bucket painted in post office red colour and written with white paint 'Fire' and mounted on MS angle iron frame duly painted with bracket of appropriate size and capacity including filling white sand complete as required. (Fire bucket - 3 nos. per set). | 6.00 | Sets |  | 5000.00 | 30000.00 | 9025.00 | 54150.00 | 1800.00 | 10800.00 | 2750.00 | 16500.00 | 10800.00 | shiv electric
81.00 | Supply and fixing of safety instruction chart (in word) duly framed with 5mm thick glass complete as required. (Approx. Front area 1.20 sq.mt.) - Safety Chart | 6.00 | Sets |  | 1500.00 | 9000.00 | 1675.00 | 10050.00 | 500.00 | 3000.00 | 650.00 | 3900.00 | 3000.00 | shiv electric
82.00 | Providing & fixing of First Aid box as approved by St. John Ambulance Brigade / Indian red Cross conforming to IS 2217 - 1963 iv) First Aid box. | 6.00 | Sets |  | 3000.00 | 18000.00 | 5350.00 | 32100.00 | 500.00 | 3000.00 | 2600.00 | 15600.00 | 3000.00 | shiv electric
| Total in Figures |  |  |  |  | 126424700.00 |  | 68532580.00 |  | 81114197.00 |  | 72467131.00
Comparative Chart(eAuction)
Sl.No | Bidder Name | Auction Start Price | Quoted Rate in Figures and Words
|  |  | Bidder Price | Amount in Words
1 | Konstelec Engineers Pvt. Ltd. | 68532580 | 68432580.00 | Six Crore Eighty Four Lakh Thirty Two Thousand Five Hundred and Eighty
2 | shiv electric | 68532580 | Not Quoted | Not Quoted
3 | K KUMAR RAJA PROJECTS PVT LIMITED | 68532580 | Not Quoted | Not Quoted
4 | EVERCREST PROJECTS PVT LTD | 68532580 | Not Quoted | Not Quoted
Lowest Amount Quoted BY: Konstelec Engineers Pvt. Ltd.(6.843258E7)

## BOQ Summary
BOQ Summary Details Tender Title: Sub Station augmentation of Power Supply Eastern side of runway (C and E) at NSCBI Airport, Kolkata. (a) Co Hangar Sub station and Plant room. SH Electrical works. (Second Recall) Tender ID: 2022_AAI_102488_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Konstelec Engineers Pvt. Ltd. | 68532580.00 | L1
| 2 | EVERCREST PROJECTS PVT LTD | 72467131.00 | L2
| 3 | shiv electric | 81114197.00 | L3
| 4 | K KUMAR RAJA PROJECTS PVT LIMITED | 126424700.00 | L4