## BoQ1
Government eProcurement System Created By: KAMBLE TANAJI Created Date/Time: 23-Feb-2022 05:36 PM Tender Title: Construction of Integrated cargo terminal at Pune Airport, SH Provision of Cold Storage, Split AC, Water cooler cum purifier and AICMC Tender ID: 2022_AAI_102662_1
Tender Inviting Authority: Asst. General Manager (Engg-Elect), Pune Airport
Name of Work: Construction of Integrated cargo terminal at Pune Airport (SH: Provision of Cold Storage, Split AC, Water cooler cum purifier and AICMC)
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Winchester Enterprises(GSTN-04AOJPS9764C1ZM) |  | MEGASTAR ENGINEERING(GSTN-27AAOFM5341A1ZG) |  | M R Cooling solution pvt,ltd(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply installation testing commissioning of 2.0 TR, 5-Star rated, high wall inverter type split Air-Conditioning unit (IDU and ODU) with washable filter, cooling coil connected to condensing units, wireless remote controler for temparature adjustment, IDU blower speed, swing adjustment, auto restart facility, sleep mode, turbo mode, LED display for temperature, stands for ODU, R410a/R32 charged etc. including 5 years compressor warranty, standard length of properly insulated copper refrigerant pipe, drain pipe, copper cable between IDU and ODU as per OEM standard. It includes required civik works with good finish of all damages to the building. Make: Bluestar. Model:DBTULV or equivalent. | 4.00 | Each |  | 496000.00 | 1984000.00 | 77584.00 | 310336.00 | 40700.00 | 162800.00 | 162800.00 | M R Cooling solution pvt,ltd
2.00 | Supply, installation, testing, commissioning of 80 Ltr storage capacity (up to float valve level) stainless steel water cooler with in-built RO+UV purifier having 7-stage filters, R134a refrigerant, 60LPH cooling capacity for operation on 1-phase, 240V, 50Hz AC supply complete as required. Make: Bluestar, Model: SWCSDLX6080UVROE or equivalent. | 2.00 | Each |  | 67600.00 | 135200.00 | 102544.00 | 205088.00 | 70345.00 | 140690.00 | 135200.00 | Winchester Enterprises
3.00 | Design, supply installation testing commissioning of 2nos. (01 main and 01 stand by ) refrigeration unit for cold storage comprising of stainless steel body ceilling mounted IDU suitable for 240V, 1-ph, 50 Hz Ac supply and air-cooled single scroll compressor ODU of capacity 24800 BTU/Hr or 5.5TR suiable for 415V, 3-ph, 50 Hz AC supply including its suitable foundation/fixing arrangement for 5mX3mX4m (approx.) room to maintain 15⁰C to 25⁰C inside temperature at an ambient of 45⁰C along with controller, suitable size elastrometric nitrile rubber insulated copper refrigerant pipe (Upto 10 mtr) in suitable size perforated tray with all necessary supporting arrangement from ceiling/wall, nitrile rubber insulated UPVC drain pipe upto the nearest drain pit, 3Cx1.5 Sqmm. 1.1kV grade flexible multistrand copper conductor communication cable in 20mm steel conduit pipe between IDU and ODU, first charge of R-404a/R407c refrigerant, 4Cx6.0 Sqmm. 1.1kV grade armoured copper cable of required length including its laying, end termination with lugs, gland etc. from exsisting DB/panel to refrigerant unit, digital cold room temperature display outside the cold room and all necessary associated accessories like ODU fan, vibration isolator, different valves, safety devices, control panel, thermostat, pressure gauge etc. complete as required as recommended by OEM. The cold room shall have 60mm thick PUF insulated PPGI sheet panels for ceiling and walls, 60mm thick PUF slab for floor with marine ply and aluminum chequered plate, 60 mm thick suitable size (78"x34" approx.) PUF insulated heavy duty hinged door with factory assembled metalic locking arrangement along with gasket sealing to ensure 100% air tightness and water absorbtion/vapour permeability below permissible limit as recommended by OEM etc. complete as required. (Make: Bluestar, Daikin or equivalent) | 1.00 | Each |  | 799300.00 | 799300.00 | 905116.00 | 905116.00 | 333726.00 | 333726.00 | 333726.00 | M R Cooling solution pvt,ltd
4.00 | Design, supply installation testing commissioning of 2nos. (01 main and 01 stand by ) refrigeration unit for cold storage comprising of stainless steel body ceilling mounted IDU suitable for 240V, 1-ph, 50 Hz Ac supply and air-cooled single scroll compressor ODU of capacity 10000-26000 BTU/Hr suiable for 415V, 3-ph, 50 Hz AC supply including its suitable foundation/fixing arrangement for 3mX3mX4m (approx.) room to maintain 2⁰C to 8⁰C inside temperature at an ambient of 45⁰C along with controller, suitable size elastrometric nitrile rubber insulated copper refrigerant pipe (Upto 10 mtr) in suitable size perforated tray with all necessary supporting arrangement from ceiling/wall, nitrile rubber insulated UPVC drain pipe upto the nearest drain pit, 3Cx1.5 Sqmm. 1.1kV grade flexible multistrand copper conductor communication cable in 20mm steel conduit pipe between IDU and ODU, first charge of R-404a refrigerant, 4Cx6.0 Sqmm. 1.1kV grade armoured copper cable of required length including its laying, end termination with lugs, gland etc. from exsisting DB/panel to refrigerant unit, digital cold room temperature display outside the cold room and all necessary associated accessories like ODU fan, vibration isolator, different valves, safety devices, control panel, thermostat, pressure gauge etc. complete as required as recommended by OEM. The cold room shall have 60mm thick PUF insulated PPGI sheet panels for ceiling and walls, 60mm thick PUF slab for floor with marine ply and aluminum chequered plate, 60 mm thick suitable size (78"x34" approx.) PUF insulated heavy duty hinged door with factory assembled metalic locking arrangement along with gasket sealing to ensure 100% air tightness and water absorbtion/vapour permeability below permissible limit as recommended by OEM etc. complete as required. (Make: Bluestar, Daikin or equivalent) | 1.00 | Each |  | 694000.00 | 694000.00 | 917682.00 | 917682.00 | 254093.00 | 254093.00 | 254093.00 | M R Cooling solution pvt,ltd
5.00 | Design, supply installation testing commissioning of 2nos. (01 main and 01 stand by ) refrigeration unit for cold storage comprising of stainless steel body ceilling mounted IDU suitable for 240V, 1-ph, 50 Hz Ac supply and air-cooled single scroll compressor ODU of capacity 15000-23600 BTU/Hr suiable for 415V, 3-ph, 50 Hz AC supply including its suitable foundation/fixing arrangement for 3mX3mX4m (approx.) room to maintain (-)8⁰C to (-)2⁰C inside temperature at an ambient of 45⁰C along with controller, suitable size elastrometric nitrile rubber insulated copper refrigerant pipe (Upto 10 mtr) in suitable size perforated tray with all necessary supporting arrangement from ceiling/wall, nitrile rubber insulated UPVC drain pipe upto the nearest drain pit, 3Cx1.5 Sqmm. 1.1kV grade flexible multistrand copper conductor communication cable in 20mm steel conduit pipe between IDU and ODU, first charge of R-404a refrigerant, 4Cx6.0 Sqmm. 1.1kV grade armoured copper cable of required length including its laying, end termination with lugs, gland etc. from exsisting DB/panel to refrigerant unit, digital cold room temperature display outside the cold room and all necessary associated accessories like ODU fan, vibration isolator, different valves, safety devices, control panel, thermostat, pressure gauge etc. complete as required as recommended by OEM. The cold room shall have 100mm thick PUF insulated PPGI sheet panels for ceiling and walls, 100mm thick PUF slab for floor with marine ply and aluminum chequered plate, 100 mm thick suitable size (78"x34" approx.) PUF insulated heavy duty hinged door with factory assembled metalic locking arrangement along with gasket sealing to ensure 100% air tightness and water absorbtion/vapour permeability below permissible limit as recommended by OEM etc. complete as required. (Make: Bluestar, Daikin or equivalent) | 1.00 | Each |  | 910000.00 | 910000.00 | 1128805.00 | 1128805.00 | 303848.00 | 303848.00 | 303848.00 | M R Cooling solution pvt,ltd
6.00 | All inclusive comprehensive maintenance of 1-ph 2.0TR split inverter type air-conditioner unit including providing of all necessary consumables/spares and replacement of faulty compressor, unserviceable parts, gas charging etc. as required and carrying out complete preventive and unlimited breakdown maintenance after completion of one year Defect Liability period through OEM/OEM's authorised dealer .
6.01 | 1st year after DLP | 4.00 | Each per year |  | 3700.00 | 14800.00 | 3305.00 | 13220.00 | 2500.00 | 10000.00 | 10000.00 | M R Cooling solution pvt,ltd
6.02 | 2nd year after DLP | 4.00 | Each per year |  | 4600.00 | 18400.00 | 3635.00 | 14540.00 | 3000.00 | 12000.00 | 12000.00 | M R Cooling solution pvt,ltd
6.03 | 3rd year after DLP | 4.00 | Each per year |  | 5500.00 | 22000.00 | 3999.00 | 15996.00 | 4000.00 | 16000.00 | 15996.00 | MEGASTAR ENGINEERING
7.00 | All inclusive comprehensive maintenance of all types upto 80 Ltr storing/cooling capacity water cooler cum purifier including regular cleaning, providing of all necessary consumables/spares and replacement of faulty compressor, filters, unserviceable parts etc. with original make of brand new material etc. complete as requied after completion of one year Defect Liability period through OEM/OEM's authorised dealer.
7.01 | 1st year after DLP | 2.00 | Each per year |  | 5500.00 | 11000.00 | 4601.00 | 9202.00 | 6000.00 | 12000.00 | 9202.00 | MEGASTAR ENGINEERING
7.02 | 2nd year after DLP | 2.00 | Each per year |  | 6400.00 | 12800.00 | 5061.00 | 10122.00 | 8000.00 | 16000.00 | 10122.00 | MEGASTAR ENGINEERING
7.03 | 3rd year after DLP | 2.00 | Each per year |  | 7300.00 | 14600.00 | 5567.00 | 11134.00 | 10000.00 | 20000.00 | 11134.00 | MEGASTAR ENGINEERING
8.00 | All Inclusive Annual Comprehensive Maintenance of cold storage air cooled refrigeration unit for cold room temp. 15⁰C to 25⁰C including all accessories like IDU, ODU, control panel etc. after completion of one year Defect Liability period through OEM/OEM's authorised dealer including unlimited breakdown visit, attending complaint along with repairing/replacement of unserviceable parts like compressor including gas charging, consumables etc. as required, quarterly visit for preventive maintenance.
8.01 | 1st year after DLP | 2.00 | Each per year |  | 46000.00 | 92000.00 | 6427.00 | 12854.00 | 10000.00 | 20000.00 | 12854.00 | MEGASTAR ENGINEERING
8.02 | 2nd year after DLP | 2.00 | Each per year |  | 55000.00 | 110000.00 | 7070.00 | 14140.00 | 12000.00 | 24000.00 | 14140.00 | MEGASTAR ENGINEERING
8.03 | 3rd year after DLP | 2.00 | Each per year |  | 64000.00 | 128000.00 | 7777.00 | 15554.00 | 14000.00 | 28000.00 | 15554.00 | MEGASTAR ENGINEERING
9.00 | All Inclusive Annual Comprehensive Maintenance of cold storage air cooled refrigeration unit for cold room temp. 2⁰C to 8⁰C including all accessories like IDU, ODU, control panel etc. after completion of one year Defect Liability period through OEM/OEM's authorised dealer including unlimited breakdown visit, attending complaint along with repairing/replacement of unserviceable parts like compressor including gas charging, consumables etc. as required, quarterly visit for preventive maintenance.
9.01 | 1st year after DLP | 2.00 | Each per year |  | 37000.00 | 74000.00 | 15320.00 | 30640.00 | 10000.00 | 20000.00 | 20000.00 | M R Cooling solution pvt,ltd
9.02 | 2nd year after DLP | 2.00 | Each per year |  | 46000.00 | 92000.00 | 16852.00 | 33704.00 | 12000.00 | 24000.00 | 24000.00 | M R Cooling solution pvt,ltd
9.03 | 3rd year after DLP | 2.00 | Each per year |  | 55000.00 | 110000.00 | 18537.00 | 37074.00 | 14000.00 | 28000.00 | 28000.00 | M R Cooling solution pvt,ltd
10.00 | All Inclusive Annual Comprehensive Maintenance of cold storage air cooled refrigeration unit for cold room temp. -8⁰C to -2⁰C including all accessories like IDU, ODU, control panel etc. after completion of one year Defect Liability period through OEM/OEM's authorised dealer including unlimited breakdown visit, attending complaint along with repairing/replacement of unserviceable parts like compressor including gas charging, consumables etc. as required, quarterly visit for preventive maintenance.
10.10 | 1st year after DLP | 2.00 | Each per year |  | 73000.00 | 146000.00 | 17982.00 | 35964.00 | 10000.00 | 20000.00 | 20000.00 | M R Cooling solution pvt,ltd
10.20 | 2nd year after DLP | 2.00 | Each per year |  | 82000.00 | 164000.00 | 19780.00 | 39560.00 | 12000.00 | 24000.00 | 24000.00 | M R Cooling solution pvt,ltd
10.30 | 3rd year after DLP | 2.00 | Each per year |  | 91000.00 | 182000.00 | 21758.00 | 43516.00 | 14000.00 | 28000.00 | 28000.00 | M R Cooling solution pvt,ltd
| Total in Figures |  |  |  |  | 5714100.00 |  | 3804247.00 |  | 1497157.00
Lowest Amount Quoted BY: M R Cooling solution pvt,ltd(1497157.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of Integrated cargo terminal at Pune Airport, SH Provision of Cold Storage, Split AC, Water cooler cum purifier and AICMC Tender ID: 2022_AAI_102662_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M R Cooling solution pvt,ltd | 1497157.00 | L1
| 2 | MEGASTAR ENGINEERING | 3804247.00 | L2
| 3 | Winchester Enterprises | 5714100.00 | L3