## BoQ1
Government eProcurement System Created By: Subhra Santa Ghosh Created Date/Time: 01-Mar-2022 02:53 PM Tender Title: Extension of Terminal Building under Phase-III at Bagdogra Airport (SH Electrical and Mechanical Works). SH-II SITC of LT Panels, Supply and laying of cables and IE works. Tender ID: 2022_AAI_103733_1
Tender Inviting Authority: SM (E-E)
Name of work: Extension of Terminal Building under Phase-III at Bagdogra Airport (SH: Electrical & Mechanical Works). SH-II: SITC of LT Panels, Supply & laying of cables and IE works.
Contract No: 2022_aai_103733_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | jaydeep agency corporation(GSTN-24ACIPP6157B1ZQ) |  | Youngmen Traders(GSTN-19AEIPB6323B1ZZ) |  | Mukherjee Commercial Enterprise(GSTN-19ALVPM0307N1ZJ) |  | Industrial Traders(GSTN-09ACJPC1773F1ZQ) |  | SAHA COMMERCIAL CONSTRUCTION(GSTN-19AASFS6288A1ZN) |  | SUPER BUILDERS(GSTN-NA)
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of LT Panel conforming to IS 8623 / IEC 60439 PTTA type & shall be of Form-3b construction with following mentioned and complete in all respect and as per technical specifications. | 1.00 | Job | 504917.00 | 732500.00 | 732500.00 | 425000.00 | 425000.00 | 410000.00 | 410000.00 | 299743.00 | 299743.00 | 575000.00 | 575000.00 | 706200.00 | 706200.00 | 299743.00 | Industrial Traders
1.10 | a)Supply, Installation, Testing and Commissioning of cubicle type LT panel, (minimum IP42 protection) for indoor application, suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, fabricated in compartmentalized modular design from CRCA sheet steel of minimum 2 mm thick for frame work and covers, 3 mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars for high conductivity, DMC/SMC bus bar supports, with short circuit withstand capacity as per design subject to minimum 50 KA for 1 sec , bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common Copper earth bus bar of size as per IS 3043 subject to minimum 50 mm x 6 mm at the rear with 2 Nos. earth stud, solid / flexible connections from main earth bus bar to switchgears with required size of Cooper conductor and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, including provision of SPD's. Surge Protection Devices (SPD’S) shall be provided to LT Panel (Type 2 / Class C), i/c providing following switchgears / accessories as per specifications. Bus-Bar: TPN aluminium extensible type main bus bars of minimum 300 Amps. capacity with heat shrinkable coloured sleeves having 100% neutral bus as that of phase i/c DMC / SMC bus bars supports at required intervals complete for cross section, size supports & having spacing etc. for withstanding fault level of 50kA capacity for 1 sec.
1.20 | b)Incomer: 2(Two) Nos MCCB(Ics=100% Icu), 250 Amps, 4 Pole, min 35 kA with adjustable setting, Microprocessor Based with adjustable Overload, Short Circuit and In-Built Earth Fault Protection, including connections etc as required. 3(Three)Nos. LED type, R,Y,B Phase indicating lamp with 2 Amp MCB for controlling. Intelligent multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc , LED display with required Nos CTs, 250 / 5,15 VA, class 1.0 and control circuit wiring with 2 Amp MCB for controlling.
1.30 | c)Buscoupler: 1 No MCCB(Ics=100% Icu), 250 Amps, 4 Pole, min 35 kA with adjustable setting, Microprocessor Based with adjustable Overload, Short Circuit and In-Built Earth Fault Protection,including connections etc as required. 3(Three)Nos. LED type, LED type, R,Y,B Phase indicating lamp with 2 Amp MCB for controlling.
1.40 | d)Outgoing:- i) 02 Nos MCCB(Ics=100% Icu),125 Amps, 4 Pole, min 35 kA with adjustable setting , Thermal Magnetic release shall have Variable Thermal (O/L) & Variable Magnetic (S/C) protection,including connections etc as required. Ii)03 Nos MCCB(Ics=100% Icu), 100 Amps, 4 Pole, min 35 kA with adjustable setting , Thermal Magnetic release shall have fixed Thermal (O/L) & fixed Magnetic (S/C) protection,including connections etc as required. iii)04 Nos MCCB(Ics=100% Icu), 63 Amps, 4 Pole, min 35 kA with adjustable setting , Thermal Magnetic release shall have fixed Thermal (O/L) & fixed Magnetic (S/C) protection,including connections etc as required. iv) 1 Nos MCCB(Ics=100% Icu), 40 Amps, 4 Pole, min 35 kA with adjustable setting , Thermal Magnetic release shall have fixed Thermal (O/L) & fixed Magnetic (S/C) protection,including connections etc as required.
1.50 | Note: a) ON, OFF & TRIP indication lamp(1 each LED type) with 2 Amp SP MCB for each incoming/outgoing. b) 1 Set Rotary operating mechanism for all MCCBs c) Terminal extension spreaders for MCCBs above 63A c)All Incoming,Buscoupler,Outgoing shall have door lock arrangement with MCCB. d)All outgoings shall have minimum 96mm*48 mm digital ammeter with selector switch,Suitable CT. e)All Incomers and buscoupler must have electrical & mechanical interlocking arrangement as suitable. f)Panel should be complete in all respect to be installed and comissioned at site.
2.00 | SITC of LT Panel conforming to IS 8623 / IEC 60439 PTTA type & shall be of Form-3b construction with following mentioned and complete in all respect and as per technical specifications. | 1.00 | Job | 444650.00 | 687500.00 | 687500.00 | 375000.00 | 375000.00 | 300000.00 | 300000.00 | 299743.00 | 299743.00 | 505000.00 | 505000.00 | 693360.00 | 693360.00 | 299743.00 | Industrial Traders
2.10 | a)Supply, Installation, Testing and Commissioning of cubicle type LT panel, (minimum IP42 protection) for indoor application, suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, fabricated in compartmentalized modular design from CRCA sheet steel of minimum 2 mm thick for frame work and covers, 3 mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars for high conductivity, DMC/SMC bus bar supports, with short circuit withstand capacity as per design subject to minimum 50 KA for 1 sec , bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common Copper earth bus bar of size as per IS 3043 subject to minimum 50 mm x 6 mm at the rear with 2 Nos. earth stud, solid / flexible connections from main earth bus bar to switchgears with required size of Cooper conductor and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, including provision of SPD's. Surge Protection Devices (SPD’S) shall be provided to LT Panel (Type 2 / Class C), i/c providing following switchgears / accessories as per specifications. Bus-Bar: TPN aluminium extensible type main bus bars of minimum 250 Amps. capacity with heat shrinkable coloured sleeves having 100% neutral bus as that of phase i/c DMC / SMC bus bars supports at required intervals complete for cross section, size supports & having spacing etc. for withstanding fault level of 50kA capacity for 1 sec.
2.20 | b)Incomer:- 2 Nos MCCB, 200 Amps, 4 Pole, min 35 kA with adjustable setting , Thermal Magnetic release shall have Variable Thermal (O/L) & Variable Magnetic (S/C) protection,including connections etc as required. 3(Three)Nos. LED type, R,Y,B Phase indicating lamp with 2 Amp MCB for controlling. Intelligent multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc , LED display with required Nos CTs, 200 / 5,15 VA, class 1.0 and control circuit wiring with 2 Amp MCB for controlling.
2.30 | c)Buscoupler:- 1 No MCCB(Ics=100% Icu), 200 Amps, 4 Pole, min 35 kA with adjustable setting , Thermal Magnetic release shall have Variable Thermal (O/L) & Variable Magnetic (S/C) protection,including connections etc as required. 3(Three)Nos. LED type, LED type, R,Y,B Phase indicating lamp with 2 Amp MCB for controlling.
2.40 | d)Outgoing:- i) 04 Nos MCCB(Ics=100% Icu), 63 Amps, 4 Pole, min 35 kA with adjustable setting ,Thermal Magnetic release shall have fixed Thermal (O/L) & fixed Magnetic (S/C) protection,including connections etc as required. ii) 06 Nos MCCB(Ics=100% Icu), 40 Amps, 4 Pole, min 35 kA with adjustable setting , Thermal Magnetic release shall have fixed Thermal (O/L) & fixed Magnetic (S/C) protection,including connections etc as required.
2.50 | Note: a) ON, OFF & TRIP indication lamp(1 each LED type) with 2 Amp SP MCB for each incoming/outgoing. b) 1 Set Rotary operating mechanism for all MCCBs c) Terminal extension spreaders for MCCBs above 63A c)All Incoming,Buscoupler,Outgoing shall have door lock arrangement with MCCB. d)All outgoings shall have minimum 96mm*48 mm digital ammeter with selector switch,Suitable CT. e)All Incomers and buscoupler must have electrical & mechanical interlocking arrangement as suitable. f)Panel should be complete in all respect to be installed and comissioned at site.
3.00 | Supply of following size XLPE insulated and PVC sheathed aluminium conductor armoured Power Cable of 1.1KV grade, confirming to IS 7098, Part-I 1988 with up to date amendments and confirming to technical specifications.(The outer sheath shall be FRLS.)
3.10 | 3.5 CORE 185 sq.mm. | 1300.00 | Metre | 1276.00 | 1000.00 | 1300000.00 | 850.00 | 1105000.00 | 1000.00 | 1300000.00 | 1059.00 | 1376700.00 | 875.00 | 1137500.00 | 1230.00 | 1599000.00 | 1105000.00 | Youngmen Traders
3.20 | 3.5 CORE 50 sq.mm. | 450.00 | Metre | 419.00 | 350.00 | 157500.00 | 295.00 | 132750.00 | 320.00 | 144000.00 | 346.00 | 155700.00 | 285.00 | 128250.00 | 414.00 | 186300.00 | 128250.00 | SAHA COMMERCIAL CONSTRUCTION
3.30 | 4 CORE 25 sq.mm. | 1100.00 | Metre | 280.00 | 225.00 | 247500.00 | 195.00 | 214500.00 | 200.00 | 220000.00 | 224.00 | 246400.00 | 185.00 | 203500.00 | 270.00 | 297000.00 | 203500.00 | SAHA COMMERCIAL CONSTRUCTION
4.00 | Supply of surface/recessed type 2' x 2' (minimum 36W) LED type downlighter suitable to operate on 140-270 V, 50 Hz, AC supply having Extruded aluminium/CRCA/standard alloy housing ,with minimum IP-20 protection,having efficacy of min 100 lm/W, complete with all types of accessories and driver ready to be installed at site as per Technical Specifications attached. | 179.00 | Each | 3167.00 | 1500.00 | 268500.00 | 1400.00 | 250600.00 | 3850.00 | 689150.00 | 1950.00 | 349050.00 | 1730.00 | 309670.00 | 2550.00 | 456450.00 | 250600.00 | Youngmen Traders
5.00 | Supply of LED type flood light (minimum 150 watt) luminaire suitable to operate on 140-270 V, 50 Hz, AC supply having Extruded aluminium/CRCA/standard alloy housing ,with minimum IP-65 protection,having efficacy of min 110 lm/W, complete with all types of accessories, mounting device and driver ready to be installed at site as per Technical Specifications attached. | 15.00 | Each | 6100.00 | 4800.00 | 72000.00 | 4500.00 | 67500.00 | 25200.00 | 378000.00 | 6344.00 | 95160.00 | 5950.00 | 89250.00 | 6200.00 | 93000.00 | 67500.00 | Youngmen Traders
6.00 | Installation, testing and commissioning of pre-wired, LED downlighter / flood light of all types, complete with all accessories etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 194.00 | Each | 162.00 | 75.00 | 14550.00 | 100.00 | 19400.00 | 150.00 | 29100.00 | 122.00 | 23668.00 | 300.00 | 58200.00 | 190.00 | 36860.00 | 14550.00 | jaydeep agency corporation
7.00 | Dismanting of existing light fitting of various wattage / ceiling fan and keeping the same in AAI store (within 50 Mtr. distance) as per site condition and as directed by E.I.C. | 223.00 | Each | 54.00 | 25.00 | 5575.00 | 35.00 | 7805.00 | 50.00 | 11150.00 | 122.00 | 27206.00 | 100.00 | 22300.00 | 80.00 | 17840.00 | 5575.00 | jaydeep agency corporation
8.00 | Supply of 1200 mm sweep, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) Motor, class of insulation: B, 3 nos. blades, 30 cm long down rod, 2 nos. canopies, shackle kit, safety rope, copper winding, Power Factor not less than 0.9, Service Value (CMM/W) minimum 6.85, Air delivery minimum 215 CMM, 350 RPM (tolerance as per IS : 374-2019), THD less than 10%, remote or electronic regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=75 degree C (max.), insulation resistance more than 2 mega ohm, suitable for 230 V, 50 Hz, single phase AC Supply, earthing etc. complete as required. (Colour of fans to be approved by EIC). | 129.00 | Each | 3529.00 | 3200.00 | 412800.00 | 2300.00 | 296700.00 | 2000.00 | 258000.00 | 2792.00 | 360168.00 | 3500.00 | 451500.00 | 2850.00 | 367650.00 | 258000.00 | Mukherjee Commercial Enterprise
9.00 | Supply of ceiling mounted exhaust fan having min sweep dia 130 mm, min air delivery 150 m³/h suitable for single phase AC operation, complete with all acessories as required and ready to be installed at site. | 8.00 | Each | 4470.00 | 1100.00 | 8800.00 | 3500.00 | 28000.00 | 2000.00 | 16000.00 | 1464.00 | 11712.00 | 1950.00 | 15600.00 | 1200.00 | 9600.00 | 8800.00 | jaydeep agency corporation
10.00 | Providing and fixing of suitable size rigid PVC pipe on wall/ above false ceiling with suitable clamping/support for outlet of ceiling mounted exhaust fan as per site conditions and as directed by EIC.(for BOQ Sl No 9) | 30.00 | Metre | 412.00 | 50.00 | 1500.00 | 300.00 | 9000.00 | 100.00 | 3000.00 | 97.00 | 2910.00 | 30.00 | 900.00 | 400.00 | 12000.00 | 900.00 | SAHA COMMERCIAL CONSTRUCTION
11.00 | SITC of single door panel board made out of CRCA sheet steel (conforming to IS 8623,IEC :60439) with provision of FP MCCB as incomer (1 No) & outgoing (4 Nos.) in following configuration including cable alley, basic analog metering module, basic indication module ,busbars etc. with all types of accessories complete in all respect as per technical specifications and ready to be commissioned at site.
11.10 | (i) Incoming MCCB : FP,100 A, 35 KA Ics= 75% Icu (min) - 01 No. (ii) Outgoing MCBB: FP, 25 A, 25 KA Ics=50% Icu (min) - 03 No. and FP, 63 A, 25 KA Ics=50% Icu (min) - 01 No. | 1.00 | Each | 114242.00 | 96500.00 | 96500.00 | 65000.00 | 65000.00 | 40000.00 | 40000.00 | 61000.00 | 61000.00 | 32000.00 | 32000.00 | 100000.00 | 100000.00 | 32000.00 | SAHA COMMERCIAL CONSTRUCTION
11.20 | (i) Incoming MCCB : FP,100 A, 35 KA Ics= 75% Icu (min) - 01 No. (ii) Outgoing MCBB: FP, 32 A, 25 KA Ics=50% Icu (min) - 04 No. | 1.00 | Each | 114242.00 | 105800.00 | 105800.00 | 65000.00 | 65000.00 | 50000.00 | 50000.00 | 61000.00 | 61000.00 | 35000.00 | 35000.00 | 100000.00 | 100000.00 | 35000.00 | SAHA COMMERCIAL CONSTRUCTION
12.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. Group C | 24.00 | Point | 1409.00 | 1240.00 | 29760.00 | 900.00 | 21600.00 | 1000.00 | 24000.00 | 610.00 | 14640.00 | 1450.00 | 34800.00 | 1400.00 | 33600.00 | 14640.00 | Industrial Traders
13.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc as required. Group C | 61.00 | Point | 868.00 | 1010.00 | 61610.00 | 650.00 | 39650.00 | 2500.00 | 152500.00 | 610.00 | 37210.00 | 1525.00 | 93025.00 | 850.00 | 51850.00 | 37210.00 | Industrial Traders
14.00 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
14.10 | 3 x 2.5 sq. mm | 100.00 | Metre | 151.00 | 120.00 | 12000.00 | 130.00 | 13000.00 | 90.00 | 9000.00 | 109.00 | 10900.00 | 125.00 | 12500.00 | 150.00 | 15000.00 | 9000.00 | Mukherjee Commercial Enterprise
14.20 | 3 x 4 sq. mm | 300.00 | Metre | 229.00 | 140.00 | 42000.00 | 175.00 | 52500.00 | 145.00 | 43500.00 | 109.00 | 32700.00 | 165.00 | 49500.00 | 230.00 | 69000.00 | 32700.00 | Industrial Traders
14.30 | 3 x 6 sq. mm | 125.00 | Metre | 339.00 | 180.00 | 22500.00 | 225.00 | 28125.00 | 200.00 | 25000.00 | 164.00 | 20500.00 | 240.00 | 30000.00 | 330.00 | 41250.00 | 20500.00 | Industrial Traders
14.40 | 6 x 6 sq. mm | 22.00 | Metre | 671.00 | 280.00 | 6160.00 | 400.00 | 8800.00 | 350.00 | 7700.00 | 329.00 | 7238.00 | 470.00 | 10340.00 | 680.00 | 14960.00 | 6160.00 | jaydeep agency corporation
15.00 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
15.10 | 20 mm | 100.00 | Metre | 151.00 | 200.00 | 20000.00 | 90.00 | 9000.00 | 100.00 | 10000.00 | 180.00 | 18000.00 | 130.00 | 13000.00 | 108.00 | 10800.00 | 9000.00 | Youngmen Traders
15.20 | 25 mm | 475.00 | Metre | 171.00 | 300.00 | 142500.00 | 115.00 | 54625.00 | 140.00 | 66500.00 | 222.00 | 105450.00 | 160.00 | 76000.00 | 138.00 | 65550.00 | 54625.00 | Youngmen Traders
15.30 | 32 mm | 22.00 | Metre | 211.00 | 400.00 | 8800.00 | 160.00 | 3520.00 | 200.00 | 4400.00 | 300.00 | 6600.00 | 220.00 | 4840.00 | 168.00 | 3696.00 | 3520.00 | Youngmen Traders
16.00 | Supplying and fixing metal box of 200 mm X 150 mm X 75 mm (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required. | 10.00 | Each | 304.00 | 250.00 | 2500.00 | 125.00 | 1250.00 | 200.00 | 2000.00 | 183.00 | 1830.00 | 325.00 | 3250.00 | 300.00 | 3000.00 | 1250.00 | Youngmen Traders
17.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
17.10 | Telephone socket outlet | 4.00 | Each | 138.00 | 280.00 | 1120.00 | 110.00 | 440.00 | 250.00 | 1000.00 | 85.00 | 340.00 | 275.00 | 1100.00 | 125.00 | 500.00 | 340.00 | Industrial Traders
17.20 | Bell push | 2.00 | Each | 147.00 | 260.00 | 520.00 | 115.00 | 230.00 | 200.00 | 400.00 | 42.00 | 84.00 | 175.00 | 350.00 | 134.00 | 268.00 | 84.00 | Industrial Traders
18.00 | Supplying and fixing 1 or 2 Module (75mmX75mm), GI box alongwith modular base & cover plate for modular switches in recess etc as required. | 6.00 | Each | 253.00 | 150.00 | 900.00 | 150.00 | 900.00 | 150.00 | 900.00 | 183.00 | 1098.00 | 250.00 | 1500.00 | 240.00 | 1440.00 | 900.00 | jaydeep agency corporation, Youngmen Traders, Mukherjee Commercial Enterprise
19.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. | 9.00 | Each | 415.00 | 200.00 | 1800.00 | 325.00 | 2925.00 | 450.00 | 4050.00 | 244.00 | 2196.00 | 250.00 | 2250.00 | 370.00 | 3330.00 | 1800.00 | jaydeep agency corporation
20.00 | Supplying and fixing suitable size GI box with modular plate and cover in FRLSont on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 9.00 | Each | 533.00 | 700.00 | 6300.00 | 350.00 | 3150.00 | 550.00 | 4950.00 | 244.00 | 2196.00 | 850.00 | 7650.00 | 500.00 | 4500.00 | 2196.00 | Industrial Traders
21.00 | Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, complete as required. | 2.00 | Each | 262.00 | 250.00 | 500.00 | 150.00 | 300.00 | 200.00 | 400.00 | 183.00 | 366.00 | 350.00 | 700.00 | 110.00 | 220.00 | 220.00 | SUPER BUILDERS
22.00 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable etc. as required. | 129.00 | Each | 172.00 | 50.00 | 6450.00 | 125.00 | 16125.00 | 100.00 | 12900.00 | 122.00 | 15738.00 | 250.00 | 32250.00 | 170.00 | 21930.00 | 6450.00 | jaydeep agency corporation
23.00 | Supplying and fixing extra down rod of 10 cm length G.I. pipe ,15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 129.00 | Each | 39.00 | 50.00 | 6450.00 | 30.00 | 3870.00 | 250.00 | 32250.00 | 73.00 | 9417.00 | 40.00 | 5160.00 | 30.00 | 3870.00 | 3870.00 | Youngmen Traders, SUPER BUILDERS
24.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providng and fixing 2 nos. 3 pin 5/6 amps modular socket outlets and 2 nos 5/6 amps modular switches, connection etc. as required. (For light plugs to be used in non residential buildings). | 6.00 | Each | 632.00 | 250.00 | 1500.00 | 450.00 | 2700.00 | 750.00 | 4500.00 | 610.00 | 3660.00 | 750.00 | 4500.00 | 550.00 | 3300.00 | 1500.00 | jaydeep agency corporation
25.00 | Providing and fixing following rating and breaking capacity MCCB with thermomagnetic release and terminal spreaders in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
25.10 | 4 Pole 32 A Ics=100% Icu at 415V | 5.00 | Each | 2100.00 | 4200.00 | 21000.00 | 1400.00 | 7000.00 | 4500.00 | 22500.00 | 3050.00 | 15250.00 | 3500.00 | 17500.00 | 6500.00 | 32500.00 | 7000.00 | Youngmen Traders
25.20 | 4 Pole 50 A Ics=100% Icu at 415V | 2.00 | Each | 2100.00 | 5200.00 | 10400.00 | 1400.00 | 2800.00 | 4500.00 | 9000.00 | 3172.00 | 6344.00 | 4000.00 | 8000.00 | 6500.00 | 13000.00 | 2800.00 | Youngmen Traders
25.30 | 4 Pole , 100 A Ics=100% Icu at 415V | 3.00 | Each | 2547.00 | 6500.00 | 19500.00 | 1600.00 | 4800.00 | 4500.00 | 13500.00 | 6100.00 | 18300.00 | 7500.00 | 22500.00 | 6500.00 | 19500.00 | 4800.00 | Youngmen Traders
26.00 | Supplying and fixing 8 way, double door single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) | 1.00 | Each | 1926.00 | 1100.00 | 1100.00 | 830.00 | 830.00 | 2000.00 | 2000.00 | 3357.00 | 3357.00 | 2500.00 | 2500.00 | 1600.00 | 1600.00 | 830.00 | Youngmen Traders
27.00 | Supplying and fixing 8 way (4 + 24), Double door, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) | 2.00 | Each | 5311.00 | 24800.00 | 49600.00 | 2600.00 | 5200.00 | 4800.00 | 9600.00 | 3357.00 | 6714.00 | 3750.00 | 7500.00 | 4200.00 | 8400.00 | 5200.00 | Youngmen Traders
28.00 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB’s (but without MCB’/MCCB ) as required .
28.10 | 4 way (4 + 12), Double door, suitable for MCCB Incoming | 6.00 | Each | 9543.00 | 5200.00 | 31200.00 | 5500.00 | 33000.00 | 5000.00 | 30000.00 | 8470.00 | 50820.00 | 4000.00 | 24000.00 | 7600.00 | 45600.00 | 24000.00 | SAHA COMMERCIAL CONSTRUCTION
28.20 | 8 way (4 + 24), Double door, suitable for MCCB Incoming | 1.00 | Each | 10968.00 | 6400.00 | 6400.00 | 6325.00 | 6325.00 | 8200.00 | 8200.00 | 9541.00 | 9541.00 | 4750.00 | 4750.00 | 9150.00 | 9150.00 | 4750.00 | SAHA COMMERCIAL CONSTRUCTION
29.00 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
29.10 | Single pole | 100.00 | Each | 235.00 | 89.00 | 8900.00 | 98.00 | 9800.00 | 200.00 | 20000.00 | 120.00 | 12000.00 | 175.00 | 17500.00 | 150.00 | 15000.00 | 8900.00 | jaydeep agency corporation
29.20 | Single pole and neutral | 2.00 | Each | 604.00 | 298.00 | 596.00 | 325.00 | 650.00 | 400.00 | 800.00 | 414.00 | 828.00 | 350.00 | 700.00 | 490.00 | 980.00 | 596.00 | jaydeep agency corporation
29.30 | Triple pole | 6.00 | Each | 1005.00 | 625.00 | 3750.00 | 565.00 | 3390.00 | 1000.00 | 6000.00 | 688.00 | 4128.00 | 500.00 | 3000.00 | 800.00 | 4800.00 | 3000.00 | SAHA COMMERCIAL CONSTRUCTION
29.40 | Triple pole and neutral | 4.00 | Each | 1300.00 | 780.00 | 3120.00 | 745.00 | 2980.00 | 1400.00 | 5600.00 | 873.00 | 3492.00 | 925.00 | 3700.00 | 1080.00 | 4320.00 | 2980.00 | Youngmen Traders
30.00 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 20.00 | Each | 9.00 | 2.00 | 40.00 | 12.00 | 240.00 | 10.00 | 200.00 | 24.00 | 480.00 | 15.00 | 300.00 | 15.00 | 300.00 | 40.00 | jaydeep agency corporation
31.00 | Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps “C” curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 4.00 | Each | 1441.00 | 1280.00 | 5120.00 | 610.00 | 2440.00 | 3000.00 | 12000.00 | 732.00 | 2928.00 | 1250.00 | 5000.00 | 1290.00 | 5160.00 | 2440.00 | Youngmen Traders
32.00 | Supplying and installing 450 mm width X 62.5 mm depth X 2.0 mm thickness of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. | 152.00 | Metre | 1450.00 | 980.00 | 148960.00 | 1100.00 | 167200.00 | 1200.00 | 182400.00 | 1415.00 | 215080.00 | 850.00 | 129200.00 | 2000.00 | 304000.00 | 129200.00 | SAHA COMMERCIAL CONSTRUCTION
33.00 | Supplying and installing 450 mm width X 62.5 mm depth X 2.0 mm thickness of perforated painted with powder coating M.S. cable tray bends with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nut painting suspenders etc as required. | 10.00 | Each | 3033.00 | 1140.00 | 11400.00 | 2500.00 | 25000.00 | 1200.00 | 12000.00 | 1220.00 | 12200.00 | 950.00 | 9500.00 | 4500.00 | 45000.00 | 9500.00 | SAHA COMMERCIAL CONSTRUCTION
34.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 8.00 | Set | 6659.00 | 5790.00 | 46320.00 | 5500.00 | 44000.00 | 4000.00 | 32000.00 | 9760.00 | 78080.00 | 8750.00 | 70000.00 | 6000.00 | 48000.00 | 32000.00 | Mukherjee Commercial Enterprise
35.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 56.00 | Metre | 138.00 | 220.00 | 12320.00 | 115.00 | 6440.00 | 140.00 | 7840.00 | 146.00 | 8176.00 | 155.00 | 8680.00 | 175.00 | 9800.00 | 6440.00 | Youngmen Traders
36.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 11.00 | Metre | 627.00 | 570.00 | 6270.00 | 475.00 | 5225.00 | 550.00 | 6050.00 | 610.00 | 6710.00 | 490.00 | 5390.00 | 600.00 | 6600.00 | 5225.00 | Youngmen Traders
37.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 66.00 | Metre | 205.00 | 200.00 | 13200.00 | 95.00 | 6270.00 | 140.00 | 9240.00 | 164.00 | 10824.00 | 150.00 | 9900.00 | 160.00 | 10560.00 | 6270.00 | Youngmen Traders
38.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
38.10 | Upto 35 sq. mm | 10.00 | Metre | 346.00 | 200.00 | 2000.00 | 250.00 | 2500.00 | 150.00 | 1500.00 | 280.00 | 2800.00 | 350.00 | 3500.00 | 190.00 | 1900.00 | 1500.00 | Mukherjee Commercial Enterprise
38.20 | Above 35 sq. mm and upto 95 sq. mm | 10.00 | Metre | 359.00 | 220.00 | 2200.00 | 260.00 | 2600.00 | 170.00 | 1700.00 | 305.00 | 3050.00 | 375.00 | 3750.00 | 200.00 | 2000.00 | 1700.00 | Mukherjee Commercial Enterprise
38.30 | Above 95 sq. mm and upto 185 sq. mm | 10.00 | Metre | 372.00 | 250.00 | 2500.00 | 275.00 | 2750.00 | 200.00 | 2000.00 | 366.00 | 3660.00 | 400.00 | 4000.00 | 250.00 | 2500.00 | 2000.00 | Mukherjee Commercial Enterprise
39.00 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required.
39.10 | Upto 35 sq. mm | 10.00 | Metre | 235.00 | 80.00 | 800.00 | 150.00 | 1500.00 | 50.00 | 500.00 | 244.00 | 2440.00 | 250.00 | 2500.00 | 235.00 | 2350.00 | 500.00 | Mukherjee Commercial Enterprise
39.20 | Above 35 sq. mm and upto 95 sq. mm | 10.00 | Metre | 248.00 | 100.00 | 1000.00 | 160.00 | 1600.00 | 60.00 | 600.00 | 244.00 | 2440.00 | 275.00 | 2750.00 | 256.00 | 2560.00 | 600.00 | Mukherjee Commercial Enterprise
39.30 | Above 95 sq. mm and upto 185 sq. mm | 10.00 | Metre | 261.00 | 110.00 | 1100.00 | 175.00 | 1750.00 | 75.00 | 750.00 | 305.00 | 3050.00 | 325.00 | 3250.00 | 260.00 | 2600.00 | 750.00 | Mukherjee Commercial Enterprise
40.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
40.10 | Upto 35 sq. mm | 56.00 | Metre | 21.00 | 20.00 | 1120.00 | 15.00 | 840.00 | 50.00 | 2800.00 | 61.00 | 3416.00 | 40.00 | 2240.00 | 25.00 | 1400.00 | 840.00 | Youngmen Traders
40.20 | Above 35 sq. mm and upto 95 sq. mm | 44.00 | Metre | 34.00 | 25.00 | 1100.00 | 25.00 | 1100.00 | 60.00 | 2640.00 | 85.00 | 3740.00 | 50.00 | 2200.00 | 35.00 | 1540.00 | 1100.00 | jaydeep agency corporation, Youngmen Traders
40.30 | Above 95 sq. mm and upto 185 sq. mm | 108.00 | Metre | 47.00 | 40.00 | 4320.00 | 30.00 | 3240.00 | 75.00 | 8100.00 | 97.00 | 10476.00 | 100.00 | 10800.00 | 50.00 | 5400.00 | 3240.00 | Youngmen Traders
41.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
41.10 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 533.00 | Metre | 38.00 | 25.00 | 13325.00 | 25.00 | 13325.00 | 50.00 | 26650.00 | 60.00 | 31980.00 | 50.00 | 26650.00 | 84.00 | 44772.00 | 13325.00 | jaydeep agency corporation, Youngmen Traders
41.20 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 367.00 | Metre | 112.00 | 35.00 | 12845.00 | 75.00 | 27525.00 | 100.00 | 36700.00 | 97.00 | 35599.00 | 70.00 | 25690.00 | 105.00 | 38535.00 | 12845.00 | jaydeep agency corporation
41.30 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 15.00 | Metre | 129.00 | 50.00 | 750.00 | 80.00 | 1200.00 | 200.00 | 3000.00 | 146.00 | 2190.00 | 120.00 | 1800.00 | 144.00 | 2160.00 | 750.00 | jaydeep agency corporation
42.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) on cable tray as required. | 608.00 | Metre | 89.00 | 65.00 | 39520.00 | 55.00 | 33440.00 | 75.00 | 45600.00 | 219.00 | 133152.00 | 75.00 | 45600.00 | 150.00 | 91200.00 | 33440.00 | Youngmen Traders
43.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
43.10 | 3½ X 50 sq. mm (35mm) | 14.00 | Each | 446.00 | 250.00 | 3500.00 | 325.00 | 4550.00 | 200.00 | 2800.00 | 305.00 | 4270.00 | 450.00 | 6300.00 | 350.00 | 4900.00 | 2800.00 | Mukherjee Commercial Enterprise
43.20 | 3½ X 185 sq. mm (57mm) | 8.00 | Each | 1158.00 | 850.00 | 6800.00 | 750.00 | 6000.00 | 600.00 | 4800.00 | 488.00 | 3904.00 | 575.00 | 4600.00 | 1000.00 | 8000.00 | 3904.00 | Industrial Traders
43.30 | 4 X 25 sq. mm (28mm) | 40.00 | Each | 352.00 | 225.00 | 9000.00 | 275.00 | 11000.00 | 150.00 | 6000.00 | 292.00 | 11680.00 | 285.00 | 11400.00 | 300.00 | 12000.00 | 6000.00 | Mukherjee Commercial Enterprise
44.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
44.10 | 3½ X 50 sq. mm | 6.00 | Each | 2165.00 | 1950.00 | 11700.00 | 1500.00 | 9000.00 | 3500.00 | 21000.00 | 6100.00 | 36600.00 | 2250.00 | 13500.00 | 2000.00 | 12000.00 | 9000.00 | Youngmen Traders
44.20 | 3½ X 185 sq. mm | 6.00 | Each | 4553.00 | 2750.00 | 16500.00 | 2500.00 | 15000.00 | 4500.00 | 27000.00 | 6100.00 | 36600.00 | 5000.00 | 30000.00 | 4000.00 | 24000.00 | 15000.00 | Youngmen Traders
45.00 | Providing laying, testing & commissioning of 'C' class heavy duty MS Pipe conforming to IS 1239/3589 i/c fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. in ground/on surface including welding, excavation & providing cement concrete blocks as supports, anticorrosive treatment with coaltar/asphalt tape as per IS 10221, refilling the trench etc. of size 200 mm. dia (wall thickness = 6.3 mm) complete as required. | 40.00 | Metre | 5294.00 | 2850.00 | 114000.00 | 4500.00 | 180000.00 | 2600.00 | 104000.00 | 2440.00 | 97600.00 | 3750.00 | 150000.00 | 5500.00 | 220000.00 | 97600.00 | Industrial Traders
| Total in Figures |  |  |  |  | 5127671.00 |  | 3976475.00 |  | 4941420.00 |  | 4554222.00 |  | 4646535.00 |  | 6087411.00
Lowest Amount Quoted BY: Youngmen Traders(3976475.00)

## BOQ Summary
BOQ Summary Details Tender Title: Extension of Terminal Building under Phase-III at Bagdogra Airport (SH Electrical and Mechanical Works). SH-II SITC of LT Panels, Supply and laying of cables and IE works. Tender ID: 2022_AAI_103733_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Youngmen Traders | 3976475.00 | L1
| 2 | Industrial Traders | 4554222.00 | L2
| 3 | SAHA COMMERCIAL CONSTRUCTION | 4646535.00 | L3
| 4 | Mukherjee Commercial Enterprise | 4941420.00 | L4
| 5 | jaydeep agency corporation | 5127671.00 | L5
| 6 | SUPER BUILDERS | 6087411.00 | L6